Subject to Future Enforcement | IRO | IRO-010 | IRO-010-6 | 2. | The Reliability Coordinator shall distribute its data and information specification(s) to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M2. The Reliability Coordinator shall make available evidence that it has distributed its specification(s) to entities that have data and information required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. This evidence could include, but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or email records. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | [13 empty] | RC
Subject to Future Enforcement | IRO | IRO-010 | IRO-010-6 | No Parts for 2. |  | M2. The Reliability Coordinator shall make available evidence that it has distributed its specification(s) to entities that have data and information required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. This evidence could include, but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or email records. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000
Subject to Future Enforcement | IRO | IRO-010 | IRO-010-6 | 3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R2 shall satisfy the obligations of the documented specifications. | M3. The Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R2 shall make available evidence that it satisfied the obligations of the documented specification using the specified criteria. Such evidence could include, but is not limited to electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | IRO | IRO-010 | IRO-010-6 | No Parts for 3. |  | M3. The Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R2 shall make available evidence that it satisfied the obligations of the documented specification using the specified criteria. Such evidence could include, but is not limited to electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000
Inactive | IRO | IRO-014 | IRO-014-1 | 1. | The Reliability Coordinator shall have Operating Procedures, Processes, or Plans in place for activities that require notification, exchange of information or coordination of actions with one or more other Reliability Coordinators to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall address Scenarios that affect other Reliability Coordinator Areas as well as those developed in coordination with other Reliability Coordinators. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1. | These Operating Procedures, Processes, or Plans shall collectively address, as a minimum, the following: | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1.1. | Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1.2. | Energy and capacity shortages. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1.3. | Planned or unplanned outage information. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1.4. | Voltage control, including the coordination of reactive resources for voltage control. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1.5. | Coordination of information exchange to support reliability assessments. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 1.1.6. | Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. | M1. The Reliability Coordinator's System Operators shall have available for Real-time use, the latest approved version of Operating Procedures, Processes, or Plans that require notifications, information exchange or the coordination of actions between Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 2. | Each Reliability Coordinator’s Operating Procedure, Process, or Plan that requires one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) shall be: | M2. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were: |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 2.1. | Agreed to by all the Reliability Coordinators required to take the indicated action(s). | M2. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were: |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 2.2. | Distributed to all Reliability Coordinators that are required to take the indicated action(s). | M2. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were: |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 3. | A Reliability Coordinator’s Operating Procedures, Processes, or Plans developed to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan shall include: | M3. The Reliability Coordinator’s Operating Procedures, Processes, or Plans developed (for its System Operators’ internal use) to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan received from another Reliability Coordinator shall: |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 3.1. | A reference to the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. | M3. The Reliability Coordinator’s Operating Procedures, Processes, or Plans developed (for its System Operators’ internal use) to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan received from another Reliability Coordinator shall: |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 3.2. | The agreed-upon actions from the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. | M3. The Reliability Coordinator’s Operating Procedures, Processes, or Plans developed (for its System Operators’ internal use) to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan received from another Reliability Coordinator shall: |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 4. | Each of the Operating Procedures, Processes, and Plans addressed in Reliability Standard IRO-014 Requirement 1 and Requirement 3 shall: | The Reliability Coordinator’s Operating Procedures, Processes, or Plans that addresses Reliability Coordinator-to-Reliability Coordinator coordination shall each include a version control number or date and a distribution list. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were reviewed within the last three years. | Operations Planning, Same-Day Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 4.1. | Include version control number or date. | The Reliability Coordinator’s Operating Procedures, Processes, or Plans that addresses Reliability Coordinator-to-Reliability Coordinator coordination shall each include a version control number or date and a distribution list. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were reviewed within the last three years. | Operations Planning, Same-Day Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 4.2. | Include a distribution list. | The Reliability Coordinator’s Operating Procedures, Processes, or Plans that addresses Reliability Coordinator-to-Reliability Coordinator coordination shall each include a version control number or date and a distribution list. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were reviewed within the last three years. | Operations Planning, Same-Day Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-1 | 4.3. | Be reviewed, at least once every three years, and updated if needed. | The Reliability Coordinator’s Operating Procedures, Processes, or Plans that addresses Reliability Coordinator-to-Reliability Coordinator coordination shall each include a version control number or date and a distribution list. The Reliability Coordinator shall have evidence that these Operating Procedures, Processes, or Plans were reviewed within the last three years. | Operations Planning, Same-Day Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1. | Each Reliability Coordinator shall have Operating Procedures, Operating Processes, or Operating Plans for activities that require notification, exchange of information or coordination of actions that may impact other Reliability Coordinator Areas to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall collectively address the following: | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.1. | Communications and notifications, including the mutually agreed to conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.2. | Energy and capacity shortages. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.3. | Planned or unplanned outage information. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.4. | Control of voltage, including the coordination of reactive resources. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.5. | Coordination of information exchange to support reliability assessments. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.6. | Authority to act to prevent and mitigate system conditions which could cause Adverse Reliability Impacts to other Reliability Coordinator Areas. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 1.7. | Weekly conference calls | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Processes, and Operating Plans that require notifications, information exchange or the coordination of actions among impacted Reliability Coordinators for conditions or activities that impact other Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements. (R1) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: | M2. Each Reliability Coordinator shall have dated evidence that the Operating Procedures, Processes, and Plans that require one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) were: 2.1 Reviewed and updated annually with no more than 15 months between reviews. 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s). This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 2.1. | Review and update annually with no more that 15 months between reviews. | M2. Each Reliability Coordinator shall have dated evidence that the Operating Procedures, Processes, and Plans that require one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) were: 2.1 Reviewed and updated annually with no more than 15 months between reviews. 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s). This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 2.2. | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. | M2. Each Reliability Coordinator shall have dated evidence that the Operating Procedures, Processes, and Plans that require one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) were: 2.1 Reviewed and updated annually with no more than 15 months between reviews. 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s). This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 2.3. | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | M2. Each Reliability Coordinator shall have dated evidence that the Operating Procedures, Processes, and Plans that require one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) were: 2.1 Reviewed and updated annually with no more than 15 months between reviews. 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s). This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | 3. | Each Reliability Coordinator shall make notifications and exchange reliability–related information with other Reliability Coordinators in accordance with the Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1. | M3. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it made notifications and exchanged reliability–related information with impacted Reliability Coordinators in accordance with the Operating Procedures, Processes, or Plans identified in Requirement R1. (R3) | Operations Planning, Real-Time Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it made notifications and exchanged reliability–related information with impacted Reliability Coordinators in accordance with the Operating Procedures, Processes, or Plans identified in Requirement R1. (R3) | Operations Planning, Real-Time Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-014 | IRO-014-2 | 4. | Each Reliability Coordinator shall participate in agreed upon conference calls, at least weekly (per Requirement 1, Part 1.7) with other Reliability Coordinators within the same Interconnection. | M4. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it participated in agreed upon (at least weekly) conference calls with other Reliability Coordinators within the same Interconnection. (R4) | Real-Time Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it participated in agreed upon (at least weekly) conference calls with other Reliability Coordinators within the same Interconnection. (R4) | Real-Time Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-014 | IRO-014-2 | 5. | Each Reliability Coordinator, upon identification of an Adverse Reliability Impact, shall notify all other Reliability Coordinators. | M5. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it, upon identification of an Adverse Reliability Impact, notified other Reliability Coordinators. (R5) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | No Parts for 5. |  | M5. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it, upon identification of an Adverse Reliability Impact, notified other Reliability Coordinators. (R5) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-014 | IRO-014-2 | 6. | During each instance where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact each impacted Reliability Coordinator shall operate as though the problem exists. | M6. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it operated under the assumption that the Adverse Reliability Impact existed during each instance where Reliability Coordinators disagreed on the existence of an Adverse Reliability Impact. (R6) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | No Parts for 6. |  | M6. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it operated under the assumption that the Adverse Reliability Impact existed during each instance where Reliability Coordinators disagreed on the existence of an Adverse Reliability Impact. (R6) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-014 | IRO-014-2 | 7. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, the Reliability Coordinator that identified the Adverse Reliability Impact shall develop an action plan to resolve the Adverse Reliability Impact. | M7. Each Reliability Coordinator that identified an Adverse Reliability Impact shall have evidence and provide evidence that it developed an action plan during those instances where Reliability Coordinators disagreed on the existence of an Adverse Reliability Impact. This evidence may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation. (R7) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | No Parts for 7. |  | M7. Each Reliability Coordinator that identified an Adverse Reliability Impact shall have evidence and provide evidence that it developed an action plan during those instances where Reliability Coordinators disagreed on the existence of an Adverse Reliability Impact. This evidence may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation. (R7) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-014 | IRO-014-2 | 8. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, each Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identified the Adverse Reliability Impact unless such actions would violate safety, equipment, regulatory or statutory requirements. | M8. Each impacted Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it implemented the action plan developed by the Reliability Coordinator who has the identified the Adverse Reliability Impact when a Reliability Coordinator has identified an Adverse Reliability Impact and the impacted Reliability Coordinators disagree on an action unless such actions would have violated safety, equipment, or regulatory or statutory requirements. (R8) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-014 | IRO-014-2 | No Parts for 8. |  | M8. Each impacted Reliability Coordinator shall have and provide evidence which may include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it implemented the action plan developed by the Reliability Coordinator who has the identified the Adverse Reliability Impact when a Reliability Coordinator has identified an Adverse Reliability Impact and the impacted Reliability Coordinators disagree on an action unless such actions would have violated safety, equipment, or regulatory or statutory requirements. (R8) | Operations Planning, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 1. | Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: [See standard for additional information.] | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 1.1. | Criteria and processes for notifications. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 1.2. | Energy and capacity shortages. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 1.3. | Control of voltage, including the coordination of reactive resources. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 1.4. | Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 1.5. | Provisions for periodic communications to support reliable operations. | M1. Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: [See standard for additional information.] | M2. Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 2.1. | Review and update annually with no more than 15 months between reviews. | M2. Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 2.2. | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. | M2. Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 2.3. | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | M2. Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | Operations Planning, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 3. | Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | M3. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to operator logs, voice recordings, or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, notified other impacted Reliability Coordinators. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to operator logs, voice recordings, or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, notified other impacted Reliability Coordinators. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 4. | Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | M4. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it operated as though an Emergency existed during each instance where Reliability Coordinators disagreed on the existence of an Emergency. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it operated as though an Emergency existed during each instance where Reliability Coordinators disagreed on the existence of an Emergency. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 5. | Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Each Reliability Coordinator that identifies an Emergency in its Reliability Coordinator Area shall have evidence that it developed an action plan during those instances where impacted Reliability Coordinators disagreed on the existence of an Emergency. This evidence may include but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | No Parts for 5. |  | Each Reliability Coordinator that identifies an Emergency in its Reliability Coordinator Area shall have evidence that it developed an action plan during those instances where impacted Reliability Coordinators disagreed on the existence of an Emergency. This evidence may include but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 6. | Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Each impacted Reliability Coordinator shall have and provide evidence which may include but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it implemented the action plan developed by the Reliability Coordinator who identifies the Emergency when Reliability Coordinators disagree on the existence of an Emergency unless such actions would have violated safety, equipment, regulatory, or statutory requirements. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | No Parts for 6. |  | Each impacted Reliability Coordinator shall have and provide evidence which may include but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent dated documentation, that will be used to determine that it implemented the action plan developed by the Reliability Coordinator who identifies the Emergency when Reliability Coordinators disagree on the existence of an Emergency unless such actions would have violated safety, equipment, regulatory, or statutory requirements. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | 7. | Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Each Reliability Coordinator shall make available upon request, evidence that requested assistance was provided, if able, to requesting Reliability Coordinators unless such actions could not be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014 | IRO-014-3 | No Parts for 7. |  | Each Reliability Coordinator shall make available upon request, evidence that requested assistance was provided, if able, to requesting Reliability Coordinators unless such actions could not be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-015 | IRO-015-1 | 1. | The Reliability Coordinator shall follow its Operating Procedures, Processes, or Plans for making notifications and exchanging reliability-related information with other Reliability Coordinators. | M1. The Reliability Coordinator shall have evidence (such as operator logs or other data sources) it has followed its Operating Procedures, Processes, or Plans for notifying other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-015 | IRO-015-1 | 1.1. | The Reliability Coordinator shall make notifications to other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. | M1. The Reliability Coordinator shall have evidence (such as operator logs or other data sources) it has followed its Operating Procedures, Processes, or Plans for notifying other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-015 | IRO-015-1 | 2. | The Reliability Coordinator shall participate in agreed upon conference calls and other communication forums with adjacent Reliability Coordinators. | M2. The Reliability Coordinator shall have evidence (such as operator logs or other data sources) that it participated in agreed upon (at least weekly) conference calls and other communication forums with adjacent Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-015 | IRO-015-1 | 2.1. | The frequency of these conference calls shall be agreed upon by all involved Reliability Coordinators and shall be at least weekly. | M2. The Reliability Coordinator shall have evidence (such as operator logs or other data sources) that it participated in agreed upon (at least weekly) conference calls and other communication forums with adjacent Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-015 | IRO-015-1 | 3. | The Reliability Coordinator shall provide reliability-related information as requested by other Reliability Coordinators. | M3. The Reliability Coordinator shall have evidence that it provided requested reliability-related information to other Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-015 | IRO-015-1 | No Parts for 3. |  | M3. The Reliability Coordinator shall have evidence that it provided requested reliability-related information to other Reliability Coordinators. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-016 | IRO-016-1 | 1. | The Reliability Coordinator that identifies a potential, expected, or actual problem that requires the actions of one or more other Reliability Coordinators shall contact the other Reliability Coordinator(s) to confirm that there is a problem and then discuss options and decide upon a solution to prevent or resolve the identified problem. | M1. For each event that requires Reliability Coordinator-to-Reliability Coordinator coordination, each involved Reliability Coordinator shall have evidence (operator logs or other data sources) of the actions taken for either the event or for the disagreement on the problem or for both. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | 1.1. | If the involved Reliability Coordinators agree on the problem and the actions to take to prevent or mitigate the system condition, each involved Reliability Coordinator shall implement the agreed-upon solution, and notify the involved Reliability Coordinators of the action(s) taken. | M1. For each event that requires Reliability Coordinator-to-Reliability Coordinator coordination, each involved Reliability Coordinator shall have evidence (operator logs or other data sources) of the actions taken for either the event or for the disagreement on the problem or for both. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | 1.2. | If the involved Reliability Coordinators cannot agree on the problem(s) each Reliability Coordinator shall re-evaluate the causes of the disagreement (bad data, status, study results, tools, etc.). | M1. For each event that requires Reliability Coordinator-to-Reliability Coordinator coordination, each involved Reliability Coordinator shall have evidence (operator logs or other data sources) of the actions taken for either the event or for the disagreement on the problem or for both. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | 1.2.1. | If time permits, this re-evaluation shall be done before taking corrective actions. | M1. For each event that requires Reliability Coordinator-to-Reliability Coordinator coordination, each involved Reliability Coordinator shall have evidence (operator logs or other data sources) of the actions taken for either the event or for the disagreement on the problem or for both. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | 1.2.2. | If time does not permit, then each Reliability Coordinator shall operate as though the problem(s) exist(s) until the conflicting system status is resolved. | M1. For each event that requires Reliability Coordinator-to-Reliability Coordinator coordination, each involved Reliability Coordinator shall have evidence (operator logs or other data sources) of the actions taken for either the event or for the disagreement on the problem or for both. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | 1.3. | If the involved Reliability Coordinators cannot agree on the solution, the more conservative solution shall be implemented. | M1. For each event that requires Reliability Coordinator-to-Reliability Coordinator coordination, each involved Reliability Coordinator shall have evidence (operator logs or other data sources) of the actions taken for either the event or for the disagreement on the problem or for both. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | 2. | The Reliability Coordinator shall document (via operator logs or other data sources) its actions taken for either the event or for the disagreement on the problem(s) or for both. |  | Real-Time Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-016 | IRO-016-1 | No Parts for 2. |  |  | Real-Time Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1. | Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1.1. | Identify applicable roles and reporting responsibilities including: | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1.1.1. | Development and communication of outage schedules. | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2017-04-01 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1.1.2. | Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2017-04-01 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1.2. | Specify outage submission timing requirements. | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1.3. | Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 1.4. | Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | M1. Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  |  | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 2. | Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | M2. Each Transmission Operator and Balancing Authority shall provide evidence upon request that it performed the functions specified in its Reliability Coordinator’s outage coordination process. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | BA | [19 empty] | TOP
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | No Parts for 2. |  | M2. Each Transmission Operator and Balancing Authority shall provide evidence upon request that it performed the functions specified in its Reliability Coordinator’s outage coordination process. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | M3. Each Planning Coordinator and Transmission Planner shall provide evidence upon request showing that it provided its Planning Assessment to impacted Reliability Coordinators. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Long-Term Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | No Parts for 3. |  | M3. Each Planning Coordinator and Transmission Planner shall provide evidence upon request showing that it provided its Planning Assessment to impacted Reliability Coordinators. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Long-Term Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | 4. | Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | M4. Each Planning Coordinator, and Transmission Planner shall provide evidence upon request showing that it jointly developed solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-term Transmission Planning Horizon. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Long-Term Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | IRO | IRO-017 | IRO-017-1 | No Parts for 4. |  | M4. Each Planning Coordinator, and Transmission Planner shall provide evidence upon request showing that it jointly developed solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-term Transmission Planning Horizon. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Long-Term Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-018 | IRO-018-1 | 1. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 1.1. | Criteria for evaluating the quality of Real-time data; | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 2. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 2.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 2.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 2.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | 3. | Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M3. Each Reliability Coordinator shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [13 empty] | RC
Inactive | IRO | IRO-018 | IRO-018-1 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 1. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 1.1. | Criteria for evaluating the quality of Real-time data; | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | M1. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 2. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | M2. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 2.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | M2. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 2.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | M2. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 2.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | M2. Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | 3. | Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M3. Each Reliability Coordinator shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018 | IRO-018-1(i) | No Parts for 3. |  | M3. Each Reliability Coordinator shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000
Inactive | IRO | IRO-STD | IRO-STD-006-0 | W1. | Curtailment of Contributing Schedules WECC’s Unscheduled Flow Mitigation Plan (Plan), which is on file with FERC and has been accepted by FERC (most recently prior to the date hereof on November 20, 2001 in Docket No. ER01-3085-000), 1/ specifies that members2/ shall comply with requests from (Qualified) Transfer Path Operators to take actions that will reduce unscheduled flow on the Qualified Path in accordance with the table entitled “WECC Unscheduled Flow Procedure Summary of Curtailment Actions,” which is located in Attachment 1 of the Plan. Plan Section 11: 11.1 When USF Accommodation, as specified in Section 7, together with coordinated operation of the Qualified Controllable Devices, as specified in Section 9, are insufficient to reduce the Actual Flow on the Qualified Transfer Path to below the Transfer Limit, the Transfer Path Operator shall request curtailments in Schedules that contribute to the USF through the Qualified Transfer Path according to the USF Reduction Procedure. 11.2 Responsible Entities shall comply in a timely manner with a Transfer Path Operator's request for Schedule Curtailments. 1/ Capitalized terms used in this section, unless separately defined in this standard, shall have the meaning specified in the Plan. 2/ Reliability Standard will apply to all Responsible Entities within theWestern Interconnection. Plan Attachment 1 Section 9: “h. Upon receipt of a curtailment request, Contributing Schedules which are subject to curtailments will be reduced (or equivalent alternative schedule adjustments will be effected) in accordance with the following procedures: i. Receivers of Contributing Schedules will initiate the requested schedule reductions unless an otherwise agreed upon procedure for schedule reduction achieving the equivalent effect on the Qualified Transfer Path is established by the Receiver and/or the Sender. ii. Responsible Entities may arrange among themselves to make curtailments called for by this USF Reduction Procedure in a manner other than prescribed provided that the arrangements are as effective as the identified schedule curtailment in reducing USF across the Qualified Transfer Path. Responsible Entities may make bilateral arrangements, which will enable a Responsible Entity with schedules on the affected Qualified Transfer Path to make the required curtailments in lieu of making larger curtailments in schedules over other parallel paths. Where alternative schedule adjustments are utilized, it is the Receiver's responsibility to cause schedule adjustments to be effected which provide the same reduction in flow across the Qualified Transfer Path as would have been achieved by the prescribed reduction in the Contributing Schedule. iii. The total amount of requested schedule reduction may be apportioned to the applicable schedules at the discretion of the Receiver subject to item iv below. iv. Irrespective of the schedules altered or the manner in which they are altered, each Responsible Entity's overall net reduction in Actual Flow across the constrained Qualified Transfer Path must be equivalent to or greater than the reduction which would have been achieved had the identified schedule reduction occurred as requested. v. System dispatchers or real-time schedulers should identify in advance those schedules that qualify for curtailment requests for all Qualified Transfer Paths. This will expedite implementation of this USF Reduction Procedure when requested. vi. While this USF Reduction Procedure does not expect receivers to curtail schedules which would result in loss of firm load, nothing in this USF Reduction Procedure shall relieve the receiver of the obligation to achieve the required reduction in USF across the constrained Qualified Transfer Path.” Contributing Schedule curtailments apply to schedules in place before initiation of the USF Procedure at Step 4 (First level Contributing Schedule Curtailment) or higher step. At the time a Step 4 Level 1 USF Action or higher step is initiated, Schedules are established by the existence of an “Implemented” NERC Transaction Tag. Restricted Transactions After the USF Event is declared, a transaction with greater than a 5% Transfer Distribution Factor (TDF) on the Qualified Path in the qualified direction will be considered a “Restricted Transaction.” Changes to Restricted Transactions, other thanthe specific curtailments used to comply with relief obligations, cannot be made unless some alternative action is taken to compensate for the full impact on the Qualified Path. This applies to: New transaction, and Extensions or Adjustments to existing transaction.” If two or more Qualified Paths become simultaneously constrained to the point where the curtailment of contributing schedules is necessary, schedule curtailments which relieve USF on one path but increase USF on any other curtailed path shall not be made, unless specific procedures or methods are provided to address this condition. The entity shall be compliant with this standard although the required curtailments were not made. |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000 | BA | [8 empty] | LSE | [10 empty] | TOP
Inactive | IRO | IRO-STD | IRO-STD-006-0 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000
Inactive | MOD | MOD-001 | MOD-001-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional TTC and ATC methodology. (Certain systems that are not required to post ATC values are exempt from this standard.) The Regional Reliability Organization’s TTC and ATC methodology shall include each of the following nine items, and shall explain its use in determining TTC and ATC values: |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.1. | A narrative explaining how TTC and ATC values are determined. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.2. | An accounting for how the reservations and schedules for firm (non-recallable) and non-firm (recallable) transfers, both within and outside the Transmission Service Provider’s system, are included. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.3. | An accounting for the ultimate points of power injection (sources) and power extraction (sinks) in TTC and ATC calculations. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.4. | A description of how incomplete or so-called partial path transmission reservations are addressed. (Incomplete or partial path transmission reservations are those for which all transmission reservations necessary to complete the transmission path from ultimate source to ultimate sink are not identifiable due to differing reservation priorities, durations, or because the reservations have not all been made.) |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.5. | A requirement that TTC and ATC values shall be determined and posted as follows: |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.5.1. | Daily values for current week at least once per day. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.5.2. | Daily values for day 8 through the first month at least once per week. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.5.3. | Monthly values for months 2 through 13 at least once per month. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.6. | Indication of the treatment and level of customer demands, including interruptible demands. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.7. | A specification of how system conditions, limiting facilities, contingencies, transmission reservations, energy schedules, and other data needed by Transmission Service Providers for the calculation of TTC and ATC values are shared and used within the Regional Reliability Organization and with neighboring interconnected electric systems, including adjacent systems, subregions, and Regional Reliability Organizations. In addition, specify how this information is to be used to determine TTC and ATC values. If some data is not used, provide an explanation. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO | [5 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-0 | 1.8. | A description of how the assumptions for and the calculations of TTC and ATC values change over different time (such as hourly, daily, and monthly) horizons. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 1.9. | A description of the Regional Reliability Organization’s practice on the netting of transmission reservations for purposes of TTC and ATC determination. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | 2. | The Regional Reliability Organization shall make the most recent version of the documentation of its TTC and ATC methodology available on a Web site accessible by NERC, the Regional Reliability Organizations, and transmission users. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-001 | MOD-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-001 | MOD-001-1 | 1. | Each Transmission Operator shall select one of the methodologies listed below for calculating Available Transfer Capability (ATC) or Available Flowgate Capability (AFC) for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area: The Area Interchange Methodology, as described in MOD-028, The Rated System Path Methodology, as described in MOD-029, The Flowgate Methodology, as described in MOD-030 | The Transmission Operator shall provide evidence (such as a calculation, inclusion of the information in the ATCID, or other written documentation) that it has selected one of the specified methodologies per time period in R2 for use in determining Transfer Capabilities of those Facilities for each ATC Path within the Transmission Operator’s operating area. (R1). | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-001 | MOD-001-1 | No Parts for 1. |  | The Transmission Operator shall provide evidence (such as a calculation, inclusion of the information in the ATCID, or other written documentation) that it has selected one of the specified methodologies per time period in R2 for use in determining Transfer Capabilities of those Facilities for each ATC Path within the Transmission Operator’s operating area. (R1). | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-001 | MOD-001-1 | 2. | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): | The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 2.1. | Hourly values for at least the next 48 hours. | The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 2.2. | Daily values for at least the next 31 calendar days. | The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 2.3. | Monthly values for at least the next 12 months (months 2-13). | The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3. | Each Transmission Service Provider shall prepare and keep current an Available Transfer Capability Implementation Document (ATCID) that includes, at a minimum, the following information: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.1. | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.2. | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.2.1. | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.2.2. | A rationale for that accounting specified in R3.2. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.3. | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.4. | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.5. | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.6. | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.6.1. | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.6.2. | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 3.6.3. | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4. | The Transmission Service Provider shall notify the following entities before implementing a new or revised ATCID: |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4.1. | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4.2. | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4.3. | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4.4. | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4.5. | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 4.6. | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 5. | The Transmission Service Provider shall make available the current ATCID to all of the entities specified in R4. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | No Parts for 5. |  |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-001 | MOD-001-1 | 6. | When calculating Total Transfer Capability (TTC) or Total Flowgate Capability (TFC) the Transmission Operator shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-001 | MOD-001-1 | No Parts for 6. |  |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-001 | MOD-001-1 | 7. | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | No Parts for 7. |  |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-001 | MOD-001-1 | 8. | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 8.1. | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 8.2. | Daily values, once per day. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 8.3. | Monthly values, once per week. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 9. | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider: Dispatch Order, Participation Factors, Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: ? A list of Elements, A list of Flowgates,? A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings.• Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. | The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. (R9) | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 9.1. | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). | The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. (R9) | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 9.1.1. | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available | The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. (R9) | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 9.1.2. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available. | The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. (R9) | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 9.1.3. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available. | The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. (R9) | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1 | 9.2. | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). | The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. (R9) | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 1. | Each Transmission Operator shall select one of the methodologies listed below for calculating Available Transfer Capability (ATC) or Available Flowgate Capability (AFC) for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area: .The Area Interchange Methodology, as described in MOD-028 .The Rated System Path Methodology, as described in MOD-029 .The Flowgate Methodology, as described in MOD-030 Footnote: All ATC Paths do not have to use the same methodology and no particular ATC Path must use the same methodology for all time periods. | The Transmission Operator shall provide evidence (such as a calculation, inclusion of the information in the ATCID, or other written documentation) that it has selected one of the specified methodologies per time period in R2 for use in determining Transfer Capabilities of those Facilities for each ATC Path within the Transmission Operator’s operating area. (R1). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-001 | MOD-001-1a | No Parts for 1. |  | The Transmission Operator shall provide evidence (such as a calculation, inclusion of the information in the ATCID, or other written documentation) that it has selected one of the specified methodologies per time period in R2 for use in determining Transfer Capabilities of those Facilities for each ATC Path within the Transmission Operator’s operating area. (R1). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-001 | MOD-001-1a | 2. | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): | M2.The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 2.1. | Hourly values for at least the next 48 hours. | M2.The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 2.2. | Daily values for at least the next 31 calendar days. | M2.The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 2.3. | Monthly values for at least the next 12 months (months 2-13). | M2.The Transmission Service Provider shall provide ATC or AFC values and identification of the selected methodologies along with other evidence (such as written documentation, processes, or data) to show it calculated ATC or AFC for the following using the selected methodology or methodologies chosen as part of R1 (R2): - There has been at least 48 hours of hourly values calculated at all times. (R2.1) - There has been at least 31 consecutive calendar days of daily values calculated at all times. (R2.2) - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). (R2.3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3. | Each Transmission Service Provider shall prepare and keep current an Available Transfer Capability Implementation Document (ATCID) that includes, at a minimum, the following information: | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.1. | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.2. | A description of the manner in which the Transmission Service Provider will account for counterflows including: | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.2.1. | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.2.2. | A rationale for that accounting specified in R3.2. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.3. | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.4. | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.5. | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.6. | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.6.1. | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.6.2. | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 3.6.3. | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. | The Transmission Service Provider shall provide its current ATCID that contains all the information specified in R3. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4. | The Transmission Service Provider shall notify the following entities before implementing a new or revised ATCID: [Time Horizon: Operations Planning] | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4.1. | Each Planning Coordinator associated with the Transmission Service Provider’s area. | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4.2. | Each Reliability Coordinator associated with the Transmission Service Provider’s area. | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4.3. | Each Transmission Operator associated with the Transmission Service Provider’s area. | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4.4. | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4.5. | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 4.6. | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. | The Transmission Service Provider shall provide evidence (such as dated electronic mail messages, mail receipts, or voice recordings) that it has notified the entities specified in R4 before a new or revised ATCID was implemented. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 5. | The Transmission Service Provider shall make available the current ATCID to all of the entities specified in R4. | M5. The Transmission Service Provider shall provide evidence (such as a demonstration) that the current ATCID is available to all of the entities specified in R4, as required by R5. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | No Parts for 5. |  | M5. The Transmission Service Provider shall provide evidence (such as a demonstration) that the current ATCID is available to all of the entities specified in R4, as required by R5. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-001 | MOD-001-1a | 6. | When calculating Total Transfer Capability (TTC) or Total Flowgate Capability (TFC) the Transmission Operator shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. | M6. The Transmission Operator shall provide a copy of the assumptions (such as contingencies, loop flow, generation re-dispatch, switching operating guides or data sources for load forecast and facility outages) used to calculate TTC or TFC as well as other evidence (such as copies of operations planning studies, models, supporting information, or data) to show that the assumptions used in determining TTC or TFC are no more limiting than those used in planning of operations for the corresponding time period studied. Alternatively the Transmission Operator may demonstrate that the same load flow cases are used for both TTC or TFC and Operations Planning. When different inputs to the calculations are used because the calculations are performed at different times, such that the most recent information is used in any calculation, a difference in that input data shall not be considered to be a difference in assumptions. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-001 | MOD-001-1a | No Parts for 6. |  | M6. The Transmission Operator shall provide a copy of the assumptions (such as contingencies, loop flow, generation re-dispatch, switching operating guides or data sources for load forecast and facility outages) used to calculate TTC or TFC as well as other evidence (such as copies of operations planning studies, models, supporting information, or data) to show that the assumptions used in determining TTC or TFC are no more limiting than those used in planning of operations for the corresponding time period studied. Alternatively the Transmission Operator may demonstrate that the same load flow cases are used for both TTC or TFC and Operations Planning. When different inputs to the calculations are used because the calculations are performed at different times, such that the most recent information is used in any calculation, a difference in that input data shall not be considered to be a difference in assumptions. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-001 | MOD-001-1a | 7. | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. | M7. The Transmission Service Provider shall provide a copy of the assumptions (such as contingencies, loop flow, generation re-dispatch, switching operating guides or data sources for load forecast and facility outages) used to calculate ATC or AFC as well as other evidence (such as copies of operations planning studies, models, supporting information, or data) to show that the assumptions used in determining ATC or AFC are no more limiting than those used in planning of operations for the corresponding time period studied. Alternatively the Transmission Service Provider may demonstrate that the same load flow cases are used for both AFC and Operations Planning. When different inputs to the calculations are used because the calculations are performed at different times, such that the most recent information is used in any calculation, a difference in that input data shall not be considered to be a difference in assumptions. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | No Parts for 7. |  | M7. The Transmission Service Provider shall provide a copy of the assumptions (such as contingencies, loop flow, generation re-dispatch, switching operating guides or data sources for load forecast and facility outages) used to calculate ATC or AFC as well as other evidence (such as copies of operations planning studies, models, supporting information, or data) to show that the assumptions used in determining ATC or AFC are no more limiting than those used in planning of operations for the corresponding time period studied. Alternatively the Transmission Service Provider may demonstrate that the same load flow cases are used for both AFC and Operations Planning. When different inputs to the calculations are used because the calculations are performed at different times, such that the most recent information is used in any calculation, a difference in that input data shall not be considered to be a difference in assumptions. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-001 | MOD-001-1a | 8. | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: | M8. The Transmission Service Provider calculating ATC shall provide evidence (such as logs or data) that it has calculated the hourly, daily, and monthly values on at least the minimum frequencies specified in R8 or provide evidence (such as data, procedures, or software documentation) that the calculated values identified in the ATC equation have not changed. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 8.1. | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. | M8. The Transmission Service Provider calculating ATC shall provide evidence (such as logs or data) that it has calculated the hourly, daily, and monthly values on at least the minimum frequencies specified in R8 or provide evidence (such as data, procedures, or software documentation) that the calculated values identified in the ATC equation have not changed. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 8.2. | Daily values, once per day. | M8. The Transmission Service Provider calculating ATC shall provide evidence (such as logs or data) that it has calculated the hourly, daily, and monthly values on at least the minimum frequencies specified in R8 or provide evidence (such as data, procedures, or software documentation) that the calculated values identified in the ATC equation have not changed. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 8.3. | Monthly values, once per week. | M8. The Transmission Service Provider calculating ATC shall provide evidence (such as logs or data) that it has calculated the hourly, daily, and monthly values on at least the minimum frequencies specified in R8 or provide evidence (such as data, procedures, or software documentation) that the calculated values identified in the ATC equation have not changed. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 9. | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider: Dispatch Order, Participation Factors, Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: - A list of Elements, -A list of Flowgates,- A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings.• Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. | M9. The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 9.1. | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). | M9. The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 9.1.1. | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available | M9. The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 9.1.2. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available | M9. The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 9.1.3. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available | M9. The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-1a | 9.2. | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). | M9. The Transmission Service Provider shall provide a copy of the dated request, if any, for ATC or AFC data as well as evidence to show it responded to that request (such as logs or data) within thirty calendar days of receiving the request, and the requested data items were made available in accordance with R9. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2024-02-01 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1. | Each Transmission Operator that determines Total Flowgate Capability (TFC) or Total Transfer Capability (TTC) shall develop a written methodology (or methodologies) for determining TFC or TTC values. The methodology (or methodologies) shall reflect the Transmission Operator’s current practices for determining TFC or TTC values. | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.1. | Each methodology shall describe the method used to account for the following limitations in both the pre- and post-contingency state: | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.1.1. | Facility ratings; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.1.2. | System voltage limits; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.1.3. | Transient stability limits; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.1.4. | Voltage stability limits; and | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.1.5. | Other System Operating Limits (SOLs). | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2. | Each methodology shall describe the method used to account for each of the following elements, provided such elements impact the determination of TFC or TTC: | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.1. | The simulation of transfers performed through the adjustment of generation, Load, or both; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.2. | Transmission topology, including, but not limited to, additions and retirements; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.3. | Expected transmission uses; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.4. | Planned outages; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.5. | Parallel path (loop flow) adjustments; | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.6. | Load forecast; and | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.2.7. | Generator dispatch, including, but not limited to, additions and retirements. | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.3. | Each methodology shall describe the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, provided that (1) the request references this specific requirement, and (2) the requesting Transmission Operator includes those constraints in its TFC or TTC determination. | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.3.1. | Each Transmission Operator that uses the Flowgate Methodology shall include in its methodology an impact test process for including requested constraints. If a generator to Load transfer in a registered entity’s area or a transfer to a neighboring registered entity impacts the requested constraint by five percent or greater, the requested constraint shall be included in the TFC determination, otherwise the requested constraint is not required to be included. | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.3.2. | Each Transmission Operator that uses the Area Interchange or Rated System Path Methodology shall describe in its methodology the process it uses to account for requested constraints that have a five percent or greater distribution factor for a transfer between areas in the TTC determination; otherwise the requested constraint is not required to be included. When testing transfers involving the requesting Transmission Operator’s area, the requested constraint may be excluded. | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 1.3.3. | A different method for determining whether requested constraints need to be included in the TFC or TTC determination may be used if agreed to by the Transmission Operators. | M1. Each Transmission Operator that determines TFC or TTC shall provide its current written methodology (or methodologies) or other evidence (such as written documentation) to show that its methodology (or methodologies) contains the following: • A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. • A description of the method used to account for the elements specified in part 1.2, provided such elements impact the determination of TFC or TTC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A statement that the element is not accounted for since it does not affect the determination of TFC or TTC. o A description of how the element is used in the determination of TFC or TTC. • A description of the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, as specified in parts 1.3, 1.3.1, 1.3.2, or 1.3.3). • Each Transmission Operator that determines TFC or TTC shall provide evidence that currently active TFC or TTC values were determined based on its current written methodology, as specified in Requirement R1. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2. | Each Transmission Service Provider that determines Available Flowgate Capability (AFC) or Available Transfer Capability (ATC) shall develop an Available Transfer Capability Implementation Document (ATCID) that describes the methodology (or methodologies) for determining AFC or ATC values. The methodology (or methodologies) shall reflect the Transmission Service Provider’s current practices for determining AFC or ATC values. | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1. | Each methodology shall describe the method used to account for the following elements, provided such elements impact the determination of AFC or ATC: | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.1. | The simulation of transfers performed through the adjustment of generation, Load, or both; | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.2. | Transmission topology, including, but not limited to, additions and retirements; | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.3. | Expected transmission uses; | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.4. | Planned outages; | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.5. | Parallel path (loop flow) adjustments; | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.6. | Load forecast; and | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.1.7. | Generator dispatch, including, but not limited to, additions and retirements. | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 2.2. | Each Transmission Service Provider that uses the Flowgate Methodology shall, for reliability-related constraints identified in part 1.3, use the AFC determined by the Transmission Service Provider for that constraint. | M2. Each Transmission Service Provider that determines AFC or ATC shall provide its current ATCID or other evidence (such as written documentation) to show that its ATCID contains the following: • A description of the method used to account for the elements specified in part 2.1, provided such elements impact the determination of AFC or ATC. Methods of accounting for these elements may include, but are not limited to, one or more of the following: o A description of how the element is used in the determination of AFC or ATC. o A statement that the element is not accounted for since it does not affect the determination of AFC or ATC. o A statement that the element is accounted for in the determination of TFC or TTC by the Transmission Operator, and does not otherwise affect the determination of AFC or ATC. • For each Transmission Service Provider that uses the Flowgate Methodology, a description of the method in which AFC provided by another Transmission Service Provider was used for the reliability-related constraints identified in part 1.3. • Each Transmission Service Provider that determines AFC or ATC shall provide evidence that currently active AFC or ATC values were determined based on its current written methodology, as specified in Requirement R2. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 3. | Each Transmission Service Provider that determines Capacity Benefit Margin (CBM) values shall develop a Capacity Benefit Margin Implementation Document (CBMID) that describes its method for determining CBM values. The method described in the CBMID shall reflect the Transmission Service Provider’s current practices for determining CBM values. | M3. Each Transmission Service Provider that determines CBM shall provide evidence, including, but not limited to, its current CBMID, current CBM values, or other evidence (such as written documentation, study reports, or supporting information) to demonstrate that it determined CBM values consistent with its methodology described in the CBMID. If a Transmission Service Provider does not maintain CBM, examples of evidence include, but are not limited to, an attestation, statement, or other documentation that states the Transmission Service Provider does not maintain CBM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [22 empty] | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | No Parts for 3. |  | M3. Each Transmission Service Provider that determines CBM shall provide evidence, including, but not limited to, its current CBMID, current CBM values, or other evidence (such as written documentation, study reports, or supporting information) to demonstrate that it determined CBM values consistent with its methodology described in the CBMID. If a Transmission Service Provider does not maintain CBM, examples of evidence include, but are not limited to, an attestation, statement, or other documentation that states the Transmission Service Provider does not maintain CBM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements.
Inactive | MOD | MOD-001 | MOD-001-2 | 4. | Each Transmission Operator that determines Transmission Reliability Margin (TRM) values shall develop a Transmission Reliability Margin Implementation Document (TRMID) that describes its method for determining TRM values. The method described in the TRMID shall reflect the Transmission Operator’s current practices for determining TRM values. | M4. Each Transmission Operator that determines TRM shall provide evidence including, but not limited to, its current TRMID, current TRM values, or other evidence (such as written documentation, study reports, or supporting information) to demonstrate that it determined TRM values consistent with its methodology described in the TRMID. If a Transmission Operator does not maintain TRM, examples of evidence include, but are not limited to, an attestation, statement, or other documentation that states the Transmission Operator does not maintain TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP
Inactive | MOD | MOD-001 | MOD-001-2 | No Parts for 4. |  | M4. Each Transmission Operator that determines TRM shall provide evidence including, but not limited to, its current TRMID, current TRM values, or other evidence (such as written documentation, study reports, or supporting information) to demonstrate that it determined TRM values consistent with its methodology described in the TRMID. If a Transmission Operator does not maintain TRM, examples of evidence include, but are not limited to, an attestation, statement, or other documentation that states the Transmission Operator does not maintain TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements.
Inactive | MOD | MOD-001 | MOD-001-2 | 5. | Within 45 calendar days of receiving a written request that references this specific requirement from a Planning Coordinator, Reliability Coordinator, Transmission Operator, Transmission Planner, Transmission Service Provider, or any other registered entity that demonstrates a reliability need, each Transmission Operator or Transmission Service Provider shall provide: | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.1. | A written response to any request for clarification of its TFC or TTC methodology, ATCID, CBMID, or TRMID. If the request for clarification is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements then a written response shall be provided explaining the clarifications not provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.2. | If not publicly posted on OASIS or its company website, the Transmission Operator’s effective: | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.2.1. | TRMID; and | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.2.2. | TFC or TTC methodology. | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.3. | If not publicly posted on OASIS or its company website, the Transmission Service Provider’s effective: | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.3.1. | ATCID; and | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 5.3.2. | CBMID. | M5. Examples of evidence include, but are not limited to: • Dated records of the request and the Transmission Operator’s or Transmission Service Provider’s response to the request; • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests; or • A statement by the Transmission Operator or Transmission Service Provider that they do not determine one or more of these values: AFC, ATC, CBM, TFC, TTC or TRM. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 6. | Each Transmission Operator or Transmission Service Provider that receives a written request from another Transmission Operator or Transmission Service Provider for data related to AFC, ATC, TFC, or TTC determinations that (1) references this specific requirement, and (2) specifies that the requested data is for use in the requesting party’s AFC, ATC, TFC, or TTC determination shall take one of the actions below. | M6. Examples of evidence for a data request that involves providing data on an ongoing basis (6.1), include, but are not limited to: • Dated records of a registered entity’s request, and examples of the response being met; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met (demonstration that the response was met is not required if the requestor confirms it is being provided); or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. Examples of evidence for all other data requests (6.2) include, but are not limited to: • Dated records of a registered entity’s request, and the response to the request; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met; or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. An example of evidence of a response by the Transmission Operator or Transmission Service Provider that providing the data would be contrary to the registered entity’s confidentiality, regulatory, or security requirements (6.3) is a response to the requestor specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 6.1. | In responding to a written request for data on an ongoing basis, the Transmission Service Provider or Transmission Operator shall make available its data on an ongoing basis no later than 45 calendar days from receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to: | M6. Examples of evidence for a data request that involves providing data on an ongoing basis (6.1), include, but are not limited to: • Dated records of a registered entity’s request, and examples of the response being met; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met (demonstration that the response was met is not required if the requestor confirms it is being provided); or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. Examples of evidence for all other data requests (6.2) include, but are not limited to: • Dated records of a registered entity’s request, and the response to the request; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met; or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. An example of evidence of a response by the Transmission Operator or Transmission Service Provider that providing the data would be contrary to the registered entity’s confidentiality, regulatory, or security requirements (6.3) is a response to the requestor specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 6.1.1. | Alter the format in which it maintains or uses the data; or | M6. Examples of evidence for a data request that involves providing data on an ongoing basis (6.1), include, but are not limited to: • Dated records of a registered entity’s request, and examples of the response being met; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met (demonstration that the response was met is not required if the requestor confirms it is being provided); or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. Examples of evidence for all other data requests (6.2) include, but are not limited to: • Dated records of a registered entity’s request, and the response to the request; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met; or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. An example of evidence of a response by the Transmission Operator or Transmission Service Provider that providing the data would be contrary to the registered entity’s confidentiality, regulatory, or security requirements (6.3) is a response to the requestor specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 6.1.2. | Make available the requested data on a more frequent basis than it produces the data and in no event shall it be required to provide the data more frequently than once an hour. | M6. Examples of evidence for a data request that involves providing data on an ongoing basis (6.1), include, but are not limited to: • Dated records of a registered entity’s request, and examples of the response being met; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met (demonstration that the response was met is not required if the requestor confirms it is being provided); or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. Examples of evidence for all other data requests (6.2) include, but are not limited to: • Dated records of a registered entity’s request, and the response to the request; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met; or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. An example of evidence of a response by the Transmission Operator or Transmission Service Provider that providing the data would be contrary to the registered entity’s confidentiality, regulatory, or security requirements (6.3) is a response to the requestor specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 6.2. | In responding to all other data requests, each Transmission Operator or Transmission Service Provider shall make available the requested data within 45 calendar days of receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to alter the format in which it maintains or uses the data. | M6. Examples of evidence for a data request that involves providing data on an ongoing basis (6.1), include, but are not limited to: • Dated records of a registered entity’s request, and examples of the response being met; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met (demonstration that the response was met is not required if the requestor confirms it is being provided); or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. Examples of evidence for all other data requests (6.2) include, but are not limited to: • Dated records of a registered entity’s request, and the response to the request; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met; or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. An example of evidence of a response by the Transmission Operator or Transmission Service Provider that providing the data would be contrary to the registered entity’s confidentiality, regulatory, or security requirements (6.3) is a response to the requestor specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-001 | MOD-001-2 | 6.3. | If making available any requested data under parts 6.1 or 6.2 of this requirement is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements, the Transmission Operator or Transmission Service Provider shall not be required to make available that data; provided that, within 45 calendar days of the written request, it responds to the requesting registered entity specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory or security concerns. | M6. Examples of evidence for a data request that involves providing data on an ongoing basis (6.1), include, but are not limited to: • Dated records of a registered entity’s request, and examples of the response being met; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met (demonstration that the response was met is not required if the requestor confirms it is being provided); or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. Examples of evidence for all other data requests (6.2) include, but are not limited to: • Dated records of a registered entity’s request, and the response to the request; • Dated records of a registered entity’s request, and a statement from the requestor that the request was met; or • A statement by the Transmission Operator or Transmission Service Provider that they have received no requests under this requirement. An example of evidence of a response by the Transmission Operator or Transmission Service Provider that providing the data would be contrary to the registered entity’s confidentiality, regulatory, or security requirements (6.3) is a response to the requestor specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | Operations Planning | 2014-02-06 | 2014-02-10 | [7 empty] | 2019-05-09 | Filing/Order Docket No. RM14-7-000 Petition for approval was withdrawn as part of Project 2018-03 SER Retirements. | [20 empty] | TOP |  | TSP
Inactive | MOD | MOD-002 | MOD-002-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and implement a procedure to periodically review (at least annually) and ensure that the TTC and ATC calculations and resulting values of member Transmission Service Providers comply with the Regional TTC and ATC methodology and applicable Regional criteria. |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-002 | MOD-002-0 | No Parts for 1. |  |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-002 | MOD-002-0 | 2. | Each Regional Reliability Organization shall document the results of its periodic reviews of TTC and ATC. |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-002 | MOD-002-0 | No Parts for 2. |  |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-002 | MOD-002-0 | 3. | The Regional Reliability Organization shall provide the results of its most current reviews of TTC and ATC to NERC on request (within 30 calendar days). |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-002 | MOD-002-0 | No Parts for 3. |  |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-003 | MOD-003-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a procedure on how transmission users can input their concerns or questions regarding the TTC and ATC methodology and values of the Transmission Service Provider(s), and how these concerns or questions will be addressed. The Regional Reliability Organization’s procedure shall specify the following: |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-003 | MOD-003-0 | 1.1. | The name, telephone number and email address of a contact person to whom concerns are to be addressed. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-003 | MOD-003-0 | 1.2. | The amount of time it will take for a response. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-003 | MOD-003-0 | 1.3. | The manner in which the response will be communicated (e.g., email, letter, telephone, etc). |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-003 | MOD-003-0 | 1.4. | What recourse a customer has if the response is deemed unsatisfactory. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-003 | MOD-003-0 | 2. | The Regional Reliability Organization shall post on a web site that is accessible by the Regional Reliability Organizations, NERC, and transmission users, its procedure for receiving and addressing concerns about the TTC and ATC methodology and TTC and ATC values of member Transmission Service Providers. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-003 | MOD-003-0 | No Parts for 2. |  |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-004 | MOD-004-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional CBM methodology. The Regional Reliability Organization’s CBM methodology shall include each of the following ten items, and shall explain its use in determining CBM value. Other items that are Regional Reliability Organization specific or that are considered in each respective Regional Reliability Organization methodology shall also be explained along with their use in determining CBM values. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.1. | Specify that the method used by each Regional Reliability Organization member to determine its generation reliability requirements as the basis for CBM shall be consistent with its generation planning criteria. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.10. | Describe the inclusion or exclusion rationale for generation reserve sharing arrangements in the CBM values. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.2. | Specify the frequency of calculation of the generation reliability requirement and associated CBM values. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.3. | Require that generation unit outages considered in a Transmission Service Provider’s CBM calculation be restricted to those units within the Transmission Service Provider’s system. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.4. | Require that CBM be preserved only on the Transmission Service Provider’s System where the Load-Serving Entity’s Load is located (i.e., CBM is an import quantity only). |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.5. | Describe the inclusion or exclusion rationale for generation resources of each Load-Serving Entity including those generation resources not directly connected to the Transmission Service Provider’s system but serving Load-Serving Entity loads connected to the Transmission Service Provider’s system. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.6. | Describe the inclusion or exclusion rationale for generation connected to the Transmission Service Provider’s system but not obligated to serve Native/Network Load connected to the Transmission Service Provider’s system. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.7. | Describe the formal process and rationale for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional Reliability Organization’s CBM methodology. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.8. | Specify the relationship of CBM to the generation reliability requirement and the allocation of the CBM values to the appropriate transmission facilities. The sum of the CBM values allocated to all interfaces shall not exceed that portion of the generation reliability requirement that is to be provided by outside resources. |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 1.9. | Describe the inclusion or exclusion rationale for the loads of each Load-Serving Entity, including interruptible demands and buy-through contracts (type of service contract that offers the customer the option to be interrupted or to accept a higher rate for service under certain conditions). |  | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | 2. | The Regional Reliability Organization shall make the most recent version of the documentation of its CBM methodology available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-004 | MOD-004-0 | No Parts for 2. |  |  | Long-Term Planning, Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-004 | MOD-004-1 | 1. | The Transmission Service Provider that maintains CBM shall prepare and keep current a “Capacity Benefit Margin Implementation Document” (CBMID) that includes, at a minimum, the following information: | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 1.1. | The process through which a Load-Serving Entity within a Balancing Authority Area associated with the Transmission Service Provider, or the Resource Planner associated with that Balancing Authority Area, may ensure that its need for Transmission capacity to be set aside as CBM will be reviewed and accommodated by the Transmission Service Provider to the extent Transmission capacity is available. | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 1.2. | The procedure and assumptions for establishing CBM for each Available Transfer Capability (ATC) Path or Flowgate. | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 1.3. | The procedure for a Load-Serving Entity or Balancing Authority to use Transmission capacity set aside as CBM, including the manner in which the Transmission Service Provider will manage situations where the requested use of CBM exceeds the amount of CBM available. | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 2. | The Transmission Service Provider that maintains CBM shall make available its current CBMID to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, Resource Planners, and Planning Coordinators that are within or adjacent to the Transmission Service Provider’s area, and to the Load Serving Entities and Balancing Authorities within the Transmission Service Provider’s area, and notify those entities of any changes to the CBMID prior to the effective date of the change. | M2. Each Transmission Service Provider that maintains CBM shall have evidence (such as dated logs and data, copies of dated electronic messages, or other equivalent evidence) to show that it made the current CBMID available to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, and Planning Coordinators specified in R2, and that prior to any change to the CBMID, it notified those entities of the change. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | No Parts for 2. |  | M2. Each Transmission Service Provider that maintains CBM shall have evidence (such as dated logs and data, copies of dated electronic messages, or other equivalent evidence) to show that it made the current CBMID available to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, and Planning Coordinators specified in R2, and that prior to any change to the CBMID, it notified those entities of the change. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000
Inactive | MOD | MOD-004 | MOD-004-1 | 3. | Each Load-Serving Entity determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: | M3. Each Load-Serving Entity that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R3. | Operations Planning, Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [9 empty] | LSE
Inactive | MOD | MOD-004 | MOD-004-1 | 3.1. | Using one or more of the following to determine the GCIR:  Loss of Load Expectation (LOLE) studies  Loss of Load Probability (LOLP) studies  Deterministic risk-analysis studies  Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | M3. Each Load-Serving Entity that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R3. | Operations Planning, Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [9 empty] | LSE
Inactive | MOD | MOD-004 | MOD-004-1 | 3.2. | Identifying expected import path(s) or source region(s). | M3. Each Load-Serving Entity that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R3. | Operations Planning, Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [9 empty] | LSE
Inactive | MOD | MOD-004 | MOD-004-1 | 4. | Each Resource Planner determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: | M4. Each Resource Planner that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R4. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [15 empty] | RP
Inactive | MOD | MOD-004 | MOD-004-1 | 4.1. | Using one or more of the following to determine the GCIR:  Loss of Load Expectation (LOLE) studies  Loss of Load Probability (LOLP) studies  Deterministic risk-analysis studies  Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | M4. Each Resource Planner that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R4. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [15 empty] | RP
Inactive | MOD | MOD-004 | MOD-004-1 | 4.2. | Identifying expected import path(s) or source region(s). | M4. Each Resource Planner that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R4. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [15 empty] | RP
Inactive | MOD | MOD-004 | MOD-004-1 | 5. | At least every 13 months, the Transmission Service Provider that maintains CBM shall establish a CBM value for each ATC Path or Flowgate to be used for ATC or Available Flowgate Capability (AFC) calculations during the 13 full calendar months (months 2-14) following the current month (the month in which the Transmission Service Provider is establishing the CBM values). This value shall: | M5. Each Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established 13 months of CBM values consistent with the requirements in R5.1 and allocated the values consistent with the requirements in R5.2. (Note that CBM values may legitimately be zero.) | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 5.1. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Service Provider’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Service Provider’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Service Provider’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | M5. Each Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established 13 months of CBM values consistent with the requirements in R5.1 and allocated the values consistent with the requirements in R5.2. (Note that CBM values may legitimately be zero.) | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 5.2. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Service Provider | M5. Each Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established 13 months of CBM values consistent with the requirements in R5.1 and allocated the values consistent with the requirements in R5.2. (Note that CBM values may legitimately be zero.) | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 6. | At least every 13 months, the Transmission Planner shall establish a CBM value for each ATC Path or Flowgate to be used in planning during each of the full calendar years two through ten following the current year (the year in which the Transmission Planner is establishing the CBM values). This value shall: | M6. Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established CBM values for years two through ten consistent with the requirements in R6.1 and allocated the values consistent with the requirements in R6.2. Inclusion of GCIR based on R6.1 and R6.2 within the transmission base case meets this requirement. (Note that CBM values may legitimately be zero.) | Long-Term Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP
Inactive | MOD | MOD-004 | MOD-004-1 | 6.1. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Planner’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Planner’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Planner’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | M6. Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established CBM values for years two through ten consistent with the requirements in R6.1 and allocated the values consistent with the requirements in R6.2. Inclusion of GCIR based on R6.1 and R6.2 within the transmission base case meets this requirement. (Note that CBM values may legitimately be zero.) | Long-Term Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP
Inactive | MOD | MOD-004 | MOD-004-1 | 6.2. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Planner. | M6. Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established CBM values for years two through ten consistent with the requirements in R6.1 and allocated the values consistent with the requirements in R6.2. Inclusion of GCIR based on R6.1 and R6.2 within the transmission base case meets this requirement. (Note that CBM values may legitimately be zero.) | Long-Term Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP
Inactive | MOD | MOD-004 | MOD-004-1 | 7. | Less than 31 calendar days after the establishment of CBM, the Transmission Service Provider that maintains CBM shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the Transmission Service Provider’s system of the amount of CBM set aside. | M7. Each Transmission Service Provider that maintains CBM shall provide evidence (such as dated e-mail, data, or other records) that it notified the entities described in R7 of the amount of CBM set aside. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | No Parts for 7. |  | M7. Each Transmission Service Provider that maintains CBM shall provide evidence (such as dated e-mail, data, or other records) that it notified the entities described in R7 of the amount of CBM set aside. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000
Inactive | MOD | MOD-004 | MOD-004-1 | 8. | Less than 31 calendar days after the establishment of CBM, the Transmission Planner shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the system being planned by the Transmission Planner of the amount of CBM set aside. | M8. Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as e-mail, data, or other records) that it notified the entities described in R8 of the amount of CBM set aside. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP
Inactive | MOD | MOD-004 | MOD-004-1 | No Parts for 8. |  | M8. Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as e-mail, data, or other records) that it notified the entities described in R8 of the amount of CBM set aside. | Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000
Inactive | MOD | MOD-004 | MOD-004-1 | 9. | The Transmission Service Provider that maintains CBM and the Transmission Planner shall each provide (subject to confidentiality and security requirements) copies of the applicable supporting data, including any models, used for determining CBM or allocating CBM over each ATC Path or Flowgate to the following: | M9. Each Transmission Service Provider that maintains CBM and each Transmission Planner shall provide evidence including copies of dated requests for data supporting the calculation of CBM along with other evidences such as copies of electronic messages or other evidence to show that it provided the required entities with copies of the supporting data, including any models, used for allocating CBM as specified in R9. | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 9.1. | Each of its associated Transmission Operators within 30 calendar days of their making a request for the data. | M9. Each Transmission Service Provider that maintains CBM and each Transmission Planner shall provide evidence including copies of dated requests for data supporting the calculation of CBM along with other evidences such as copies of electronic messages or other evidence to show that it provided the required entities with copies of the supporting data, including any models, used for allocating CBM as specified in R9. | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 9.2. | To any Transmission Service Provider, Reliability Coordinator, Transmission Planner, Resource Planner, or Planning Coordinator within 30 calendar days of their making a request for the data. | M9. Each Transmission Service Provider that maintains CBM and each Transmission Planner shall provide evidence including copies of dated requests for data supporting the calculation of CBM along with other evidences such as copies of electronic messages or other evidence to show that it provided the required entities with copies of the supporting data, including any models, used for allocating CBM as specified in R9. | Long-Term Planning, Operations Planning | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [21 empty] | TP | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 10. | The Load-Serving Entity or Balancing Authority shall request to import energy over firm Transfer Capability set aside as CBM only when experiencing a declared NERC Energy Emergency Alert (EEA) 2 or higher. | M10. Each Load-Serving Entity and Balancing Authority shall provide evidence (such as logs, copies of tag data, or other data from its Reliability Coordinator) that at the time it requested to import energy using firm Transfer Capability set aside as CBM, it was in an EEA 2 or higher. | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | BA | [8 empty] | LSE
Inactive | MOD | MOD-004 | MOD-004-1 | No Parts for 10. |  | M10. Each Load-Serving Entity and Balancing Authority shall provide evidence (such as logs, copies of tag data, or other data from its Reliability Coordinator) that at the time it requested to import energy using firm Transfer Capability set aside as CBM, it was in an EEA 2 or higher. | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000
Inactive | MOD | MOD-004 | MOD-004-1 | 11. | When reviewing an Arranged Interchange using CBM, all Balancing Authorities and Transmission Service Providers shall waive, within the bounds of reliable operation, any Real-time timing and ramping requirements. | M11. Each Balancing Authority and Transmission Service Provider shall provide evidence (such as operating logs and tag data) that it waived Real-time timing and ramping requirements when approving an Arranged Interchange using CBM | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | BA | [21 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | No Parts for 11. |  | M11. Each Balancing Authority and Transmission Service Provider shall provide evidence (such as operating logs and tag data) that it waived Real-time timing and ramping requirements when approving an Arranged Interchange using CBM | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000
Inactive | MOD | MOD-004 | MOD-004-1 | 12. | The Transmission Service Provider that maintains CBM shall approve, within the bounds of reliable operation, any Arranged Interchange using CBM that is submitted by an “energy deficient entity ” under an EEA 2 if: Footnote: See Attachment 1-EOP-002-0 for explanation. | M12. Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 12.1. | The CBM is available | M12. Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 12.2. | The EEA 2 is declared within the Balancing Authority Area of the “energy deficient entity,” and | M12. Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-004 | MOD-004-1 | 12.3. | The Load of the “energy deficient entity” is located within the Transmission Service Provider’s area. | M12. Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. | Same-Day Operations | 2008-11-13 | 2008-11-21 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM05-17-000, RM05-25-000 | [22 empty] | TSP
Inactive | MOD | MOD-005 | MOD-005-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and implement a procedure to review (at least annually) the CBM calculations and the resulting values of member Transmission Service Providers to ensure that they comply with the Regional Reliability Organization’s CBM methodology. The procedure shall include the following four requirements: |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | 1.1. | Indicate the frequency under which the verification review shall be implemented. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | 1.2. | Require review of the process by which CBM values are updated, and their frequency of update, to ensure that the most current CBM values are available to transmission users. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | 1.3. | Require review of the consistency of the Transmission Service Provider’s CBM components with its published planning criteria. A CBM value is considered consistent with published planning criteria if the components that comprise CBM are addressed in the planning criteria. The methodology used to determine and apply CBM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumptions explained. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | 1.4. | Require CBM values to be periodically updated (at least annually) and available to the Regional Reliability Organizations, NERC, and transmission users. |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | 2. | Each Regional Reliability Organization shall document its CBM procedure and shall make its CBM review procedure available to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-005 | MOD-005-0 | 3. | The Regional Reliability Organization shall provide documentation of the results of the most current implementation of its CBM review procedure to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-005 | MOD-005-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-006 | MOD-006-0 | 1. | Each Transmission Service Provider shall document its procedure on the use of Capacity Benefit Margin (CBM) (scheduling of energy against a CBM reservation). The procedure shall include the following three components: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0 | 1.1. | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0 | 1.2. | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0 | 1.3. | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0 | 2. | Each Transmission Service Provider shall make its CBM use procedure available on a web site accessible by the Regional Reliability Organizations, NERC, and transmission users. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-006 | MOD-006-0.1 | 1. | Each Transmission Service Provider shall document its procedure on the use of Capacity Benefit Margin (CBM) (scheduling of energy against a CBM reservation). The procedure shall include the following three components: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0.1 | 1.1. | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0.1 | 1.2. | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0.1 | 1.3. | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0.1 | 2. | Each Transmission Service Provider shall make its CBM use procedure available on a web site accessible by the Regional Reliability Organizations, NERC, and transmission users. |  | Operations Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | [22 empty] | TSP
Inactive | MOD | MOD-006 | MOD-006-0.1 | No Parts for 2. |  |  | Operations Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | MOD | MOD-007 | MOD-007-0 | 1. | Each Transmission Service Provider that uses CBM shall report (to the Regional Reliability Organization, NERC and the transmission users) the use of CBM by the Load-Serving Entities’ Loads on its system, except for CBM sales as Non-Firm Transmission Service. (This use of CBM shall be consistent with the Transmission Service Provider’s procedure for use of CBM.) |  | Operations Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-007 | MOD-007-0 | No Parts for 1. |  |  | Operations Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-007 | MOD-007-0 | 2. | The Transmission Service Provider shall post the following three items within 15 calendar days after the use of CBM for an Energy Emergency. This posting shall be on a web site accessible by the Regional Reliability Organizations, NERC, and transmission users. |  | Operations Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-007 | MOD-007-0 | 2.1. | Circumstances. |  | Operations Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-007 | MOD-007-0 | 2.2. | Duration. |  | Operations Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-007 | MOD-007-0 | 2.3. | Amount of CBM used. |  | Operations Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | MOD | MOD-008 | MOD-008-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional TRM methodology. The Region’s TRM methodology shall specify or describe each of the following five items, and shall explain its use, if any, in determining TRM values. Other items that are Region-specific or that are considered in each respective Regional methodology shall also be explained along with their use in determining TRM values. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.1. | Specify the update frequency of TRM calculations. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.2. | Specify how TRM values are incorporated into Available Transfer Capability calculations. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3. | Specify the uncertainties accounted for in TRM and the methods used to determine their impacts on the TRM values. Any component of uncertainty, other than those identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, shall benefit the interconnected transmission systems as a whole before they shall be permitted to be included in TRM calculations. The components of uncertainty identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, if applied, shall be accounted for solely in TRM and not CBM. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.1. | Aggregate Load forecast error (not included in determining generation reliability requirements). | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.2. | Load distribution error. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.3. | Variations in facility Loadings due to balancing of generation within a Balancing Authority Area. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.4. | Forecast uncertainty in transmission system topology. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.5. | Allowances for parallel path (loop flow) impacts. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.6. | Allowances for simultaneous path interactions. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.7. | Variations in generation dispatch. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.3.8. | Short-term System Operator response (Operating Reserve actions not exceeding a 59-minute window). | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.4. | Describe the conditions, if any, under which TRM may be available to the market as Non-Firm Transmission Service. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 1.5. | Describe the formal process for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional TRM methodology. | The Regional Reliability Organization’s most recent version of the documentation of its TRM methodology is available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | Operations Planning | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | 2. | The Regional Reliability Organization shall make its most recent version of the documentation of its TRM methodology available on a web site accessible by NERC, the Regional Reliability Organizations, and transmission users. | The Regional Reliability Organization’s most recent version of the documentation of its TRM contains all items in Reliability Standard MOD-008-0_R1. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-008 | MOD-008-0 | No Parts for 2. |  | The Regional Reliability Organization’s most recent version of the documentation of its TRM contains all items in Reliability Standard MOD-008-0_R1. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-008 | MOD-008-1 | 1. | Each Transmission Operator shall prepare and keep current a TRM Implementation Document (TRMID) that includes, as a minimum, the following information: | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 1.1. | Identification of (on each of its respective ATC Paths or Flowgates) each of the following components of uncertainty if used in establishing TRM, and a description of how that component is used to establish a TRM value: Aggregate Load forecast.; Load distribution uncertainty.; Forecast uncertainty in Transmission system topology (including, but not limited to, forced or unplanned outages and maintenance outages).; Allowances for parallel path (loop flow) impacts.; Allowances for simultaneous path interactions.; Variations in generation dispatch (including, but not limited to, forced or unplanned outages, maintenance outages and location of future generation).; Short-term System Operator response (Operating Reserve actions ).; Reserve sharing requirements.; Inertial response and frequency bias. | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 1.2. | The description of the method used to allocate TRM across ATC Paths or Flowgates. | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 1.3. | The identification of the TRM calculation used for the following time periods: | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 1.3.1. | Same day and real-time. | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 1.3.2. | Day-ahead and pre-schedule. | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 1.3.3. | Beyond day-ahead and pre-schedule, up to thirteen months ahead. | M1. Each Transmission Operator shall produce its TRMID evidencing inclusion of all specified information in R1. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | 2. | Each Transmission Operator shall only use the components of uncertainty from R1.1 to establish TRM, and shall not include any of the components of Capacity Benefit Margin (CBM). Transmission capacity set aside for reserve sharing agreements can be included in TRM. | M2. Each Transmission Operator shall provide evidence including its TRMID, TRM values, CBM values, or other evidence, (such as written documentation, study reports, documentation of its CBM process, and supporting information) to demonstrate that its TRM values did not include any elements of uncertainty beyond those defined in R1.1 and to show that it did not include any of the components of CBM. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | No Parts for 2. |  | M2. Each Transmission Operator shall provide evidence including its TRMID, TRM values, CBM values, or other evidence, (such as written documentation, study reports, documentation of its CBM process, and supporting information) to demonstrate that its TRM values did not include any elements of uncertainty beyond those defined in R1.1 and to show that it did not include any of the components of CBM. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-008 | MOD-008-1 | 3. | Each Transmission Operator shall make available its TRMID, and if requested, underlying documentation (if any) used to determine TRM, in the format used by the Transmission Operator, to any of the following who make a written request no more than 30 calendar days after receiving the request. [Time Horizon: Operations Planning] Transmission Service Providers, Reliability Coordinators, Planning Coordinators, Transmission Planner, Transmission Operators | M3. Each Transmission Operator shall provide a dated copy of any request from an entity described in R3. The Transmission Operator shall also provide evidence (such as copies of emails or postal receipts that show the recipient, date and contents) that the requested documentation (such as work papers and load flow cases) was made available within the specified timeframe to the requestor. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | No Parts for 3. |  | M3. Each Transmission Operator shall provide a dated copy of any request from an entity described in R3. The Transmission Operator shall also provide evidence (such as copies of emails or postal receipts that show the recipient, date and contents) that the requested documentation (such as work papers and load flow cases) was made available within the specified timeframe to the requestor. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-008 | MOD-008-1 | 4. | Each Transmission Operator that maintains TRM shall establish TRM values in accordance with the TRMID at least once every 13 months. [Time Horizon: Operations Planning] | M4. Each Transmission Operator shall provide evidence (such as logs, study report, review notes, or data) that it established TRM values at least once every thirteen months for each of the TRM time periods. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | No Parts for 4. |  | M4. Each Transmission Operator shall provide evidence (such as logs, study report, review notes, or data) that it established TRM values at least once every thirteen months for each of the TRM time periods. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-008 | MOD-008-1 | 5. | The Transmission Operator that maintains TRM shall provide the TRM values to its Transmission Service Provider(s) and Transmission Planner(s) no more than seven calendar days after a TRM value is initially established or subsequently changed. [Time Horizon: Operations Planning] | M5. Each Transmission Operator shall provide evidence (such as logs, email, website postings) that it provided their Transmission Service Provider(s) and Transmission Planner(s) with the updated TRM value as described in R5. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-008 | MOD-008-1 | No Parts for 5. |  | M5. Each Transmission Operator shall provide evidence (such as logs, email, website postings) that it provided their Transmission Service Provider(s) and Transmission Planner(s) with the updated TRM value as described in R5. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-009 | MOD-009-0 | 1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and implement a procedure to review Transmission Reliability Margin (TRM) calculations and resulting values of member Transmission Service Providers to ensure they comply with the Regional TRM methodology, and are periodically updated and available to transmission users. This procedure shall include the following four required elements: | The Regional Reliability Organization shall have evidence that it provided to NERC upon request (within 30 calendar days) a copy of its written procedure developed for the performance of periodic reviews of Regional TRM calculations. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | 1.1. | Indicate the frequency under which the verification review shall be implemented. | The Regional Reliability Organization shall have evidence that it provided to NERC upon request (within 30 calendar days) a copy of its written procedure developed for the performance of periodic reviews of Regional TRM calculations. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | 1.2. | Require review of the process by which TRM values are updated, and their frequency of update, to ensure that the most current TRM values are available to transmission users. | The Regional Reliability Organization shall have evidence that it provided to NERC upon request (within 30 calendar days) a copy of its written procedure developed for the performance of periodic reviews of Regional TRM calculations. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | 1.3. | Require review of the consistency of the Transmission Service Provider’s TRM components with its published planning criteria. A TRM value is considered consistent with published planning criteria if the same components that comprise TRM are also addressed in the planning criteria. The methodology used to determine and apply TRM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumption explained. | The Regional Reliability Organization shall have evidence that it provided to NERC upon request (within 30 calendar days) a copy of its written procedure developed for the performance of periodic reviews of Regional TRM calculations. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | 1.4. | Require TRM values to be periodically updated (at least prior to each season — winter, spring, summer, and fall), as necessary, and made available to the Regional Reliability Organizations, NERC, and transmission users. | The Regional Reliability Organization shall have evidence that it provided to NERC upon request (within 30 calendar days) a copy of its written procedure developed for the performance of periodic reviews of Regional TRM calculations. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | 2. | The Regional Reliability Organization shall make documentation of its Regional TRM review procedure available to NERC on request (within 30 calendar days). | The Regional Reliability Organization shall have evidence it provided to NERC on request (within 30 calendar days) documentation of the results of the most current implementation of its TRM review procedure. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | No Parts for 2. |  | The Regional Reliability Organization shall have evidence it provided to NERC on request (within 30 calendar days) documentation of the results of the most current implementation of its TRM review procedure. |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-009 | MOD-009-0 | 3. | The Regional Reliability Organization shall make documentation of the results of the most current implementation of its TRM review procedure available to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [16 empty] | RRO
Inactive | MOD | MOD-009 | MOD-009-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2009-11-24 | Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-010 | MOD-010-0 | 1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide appropriate equipment characteristics, system data, and existing and future Interchange Schedules in compliance with its respective Interconnection Regional steady-state modeling and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-011-0_R1. | M1. The Transmission Owner, Transmission Planner, Generator Owner, and Resource Planner, (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall have evidence that it provided equipment characteristics, system data, and Interchange Schedules for steady-state modeling and simulation to the Regional Reliability Organizations and NERC as specified in Standard MOD-010-0_R1 and MOD-010-0_R2. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [10 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-010 | MOD-010-0 | No Parts for 1. |  | M1. The Transmission Owner, Transmission Planner, Generator Owner, and Resource Planner, (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall have evidence that it provided equipment characteristics, system data, and Interchange Schedules for steady-state modeling and simulation to the Regional Reliability Organizations and NERC as specified in Standard MOD-010-0_R1 and MOD-010-0_R2. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-010 | MOD-010-0 | 2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide this steady-state modeling and simulation data to the Regional Reliability Organizations, NERC, and those entities specified within Reliability Standard MOD-011-0_R1. If no schedule exists, then these entities shall provide the data on request (30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [10 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-010 | MOD-010-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-011 | MOD-011-0 | 1. | The Regional Reliability Organizations within an Interconnection, in conjunction with the Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners, shall develop comprehensive steady-state data requirements and reporting procedures needed to model and analyze the steady-state conditions for each of the NERC Interconnections: Eastern, Western, and ERCOT. Within an Interconnection, the Regional Reliability Organizations shall jointly coordinate the development of the data requirements and reporting procedures for that Interconnection. The Interconnection-wide requirements shall include the following steady-state data requirements: | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.1. | Bus (substation): name, nominal voltage, electrical demand supplied (consistent with the aggregated and dispersed substation demand data supplied per Reliability Standards MOD-016-0, MOD-017-0, and MOD-020-0 ), and location. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.2. | Generating Units (including synchronous condensers, pumped storage, etc.): location, minimum and maximum Ratings (net Real and Reactive Power), regulated bus and voltage set point, and equipment status. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.3. | AC Transmission Line or Circuit (overhead and underground): nominal voltage, impedance, line charging, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0 ) equipment status, and metering locations. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.4. | DC Transmission Line (overhead and underground): line parameters, Normal and Emergency Ratings, control parameters, rectifier data, and inverter data. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.5. | Transformer (voltage and phase-shifting): nominal voltages of windings, impedance, tap ratios (voltage and/or phase angle or tap step size), regulated bus and voltage set point, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0.), and equipment status. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.6. | Reactive Compensation (shunt and series capacitors and reactors): nominal Ratings, impedance, percent compensation, connection point, and controller device. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 1.7. | Interchange Schedules: Existing and future Interchange Schedules and/or assumptions. | M1. The Regional Reliability Organization shall have documentation of its Interconnection’s steady-state data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-011-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | 2. | The Regional Reliability Organizations within an Interconnection shall document their Interconnection’s steady-state data requirements and reporting procedures, shall review those data requirements and reporting procedures (at least every five years), and shall make the data requirements and reporting procedures available on request (within five business days) to Regional Reliability Organizations, NERC, and all users of the interconnected transmission systems. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-011 | MOD-011-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-012 | MOD-012-0 | 1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide appropriate equipment characteristics and system data in compliance with the respective Interconnection-wide Regional dynamics system modeling and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-013-0_R1. | M1. The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall each have evidence that it provided equipment characteristics and system data for dynamics system modeling and simulation in accordance with Reliability Standard MOD-012-0_R1 and Reliability Standard MOD-012-0_R2. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [10 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-012 | MOD-012-0 | No Parts for 1. |  | M1. The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall each have evidence that it provided equipment characteristics and system data for dynamics system modeling and simulation in accordance with Reliability Standard MOD-012-0_R1 and Reliability Standard MOD-012-0_R2. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-012 | MOD-012-0 | 2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide dynamics system modeling and simulation data to its Regional Reliability Organization(s), NERC, and those entities specified within the applicable reporting procedures identified in Reliability Standard MOD-013-0_R1. If no schedule exists, then these entities shall provide data on request (30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [10 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-012 | MOD-012-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-013 | MOD-013-0 | 1. | The Regional Reliability Organization, in coordination with its Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners, shall develop comprehensive dynamics data requirements and reporting procedures needed to model and analyze the dynamic behavior or response of each of the NERC Interconnections: Eastern, Western, and ERCOT. Within an Interconnection, the Regional Reliability Organizations shall jointly coordinate on the development of the data requirements and reporting procedures for that Interconnection. Each set of Interconnection-wide dynamics data requirements shall include the following dynamics data requirements: | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 1.1. | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 1.1.1. | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 1.1.2. | The Interconnection-wide requirements shall specify unit size thresholds for permitting: − The use of non-detailed vs. detailed models, − The netting of small generating units with bus load, and − The combining of multiple generating units at one plant. | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 1.2. | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 1.3. | Dynamics data representing electrical demand characteristics as a function of frequency and voltage. | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 1.4. | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010-0_R1. | The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Reliability Standard MOD-013-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | 2. | The Regional Reliability Organization shall participate in the documentation of its Interconnection’s data requirements and reporting procedures and, shall participate in the review of those data requirements and reporting procedures (at least every five years), and shall provide those data requirements and reporting procedures to Regional Reliability Organizations, NERC, and all users of the Interconnected systems on request (within five business days). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-11-02 | Filing/Order Docket No. RM06-16-000 MOD-013-0 was never enforceable
Inactive | MOD | MOD-013 | MOD-013-1 | 1. | The Regional Reliability Organization, in coordination with its Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners, shall develop comprehensive dynamics data requirements and reporting procedures needed to model and analyze the dynamic behavior or response of each of the NERC Interconnections: Eastern, Western, and ERCOT. Within an Interconnection, the Regional Reliability Organizations shall jointly coordinate on the development of the data requirements and reporting procedures for that Interconnection. Each set of Interconnection-wide dynamics data requirements shall include the following dynamics data requirements: | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.1. | Design data shall be provided for new or refurbished excitation systems (for synchronous generators and synchronous condensers) at least three months prior to the installation date. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.1.1. | If design data is unavailable from the manufacturer 3 months prior to the installation date, estimated or typical manufacturer’s data, based on excitation systems of similar design and characteristics, shall be provided. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.2. | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.2.1. | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.2.2. | The Interconnection-wide requirements shall specify unit size thresholds for permitting: The use of non-detailed vs. detailed models, The netting of small generating units with bus load, and The combining of multiple generating units at one plant. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.3. | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.4. | Dynamics data representing electrical Demand characteristics as a function of frequency and voltage. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 1.5. | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010 Requirement 1. | M1. The Regional Reliability Organizations within each Interconnection shall have documentation of their Interconnection’s dynamics data requirements and reporting procedures and shall provide the documentation as specified in Requirement 2. |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | 2. | The Regional Reliability Organization shall participate in the documentation of its Interconnection’s data requirements and reporting procedures and, shall participate in the review of those data requirements and reporting procedures (at least every five years), and shall provide those data requirements and reporting procedures to Regional Reliability Organizations, NERC, and all users of the Interconnected systems on request (within five business days). |  |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-013 | MOD-013-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | MOD | MOD-014 | MOD-014-0 | 1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of solved (converged) Interconnection-specific steadystate system models. The Interconnection-specific models shall include near- and longer-term planning horizons that are representative of system conditions for projected seasonal peak, minimum, and other appropriate system demand levels. | M1. Each Regional Reliability Organization shall have Interconnection-specific steady-state system models as specified in MOD-014-0_R1 and MOD-014-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-014 | MOD-014-0 | No Parts for 1. |  | M1. Each Regional Reliability Organization shall have Interconnection-specific steady-state system models as specified in MOD-014-0_R1 and MOD-014-0_R2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-014 | MOD-014-0 | 2. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop steady-state system models annually for selected study years, as determined by the Regional Reliability Organizations within its Interconnection. The Regional Reliability Organization shall provide the most recent solved (converged) Interconnection-specific steadystate models to NERC in accordance with each Interconnection’s schedule for submission. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-014 | MOD-014-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-015 | MOD-015-0 | 1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of initialized (with no Faults or system Disturbances) Interconnection-specific dynamics system models linked to the steadystate system models, as appropriate, of Reliability Standard MOD-014-0_R1. | M1. The Regional Reliability Organization shall have Interconnection-specific dynamics system models in accordance with Reliability Standard MOD-015-0 Requirement 1 and MOD-015-0 Requirement 2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-015 | MOD-015-0 | 1.1. | The Regional Reliability Organization(s) shall develop Interconnectionspecific dynamics system models for at least two timeframes (present or nearterm model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. | M1. The Regional Reliability Organization shall have Interconnection-specific dynamics system models in accordance with Reliability Standard MOD-015-0 Requirement 1 and MOD-015-0 Requirement 2. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-015 | MOD-015-0 | 2. | The Regional Reliability Organization(s) within each Interconnection shall develop Interconnection dynamics system models for their Interconnection annually for selected study years as determined by the Regional Reliability Organization(s) within each Interconnection and shall provide the most recent initialized (approximately 25 seconds, no-fault) models to NERC in accordance with each Interconnection’s schedule for submission. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-015 | MOD-015-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-015 | MOD-015-0.1 | 1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of initialized (with no Faults or system Disturbances) Interconnection-specific dynamics system models linked to the steadystate system models, as appropriate, of Reliability Standard MOD-014-0_R1. | M1. The Regional Reliability Organization shall have Interconnection-specific dynamics system models in accordance with Reliability Standard MOD-015-0 Requirement 1 and MOD-015-0 Requirement 2. |  | 2008-10-29 | [8 empty] | 2016-06-30 | This standard was not approved by FERC in Order 693. MOD-015-0.1 retires midnight of the day immediately prior to the Effective Date of MOD-032-1, Requirement R2, in the particular Jurisdiction in which the new standard is becomin | [16 empty] | RRO
Inactive | MOD | MOD-015 | MOD-015-0.1 | 1.1. | The Regional Reliability Organization(s) shall develop Interconnection specific dynamics system models for at least two timeframes (present or near-term model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. | M1. The Regional Reliability Organization shall have Interconnection-specific dynamics system models in accordance with Reliability Standard MOD-015-0 Requirement 1 and MOD-015-0 Requirement 2. |  | 2008-10-29 | [8 empty] | 2016-06-30 | This standard was not approved by FERC in Order 693. MOD-015-0.1 retires midnight of the day immediately prior to the Effective Date of MOD-032-1, Requirement R2, in the particular Jurisdiction in which the new standard is becomin | [16 empty] | RRO
Inactive | MOD | MOD-015 | MOD-015-0.1 | 2. | The Regional Reliability Organization(s) within each Interconnection shall develop Interconnection dynamics system models for their Interconnection annually for selected study years as determined by the Regional Reliability Organization(s) within each Interconnection and shall provide the most recent initialized (approximately 25 seconds, no-fault) models to NERC in accordance with each Interconnection’s schedule for submission. |  |  | 2008-10-29 | [8 empty] | 2016-06-30 | This standard was not approved by FERC in Order 693. MOD-015-0.1 retires midnight of the day immediately prior to the Effective Date of MOD-032-1, Requirement R2, in the particular Jurisdiction in which the new standard is becomin | [16 empty] | RRO
Inactive | MOD | MOD-015 | MOD-015-0.1 | No Parts for 2. |  |  |  | 2008-10-29 | [8 empty] | 2016-06-30 | This standard was not approved by FERC in Order 693. MOD-015-0.1 retires midnight of the day immediately prior to the Effective Date of MOD-032-1, Requirement R2, in the particular Jurisdiction in which the new standard is becomin
Inactive | MOD | MOD-016 | MOD-016-0 | 1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. |  |  | 2005-02-08 | [8 empty] | 2006-11-02 | Replaced with MOD-013-1 (MOD-016-0 was never enforceable) | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-0 | 1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005-0, TPL-006-0, MOD-010-0, MOD011-0, MOD-012-0, MOD-013-0, MOD-014-0, MOD-015-0, MOD-016, MOD-017- 0, MOD-018-0, MOD-019-0, MOD-020-0, and MOD-021-0. |  |  | 2005-02-08 | [8 empty] | 2006-11-02 | Replaced with MOD-013-1 (MOD-016-0 was never enforceable) | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-0 | 2. | The documentation of the scope and details of the data reporting requirements shall be available on request (five business days). |  |  | 2005-02-08 | [8 empty] | 2006-11-02 | Replaced with MOD-013-1 (MOD-016-0 was never enforceable) | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-02 | Replaced with MOD-013-1 (MOD-016-0 was never enforceable)
Inactive | MOD | MOD-016 | MOD-016-1 | 1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-1 | 1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-1 | 2. | The Regional Reliability Organization shall distribute its documentation required in Requirement 1 and any changes to that documentation, to all Planning Authorities that work within its Region. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-016 | MOD-016-1 | 2.1. | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [16 empty] | RRO
Inactive | MOD | MOD-016 | MOD-016-1 | 3. | The Planning Authority shall distribute its documentation required in R1 for reporting customer data and any changes to that documentation, to its Transmission Planners and Load-Serving Entities that work within its Planning Authority Area. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-016 | MOD-016-1 | 3.1. | The Planning Authority shall make this distribution within 30 calendar days of approval. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-016 | MOD-016-1.1 | 1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. | M1. The Planning Authority and Regional Reliability Organization’s documentation for actual and forecast customer data shall contain all items identified in R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-1.1 | 1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. | M1. The Planning Authority and Regional Reliability Organization’s documentation for actual and forecast customer data shall contain all items identified in R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC |  |  |  |  | RRO
Inactive | MOD | MOD-016 | MOD-016-1.1 | 2. | The Regional Reliability Organization shall distribute its documentation required in Requirement 1 and any changes to that documentation, to all Planning Authorities that work within its Region. | M2. The Regional Reliability Organization shall have evidence it provided its actual and forecast customer data reporting requirements as required in Requirement 2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [16 empty] | RRO
Inactive | MOD | MOD-016 | MOD-016-1.1 | 2.1. | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. | M2. The Regional Reliability Organization shall have evidence it provided its actual and forecast customer data reporting requirements as required in Requirement 2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [16 empty] | RRO
Inactive | MOD | MOD-016 | MOD-016-1.1 | 3. | The Planning Authority shall distribute its documentation required in R1 for reporting customer data and any changes to that documentation, to its Transmission Planners and Load-Serving Entities that work within its Planning Authority Area. | M3. The Planning Authority shall have evidence it provided its actual and forecast customer data and reporting requirements as required in Requirement 3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-016 | MOD-016-1.1 | 3.1. | The Planning Authority shall make this distribution within 30 calendar days of approval. | M3. The Planning Authority shall have evidence it provided its actual and forecast customer data and reporting requirements as required in Requirement 3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-017 | MOD-017-0 | 1. | The Load-Serving Entity, Planning Authority, and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R 1. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0 | 1.1. | Integrated hourly demands in megawatts (MW) for the prior year. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0 | 1.2. | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0 | 1.3. | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0 | 1.4. | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0.1 | 1. | The Load-Serving Entity, Planning Authority and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R1. | M1. Load-Serving Entity, Planning Authority, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided load data per Standard MOD-017-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0.1 | 1.1. | Integrated hourly demands in megawatts (MW) for the prior year. | M1. Load-Serving Entity, Planning Authority, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided load data per Standard MOD-017-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0.1 | 1.2. | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. | M1. Load-Serving Entity, Planning Authority, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided load data per Standard MOD-017-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0.1 | 1.3. | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. | M1. Load-Serving Entity, Planning Authority, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided load data per Standard MOD-017-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-017 | MOD-017-0.1 | 1.4. | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. | M1. Load-Serving Entity, Planning Authority, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided load data per Standard MOD-017-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE | PA | PC |  |  |  | RP
Inactive | MOD | MOD-018 | MOD-018-0 | 1. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner’s report of actual and forecast demand data (reported on either an aggregated or dispersed basis) shall: | M1. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide evidence to its Compliance Monitor that its actual and forecast demand data were addressed as described in the reporting procedures developed for Reliability Standard MOD-018-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-018 | MOD-018-0 | 1.1. | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and | M1. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide evidence to its Compliance Monitor that its actual and forecast demand data were addressed as described in the reporting procedures developed for Reliability Standard MOD-018-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-018 | MOD-018-0 | 1.2. | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. | M1. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide evidence to its Compliance Monitor that its actual and forecast demand data were addressed as described in the reporting procedures developed for Reliability Standard MOD-018-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-018 | MOD-018-0 | 1.3. | Items (MOD-018-0_R 1.1) and (MOD-018-0_R 1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-1_R 1. | M1. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide evidence to its Compliance Monitor that its actual and forecast demand data were addressed as described in the reporting procedures developed for Reliability Standard MOD-018-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-018 | MOD-018-0 | 2. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each report data associated with Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). | M2. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each report current information for Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-018 | MOD-018-0 | No Parts for 2. |  | M2. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each report current information for Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-019 | MOD-019-0 | 1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R 1. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-019 | MOD-019-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-019 | MOD-019-0.1 | 1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R1. | M1. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided forecasts of interruptible demands and DCLM data per Reliability Standard MOD-019-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-019 | MOD-019-0.1 | No Parts for 1. |  | M1. The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide evidence to its Compliance Monitor that it provided forecasts of interruptible demands and DCLM data per Reliability Standard MOD-019-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000
Inactive | MOD | MOD-020 | MOD-020-0 | 1. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | M1. The Load-Serving Entity, Transmission Planner, and Resource Planner each make known its amount of interruptible demands and DCLM to Transmission Operators, Balancing Authorities and Reliability Coordinators on request within 30 calendar days. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-020 | MOD-020-0 | No Parts for 1. |  | M1. The Load-Serving Entity, Transmission Planner, and Resource Planner each make known its amount of interruptible demands and DCLM to Transmission Operators, Balancing Authorities and Reliability Coordinators on request within 30 calendar days. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-021 | MOD-021-0 | 1. | The Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-021 | MOD-021-0 | 2. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R 1. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-021 | MOD-021-0 | 3. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-021 | MOD-021-0.1 | 1. | The Load-Serving Entity, Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-9-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-0.1 | No Parts for 1. |  |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-9-000
Inactive | MOD | MOD-021 | MOD-021-0.1 | 2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-9-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-0.1 | No Parts for 2. |  |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-9-000
Inactive | MOD | MOD-021 | MOD-021-0.1 | 3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-9-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-0.1 | No Parts for 3. |  |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-9-000
Inactive | MOD | MOD-021 | MOD-021-1 | 1. | The Load-Serving Entity, Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | M1. The Load-Serving Entity, Transmission Planner and Resource Planner forecasts clearly document how the demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible demands, and Direct Control Load Management) are addressed. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-15-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-1 | No Parts for 1. |  | M1. The Load-Serving Entity, Transmission Planner and Resource Planner forecasts clearly document how the demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible demands, and Direct Control Load Management) are addressed. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-15-000
Inactive | MOD | MOD-021 | MOD-021-1 | 2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | M2. The Load-Serving Entity, Transmission Planner and Resource Planner information detailing how Demand-Side Management measures are addressed in the forecasts of Peak Demand and annual Net Energy for Load are included in the data reporting procedures of Reliability Standard MOD-016-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-15-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-1 | No Parts for 2. |  | M2. The Load-Serving Entity, Transmission Planner and Resource Planner information detailing how Demand-Side Management measures are addressed in the forecasts of Peak Demand and annual Net Energy for Load are included in the data reporting procedures of Reliability Standard MOD-016-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-15-000
Inactive | MOD | MOD-021 | MOD-021-1 | 3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | M3. The Load-Serving Entity, Planning Authority and Resource Planner shall each provide evidence to its Compliance Monitor that it provided documentation on the treatment of DSM programs to NERC as requested (within 30 calendar days). |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-15-000 | [9 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021 | MOD-021-1 | No Parts for 3. |  | M3. The Load-Serving Entity, Planning Authority and Resource Planner shall each provide evidence to its Compliance Monitor that it provided documentation on the treatment of DSM programs to NERC as requested (within 30 calendar days). |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-15-000
Inactive | MOD | MOD-024 | MOD-024-1 | 1. | The Regional Reliability Organization shall establish and maintain procedures to address verification of generator gross and net Real Power capability. These procedures shall include the following: | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.1. | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.2. | Criteria for reporting generating unit auxiliary loads. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.3. | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of manufacturer data, commissioning data, performance tracking, and testing, etc. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.4. | Periodicity and schedule of model and data verification and reporting. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.5. | Information to be verified and reported: | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.5.1. | Seasonal gross and net Real Power generating capabilities. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.5.2. | Real power requirements of auxiliary loads. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 1.5.3. | Method of verification, including date and conditions. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Real Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | 2. | The Regional Reliability Organization shall provide its generator gross and net Real Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. | M2. The Regional Reliability Organization shall have evidence that its procedures, and any revisions to those procedures, for verification and reporting of generator gross and net Real Power capability were provided to affected Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners within 30 calendar days of approval. | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-024 | MOD-024-1 | No Parts for 2. |  | M2. The Regional Reliability Organization shall have evidence that its procedures, and any revisions to those procedures, for verification and reporting of generator gross and net Real Power capability were provided to affected Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners within 30 calendar days of approval. | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-024 | MOD-024-1 | 3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Real Power generating capability per R1. | The Generator Owner shall have evidence it provided verified information of its generator gross and net Real Power capability, consistent with that Regional Reliability Organization’s procedures. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-024 | MOD-024-1 | No Parts for 3. |  | The Generator Owner shall have evidence it provided verified information of its generator gross and net Real Power capability, consistent with that Regional Reliability Organization’s procedures. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-025 | MOD-025-1 | 1. | The Regional Reliability Organization shall establish and maintain procedures to address verification of generator gross and net Reactive Power capability. These procedures shall include the following: | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.1. | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.2. | Criteria for reporting generating unit auxiliary loads. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.3. | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of commissioning data, performance tracking, engineering analysis, testing, etc. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.4. | Periodicity and schedule of model and data verification and reporting. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.5. | Information to be reported: | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.5.1. | Verified maximum gross and net Reactive Power capability (both lagging and leading) at Seasonal Real Power generating capabilities as reported in accordance with Reliability Standard MOD-024 Requirement 1.5.1. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.5.2. | Verified Reactive Power limitations, such as generator terminal voltage limitations, shorted rotor turns, etc. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.5.3. | Verified Reactive Power of auxiliary loads. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 1.5.4. | Method of verification, including date and conditions. | M1. The Regional Reliability Organization shall have available for inspection the procedures for the verification and reporting of generator gross and net Reactive Power capability in accordance with R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | 2. | The Regional Reliability Organization shall provide its generator gross and net Reactive Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. | The Regional Reliability Organization shall have evidence that its procedures, and any revisions to these procedures, for verification and reporting of generator gross and net Reactive Power capability were provided to affected Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners within 30 calendar days of approval. | Operations Planning | 2006-02-07 | 2006-04-04 | [5 empty] | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | MOD | MOD-025 | MOD-025-1 | No Parts for 2. |  | The Regional Reliability Organization shall have evidence that its procedures, and any revisions to these procedures, for verification and reporting of generator gross and net Reactive Power capability were provided to affected Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners within 30 calendar days of approval. | Operations Planning | 2006-02-07 | 2006-04-04 | [5 empty] | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | MOD | MOD-025 | MOD-025-1 | 3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Reactive Power generating capability per R1. | The Generator Owner shall have evidence it provided verified information of its generator gross and net Reactive Power capability, consistent with that Regional Reliability Organization’s procedures. | Operations Planning | 2006-02-07 | 2006-04-04 | [5 empty] | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-025 | MOD-025-1 | No Parts for 3. |  | The Generator Owner shall have evidence it provided verified information of its generator gross and net Reactive Power capability, consistent with that Regional Reliability Organization’s procedures. | Operations Planning | 2006-02-07 | 2006-04-04 | [5 empty] | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 1. | Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. |  |  |  |  | GO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 1.1 . | Verify the Real Power capability of its generating units in accordance with Attachment 1. | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2016-07-01 |  | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. |  |  |  |  | GO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 1.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2014-05-27 |  | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. |  |  |  |  | GO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 2. | Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: | M2. Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information, or dated information collected and used to complete attachments and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. |  |  |  |  | GO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 2.1 . | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. | M2. Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information, or dated information collected and used to complete attachments and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. |  |  |  |  | GO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 2.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | M2. Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information, or dated information collected and used to complete attachments and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2014-05-27 |  |  |  |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. |  |  |  |  | GO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 3. | Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: | Each Transmission Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Transmission Owner form with equivalent information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. | [19 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 3.1. | Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. | Each Transmission Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Transmission Owner form with equivalent information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2016-07-01 |  | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. | [19 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-025 | MOD-025-2 | 3.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Each Transmission Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Transmission Owner form with equivalent information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2014-05-27 |  | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  |  | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. | [19 empty] | TO
Inactive | MOD | MOD-025 | MOD-025-RFC-01 | 1. | Each Generator Owner shall verify the operating range of Reactive Power capability for each of its applicable units by operational tracking or by test at least every five years, (with no more than 66 calendar months between verifications) in accordance with MOD-025-RFC-01 Attachment 1. |  | Long-Term Planning | 2011-11-03 | [8 empty] | 2012-11-07 | The NERC Board of Trustees withdrew approval of MOD-025-RFC-01 at its meeting on November 7, 2012. |  |  |  |  | GO
Inactive | MOD | MOD-025 | MOD-025-RFC-01 | No Parts for 1. |  |  | Long-Term Planning | 2011-11-03 | [8 empty] | 2012-11-07 | The NERC Board of Trustees withdrew approval of MOD-025-RFC-01 at its meeting on November 7, 2012.
Inactive | MOD | MOD-025 | MOD-025-RFC-01 | 2. | Each Generator Owner shall provide the following data from the most recent Reactive Power capability verification within 30 calendar days of a written request from its Transmission Planner, Transmission Operator, Reliability Coordinator or Planning Coordinator. [See standard pdf for additional information] |  | Long-Term Planning | 2011-11-03 | [8 empty] | 2012-11-07 | The NERC Board of Trustees withdrew approval of MOD-025-RFC-01 at its meeting on November 7, 2012. |  |  |  |  | GO
Inactive | MOD | MOD-025 | MOD-025-RFC-01 | No Parts for 2. |  |  | Long-Term Planning | 2011-11-03 | [8 empty] | 2012-11-07 | The NERC Board of Trustees withdrew approval of MOD-025-RFC-01 at its meeting on November 7, 2012.
Inactive | MOD | MOD-026 | MOD-026-1 | 1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | M1. The Transmission Planner must have and provide the dated request for instructions or data, the transmitted instructions or data, and dated evidence of a written transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence that it provided the request within 90 calendar days in accordance with Requirement R1. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information | [21 empty] | TP
Inactive | MOD | MOD-026 | MOD-026-1 | No Parts for 1. |  | M1. The Transmission Planner must have and provide the dated request for instructions or data, the transmitted instructions or data, and dated evidence of a written transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence that it provided the request within 90 calendar days in accordance with Requirement R1. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information
Inactive | MOD | MOD-026 | MOD-026-1 | 2. | Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 |  | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1.1. | Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1.2. | Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1.3. | Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1.4. | Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1.5. | Compensation settings (such as droop, line drop, differential compensation), if used, and | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 2.1.6. | Model structure and data for power system stabilizer, if so equipped. | M2. The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2018-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA are compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection is compliant with Requirement R2 By the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure 100 percent of its applicable unit gross MVA is compliant with Requirement R2 By the first day of the first calendar quarter, 10 years following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | 3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). Footnote: If verification is performed, the 10-year period as outlined in MOD-026 Attachment 1 is reset. | M3. Evidence for Requirement R3 must include the Generator Owner’s dated written response containing the information identified in Requirement R3 and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) of the response. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | No Parts for 3. |  | M3. Evidence for Requirement R3 must include the Generator Owner’s dated written response containing the information identified in Requirement R3 and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) of the response. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information
Inactive | MOD | MOD-026 | MOD-026-1 | 4. | Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. Footnote:Exciter, voltage regulator, plant volt/var or power system stabilizer control replacement including software alterations that alter excitation control system equipment response, plant digital control system addition or replacement, plant digital control system software alterations that alter excitation control system equipment response, plant volt/var function equipment addition or replacement (such as static var systems, capacitor banks, individual unit excitation systems, etc), a change in the voltage control mode (such as going from power factor control to automatic voltage control, etc), exciter, voltage regulator, impedance compensator, or power system stabilizer settings change. Automatic changes in settings that occur due to changes in operating mode do not apply to Requirement R4. | M4. Evidence for Requirement R4 must include, for each of the Generator Owner’s applicable units for which system changes specified in Requirement R4 were made, a dated revised model data or plans to perform a model verification and dated evidence (e.g., electronic mail message, postal receipt, or confirmation of facsimile) it provided the revised model and data or plans within 180 calendar days of making changes. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | No Parts for 4. |  | M4. Evidence for Requirement R4 must include, for each of the Generator Owner’s applicable units for which system changes specified in Requirement R4 were made, a dated revised model data or plans to perform a model verification and dated evidence (e.g., electronic mail message, postal receipt, or confirmation of facsimile) it provided the revised model and data or plans within 180 calendar days of making changes. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information
Inactive | MOD | MOD-026 | MOD-026-1 | 5. | Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | M5. Evidence for Requirement R5 must include the Generator Owner’s dated written response containing the information identified in Requirement R5 and dated evidence (e.g., electronic mail message, postal receipt, or confirmation of facsimile) it provided a written response within 90 calendar days following receipt of a technically justified request. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | MOD | MOD-026 | MOD-026-1 | No Parts for 5. |  | M5. Evidence for Requirement R5 must include the Generator Owner’s dated written response containing the information identified in Requirement R5 and dated evidence (e.g., electronic mail message, postal receipt, or confirmation of facsimile) it provided a written response within 90 calendar days following receipt of a technically justified request. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information
Inactive | MOD | MOD-026 | MOD-026-1 | 6. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. | M6. Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information | [21 empty] | TP
Inactive | MOD | MOD-026 | MOD-026-1 | 6.1. | The excitation control system or plant volt/var control function model initializes to compute modeling data without error, | M6. Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-05-26 | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information | [21 empty] | TP
Inactive | MOD | MOD-026 | MOD-026-1 | 6.2. | A no-disturbance simulation results in negligible transients, and | M6. Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-05-26 | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information | [21 empty] | TP
Inactive | MOD | MOD-026 | MOD-026-1 | 6.3. | For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. | M6. Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-05-26 | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 See Implementation Plan for additional compliance information | [21 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1. | Each Transmission Planner and its Planning Coordinator shall jointly develop dynamic model requirements for the purpose of evaluating submitted dynamic models and accompanying documentation of Model Verification and Model Validation. The dynamic model requirements shall be made available to Generator Owner(s) and Transmission Owner(s) by the Transmission Planner and shall include at a minimum the following: | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1.1. | Positive sequence dynamic model requirements, including requirements for the models and functions listed in Attachment 1; | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 | 2027-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1.1.1. | Specification of which limiting and protective functions listed within Attachment 1, Table 1.1 are required to be represented in the model. | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 | 2027-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1.2. | For the facilities listed in Applicability Sections 4.2.5 and 4.2.6 (Inverter-Based Resources), 4.2.3.2 (FACTS devices), 4.2.4.1 (LCC HVDC), and 4.2.4.2 (VSC HVDC): | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 | 2027-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1.2.1. | Identification of which legacy [1] facilities require electromagnetic transient (EMT) model(s) under Requirement R3 accompanied by a statement of need; and [1] A legacy facility for the purpose of this standard is any facility with a commercial operation date prior to the effective date of MOD-026-2. | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 | 2027-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1.2.2. | Specification of acceptable EMT models, format, and level of detail. | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 | 2027-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 1.3. | Any additional requirements not listed under Requirement R1, Parts 1.1 and 1.2 used by the Transmission Planner to determine the acceptability of submitted dynamic models and accompanying documentation under Requirement R5. If no such additional requirements exist, the Transmission Planner shall document that none are applicable. | M1. Each Transmission Planner and Planning Coordinator must provide dated evidence such as document(s), webpage(s), or web portal(s) outlining the jointly developed dynamic model requirements. Each Transmission Planner shall have evidence demonstrating that the dynamic model requirements were made available to Generator Owner(s) and Transmission Owner(s) in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 | 2027-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2. | Each Generator Owner or Transmission Owner shall provide to its Transmission Planner positive sequence dynamic model(s) with associated parameters, any information pertaining to changes to the model(s) or its parameters, and accompanying documentation in accordance with the periodicity requirements of Attachment 2. Each Generator Owner or Transmission Owner shall provide the following: | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.1. | Positive sequence dynamic model(s) representing the in-service equipment of the facility including, at a minimum, each of the applicable models and functions listed in Attachment 1 in accordance with the requirements developed in Requirement R1; | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.2. | Documentation of Model Verification demonstrating that the configurable, site-specific parameters of the model(s) are representative of the design and settings of the in-service equipment of the facility; | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.2.1. | For any parameters that cannot be verified, the Generator Owner or Transmission Owner shall provide a written statement to the Transmission Planner identifying the unverifiable parameters and reasons they cannot be verified. | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.3. | Documentation of Model Validation comparing the behavior of the model(s) to the measured behavior during a staged test or system disturbance for: | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.3.1. | A dynamic reactive power or voltage excursion event to perform Model Validation of generator, excitation control, reactive power control, and voltage control models, as applicable; and | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.3.2. | A dynamic active power or frequency excursion event to perform Model Validation of governor control, active power control, and frequency control models, as applicable. For a frequency excursion event to be sufficient for Model Validation, the applicable facility must be operating in a frequency responsive mode and the frequency deviation (nadir point) from the scheduled frequency must be greater than or equal to: | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.3.2.1. | 0.04 hertz in the Eastern Interconnection; | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.3.2.2. | 0.08 hertz in the ERCOT and Western Interconnections; and | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 2.3.2.3. | 0.30 hertz in the Quebec Interconnection. | M2. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided positive sequence dynamic model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3. | For facilities listed in Applicability Sections 4.2.3.2 (FACTS devices), 4.2.4 (HVDC), 4.2.5 (BES IBRs), and 4.2.6 (Non-BES IBRs), excluding legacy facilities where the original equipment manufacturer [2] no longer supports EMT model(s) for the facility as well as legacy facilities not identified by the Transmission Planner under Requirement R1, Part 1.2.1, each Generator Owner or Transmission Owner shall provide to its Transmission Planner EMT model(s) with associated parameters, any information pertaining to changes to the model(s) or its parameters, and accompanying documentation, in accordance with the periodicity requirements of Attachment 2. Each Generator Owner or Transmission Owner shall provide the following: [2] If the original equipment manufacturer that commissioned the facility was acquired, merged, or operating under a different name, the new company would be considered the original equipment manufacturer. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.1. | A facility EMT model with associated parameters representing the applicable HVDC, FACTS device, IBR unit(s), [3] collector system, auxiliary control device(s),[4] power plant controller, generator step-up transformer(s), and main power transformer(s) that includes: [3] For purposes of this standard, the phrase “IBR unit” refers to an individual device, or a grouping of multiple devices, that uses a power electronic interface(s), such as an inverter or converter, that is capable of exporting Real Power from a primary energy source or energy storage system, and that connects at a single point on the collector system. [4] Only to include those auxiliary control devices that act on voltage and/or frequency. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.1.1. | Enabled protective functions [5] that directly trip the IBR unit(s) or facility; and [5] Required protective functions are those that act directly on, or act on quantities derived from, voltage, frequency, and/or current. Examples of protections include DC reverse current, DC bus over-voltage and under-voltage, DC voltage unbalance, DC overcurrent, AC over-voltage and under-voltage protection (instantaneous and RMS), AC overcurrent, over-frequency and under-frequency protection, feeder (equivalent) AC over-voltage and under-voltage, feeder (equivalent) over-frequency and under-frequency, PLL (or equivalent) loss of synchronism, and phase jump tripping. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.1.2. | Limiting functions [6] that limit active/reactive output of the IBR unit(s) or facility. [6] Required limiting functions are those that act directly on, or act on quantities derived from, voltage, frequency, and/or current. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.2. | Documentation of Model Verification demonstrating that the configurable, site-specific parameters of the model(s) are representative of the design and settings of the in-service equipment of the facility; | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.2.1. | For any parameters that cannot be verified, the Generator Owner or Transmission Owner shall provide a written statement to the Transmission Planner identifying the unverifiable parameters and reasons they cannot be verified. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.3. | Documentation of Model Validation comparing the behavior of the facility EMT model to the measured behavior during a staged test or system disturbance for: | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.3.1. | A dynamic reactive power or voltage excursion event to perform Model Validation of reactive power control and voltage control models, as applicable; and | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.3.2. | A dynamic active power or frequency excursion event to perform Model Validation of active power control and frequency control models, as applicable. For a frequency excursion event to be sufficient for Model Validation, the applicable facility must be operating in a frequency responsive mode and the frequency deviation (nadir point) from the scheduled frequency must be greater than or equal to: | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.3.2.1. | 0.04 hertz in the Eastern Interconnection; | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.3.2.2. | 0.08 hertz in the ERCOT and Western Interconnections; and | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.3.2.3. | 0.30 hertz in the Quebec Interconnection. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.4. | For IBR facilities, test [7] result(s) demonstrating a comparison of the IBR unit response and the IBR unit EMT model response for large signal disturbances. If test results are not obtainable, the Generator Owner shall document the reason; and [7] A hardware specific test may include a factory type test, hardware in the loop test, or other manufacturer test to ensure the EMT model’s large signal response emulates the supplied equipment to the extent possible. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 3.5. | Documentation comparing the response of the facility positive sequence dynamic model provided in Requirement R2 to the response of the facility EMT model for large signal disturbances as defined by the Transmission Planner. | M3. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) for each applicable facility that it provided EMT model(s) and accompanying documentation to its Transmission Planner in accordance with Requirement R3. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 4. | Each Generator Owner or Transmission Owner shall, within 180 calendar days after making a hardware, software, firmware, control mode, or setting change(s) [8] to an applicable unit or facility that alters the dynamic response characteristic(s), provide its Transmission Planner with updated model(s) and accompanying documentation as described in Requirement R2, Parts 2.1 through 2.3 and, if applicable, Requirement R3, Parts 3.1 through 3.5. If mutually agreed upon with the Transmission Planner, model(s) and accompanying documentation may be provided according to a revised timeline. [8] Automatic changes in settings that occur due to changes in operating mode are excluded from Requirement R4. | M4. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) that it provided its Transmission Planner with updated model(s) and accompanying documentation in accordance with Requirement R4 for each change altering dynamic response characteristic(s) of an applicable unit or facility. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | No Parts for 4. |  | M4. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, upload via web portal, etc.) that it provided its Transmission Planner with updated model(s) and accompanying documentation in accordance with Requirement R4 for each change altering dynamic response characteristic(s) of an applicable unit or facility. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 5. | Each Transmission Planner shall, within 120 calendar days after receiving model(s) and accompanying documentation provided by a Generator Owner or Transmission Owner or within a mutually agreed upon timeline with the applicable Generator Owner or Transmission Owner, evaluate the model(s) and accompanying documentation to determine if it meets the dynamic model requirements developed under Requirement R1 and provide: • A written notification to the Generator Owner or Transmission Owner that the model(s) and accompanying documentation are acceptable, and a written notification, or the accepted model(s) and accompanying documentation, to its Planning Coordinator; or • A written notification to the Generator Owner or Transmission Owner that the model(s) and accompanying documentation are not acceptable, along with an explanation and any supporting evidence demonstrating the issue(s). | M5. Each Transmission Planner must provide dated evidence that it reviewed provided model(s) and accompanying documentation in accordance with the dynamic model requirements developed in Requirement R1 and provided a written response notification in accordance with Requirement R5. Dated evidence may include date received, review date of provided model(s) and accompanying documentation, and dated response (e.g., email message, postal receipt, etc.). | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [21 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | No Parts for 5. |  | M5. Each Transmission Planner must provide dated evidence that it reviewed provided model(s) and accompanying documentation in accordance with the dynamic model requirements developed in Requirement R1 and provided a written response notification in accordance with Requirement R5. Dated evidence may include date received, review date of provided model(s) and accompanying documentation, and dated response (e.g., email message, postal receipt, etc.). | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 6. | Each Generator Owner or Transmission Owner shall, within 120 calendar days after receiving a notification of unacceptability under Requirement R5 or within 180 calendar days after receiving a request from its Transmission Planner to perform a model review due to identified model or accompanying documentation deficiencies, provide a response to its Transmission Planner. If mutually agreed upon with the Transmission Planner, the response to a request to perform a model review may be provided according to a revised timeline. The provided response shall include one of the following: • Updated model(s) and accompanying documentation as described in Requirement R2, Parts 2.1 through 2.3 and, if applicable, Requirement R3, Parts 3.1 through 3.5; or • A technical justification and supporting evidence for maintaining the current model(s) and accompanying documentation. | M6. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, etc.) that it provided a response to its Transmission Planner in accordance with Requirement R6. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | No Parts for 6. |  | M6. Each Generator Owner or Transmission Owner must provide dated evidence (e.g., email message, postal receipt, etc.) that it provided a response to its Transmission Planner in accordance with Requirement R6. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | 7. | Each Transmission Planner shall provide the current (in-use) model(s) and accompanying documentation for an existing facility within 90 calendar days of receiving a written request for such data from the Generator Owner or Transmission Owner that owns the facility. | M7. Each Transmission Planner must provide dated evidence (e.g., email message, postal receipt, etc.) that it provided the current (in-use) model(s) and accompanying documentation to the Generator Owner or Transmission Owner in accordance with Requirement R7. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model | [21 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026 | MOD-026-2 | No Parts for 7. |  | M7. Each Transmission Planner must provide dated evidence (e.g., email message, postal receipt, etc.) that it provided the current (in-use) model(s) and accompanying documentation to the Generator Owner or Transmission Owner in accordance with Requirement R7. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2027-04-01 |  | X | See the Implementation Plan for additional information on Initial Performance Dates for periodic requirements, newly commissioned and newly applicable facilities, and early compliance. |  |  | Filing/Order Docket No. RD26-3-000 Additional Effective Date Details Requirements R1 and R7 - April 1, 2027 Entities shall not be required to comply with Requirement R1 relating to the jointly developed dynamic model
Inactive | MOD | MOD-027 | MOD-027-1 | 1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | M1. The Transmission Planner must have and provide the dated request for instructions or data, the transmitted instruction or data, and dated evidence of a written transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence that it provided the request within 90 calendar days in accordance with Requirement R1. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 | [21 empty] | TP
Inactive | MOD | MOD-027 | MOD-027-1 | No Parts for 1. |  | M1. The Transmission Planner must have and provide the dated request for instructions or data, the transmitted instruction or data, and dated evidence of a written transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence that it provided the request within 90 calendar days in accordance with Requirement R1. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000
Inactive | MOD | MOD-027 | MOD-027-1 | 2. | Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 2.1.1. | Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: ? A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, ? A speed governor reference change with the applicable unit online, or ? A partial load rejection test, Footnote: Differences between the control mode tested and the final simulation model must be identified, particularly when analyzing load rejection data. Most controls change gains or have a set point runback which takes effect when the breaker opens. Load or set point controls will also not be in effect once the breaker opens. Some method of accounting for these differences must be presented if the final model is not validated from on-line data under the normal operating conditions under which the model is expected to apply. | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 2.1.2. | Type of governor and load control or active power control/frequency control equipment, Footnote: Turbine/governor and load control or active power/frequency control: | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 2.1.3. | A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 2.1.4. | Model structure and data for turbine/governor and load control or active power/frequency control, and | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 2.1.5. | Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | M2. The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2018-07-01 | X | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | 3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | M3. Evidence for Requirement R3 must include the Generator Owner’s dated written response containing the information identified in Requirement R3 and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) of the response. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | No Parts for 3. |  | M3. Evidence for Requirement R3 must include the Generator Owner’s dated written response containing the information identified in Requirement R3 and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) of the response. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000
Inactive | MOD | MOD-027 | MOD-027-1 | 4. | Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. Footnote: Control replacement or alteration including software alterations or plant digital control system addition or replacement, plant digital control system software alterations that alter droop, and/or dead band, and/or frequency response and/or a change in the frequency control mode (such as going from droop control to constant MW control, etc). | M4. Evidence for Requirement R4 must include, for each of the Generator Owner’s applicable units for which system changes specified in Requirement R4 were made, dated revised model data or dated plans to perform a model verification and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) within 180 calendar days of making changes. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | MOD | MOD-027 | MOD-027-1 | No Parts for 4. |  | M4. Evidence for Requirement R4 must include, for each of the Generator Owner’s applicable units for which system changes specified in Requirement R4 were made, dated revised model data or dated plans to perform a model verification and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) within 180 calendar days of making changes. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000
Inactive | MOD | MOD-027 | MOD-027-1 | 5. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. | M5. Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 |  | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 | [21 empty] | TP
Inactive | MOD | MOD-027 | MOD-027-1 | 5.1 . | The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, | M5. Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-07-01 | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. | 2026-03-31 | Filing/Order Docket No. RM13-16-000 | [21 empty] | TP
Inactive | MOD | MOD-027 | MOD-027-1 | 5.2. | A no-disturbance simulation results in negligible transients, and | M5. Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-05-26 | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 | [21 empty] | TP
Inactive | MOD | MOD-027 | MOD-027-1 | 5.3. | For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. | M5. Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | Operations Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-26 | 2014-07-01 | 2014-05-26 | X | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. |  | 2026-03-31 | Filing/Order Docket No. RM13-16-000 | [21 empty] | TP
Inactive | MOD | MOD-028 | MOD-028-1 | 1. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.1. | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.2. | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.3. | Any contractual obligations for allocation of TTC. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.4. | A description of the manner in which Contingencies are identified for use in the TTC process. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.5. | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.5.1. | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.5.2. | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.5.3. | The source/sink or POR/POD identification and mapping to the model. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 1.5.4. | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | 2. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 2.1. | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 2.2. | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 2.3. | Facility Ratings specified by the Generator Owners and Transmission Owners. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.1. | For on-peak and off-peak intra-day and next-day TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.1.1. | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.1.2. | Load forecast for the applicable period being calculated. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.1.3. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.2. | For days two through 31 TTCs and for months two through 13 TTCs, use the following (as well as any other values and internal parameters as specified in the ATCID): |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.2.1. | Expected generation and Transmission outages, additions, and Retirements, included as specified in the ATCID. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.2.2. | Daily load forecast for the days two through 31 TTCs being calculated and monthly forecast for months two through 13 months TTCs being calculated. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 3.2.3. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 4. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: [Time Horizon: Operations Planning] |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 4.1. | Use all Contingencies meeting the criteria described in the ATCID. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 4.2. | Respect any contractual allocations of TTC. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 4.3. | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 5. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: [Time Horizon: Operations Planning] |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 5.1. | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 5.2. | At least once per calendar month for TTCs used in monthly ATC calculations. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 5.3. | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 6. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: [Time Horizon: Operations Planning] | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 6.1. | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 6.2. | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 6.3. | Use (as the TTC) the lesser of: The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or The sum of Facility Ratings of all ties comprising the ATC Path. | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 6.4. | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 7. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: [Time Horizon: Operations Planning] |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 7.1. | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 7.2. | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-1 | 8. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | No Parts for 8. |  |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-028 | MOD-028-1 | 9. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | No Parts for 9. |  |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-028 | MOD-028-1 | 10. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: [Time Horizon: Operations Planning] See Standard for formula. |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | No Parts for 10. |  |  | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-028 | MOD-028-1 | 11. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for formula. | M4. Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-1 | No Parts for 11. |  | M4. Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | Operations Planning | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-028 | MOD-028-2 | 1. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.1. | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.2. | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.3. | Any contractual obligations for allocation of TTC. | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.4. | A description of the manner in which Contingencies are identified for use in the TTC process. | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.5. | The following information on how source and sink for transmission service is accounted for in ATC calculations including: | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.5.1. | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.5.2. | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.5.3. | The source/sink or POR/POD identification and mapping to the model. | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 1.5.4. | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | M1. Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | 2. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 2.1. | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 2.2. | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 2.3. | Facility Ratings specified by the Generator Owners and Transmission Owners. | M2. Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3.1. | For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3.1.1. | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3.1.2. | A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3.1.3. | A daily load forecast for TTCs used in ATC calculations for days two through 31. | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3.1.4. | A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 3.1.5. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | M3. Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-10-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 4. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: | M4. Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 4.1. | Use all Contingencies meeting the criteria described in the ATCID. | M4. Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 4.2. | Respect any contractual allocations of TTC. | M4. Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 4.3. | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | M4. Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 5. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: | M5. Each Transmission Operator shall provide copies of contracts that contain requirements to allocate TTCs and TTC values to show that any contractual allocations of TTC were respected as required in R4.2. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 5.1. | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. | M5. Each Transmission Operator shall provide copies of contracts that contain requirements to allocate TTCs and TTC values to show that any contractual allocations of TTC were respected as required in R4.2. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 5.2. | At least once per calendar month for TTCs used in monthly ATC calculations. | M5. Each Transmission Operator shall provide copies of contracts that contain requirements to allocate TTCs and TTC values to show that any contractual allocations of TTC were respected as required in R4.2. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 5.3. | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | M5. Each Transmission Operator shall provide copies of contracts that contain requirements to allocate TTCs and TTC values to show that any contractual allocations of TTC were respected as required in R4.2. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 6. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 6.1. | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . Footnote: The Transmission operator may honor distribution factors less than 5% if desired. | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 6.2. | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 6.3. | Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 6.4. | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 7. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: | M7. Each Transmission Operator shall provide evidence (such as logs and data and dated copies of requests from the Transmission Service Provider to establish TTCs at specific intervals) that TTCs have been established at least once in the calendar week prior to the specified period for TTCs used in hourly and daily ATC calculations, at least once per calendar month for TTCs used in monthly ATC calculations, and within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a autotransformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage; provided such outage is expected to last 24 hours or longer in duration per the specifications in R5. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 7.1. | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. | M7. Each Transmission Operator shall provide evidence (such as logs and data and dated copies of requests from the Transmission Service Provider to establish TTCs at specific intervals) that TTCs have been established at least once in the calendar week prior to the specified period for TTCs used in hourly and daily ATC calculations, at least once per calendar month for TTCs used in monthly ATC calculations, and within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a autotransformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage; provided such outage is expected to last 24 hours or longer in duration per the specifications in R5. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 7.2. | Seven calendar days after its determination for TTCs used in monthly ATC calculations. | M7. Each Transmission Operator shall provide evidence (such as logs and data and dated copies of requests from the Transmission Service Provider to establish TTCs at specific intervals) that TTCs have been established at least once in the calendar week prior to the specified period for TTCs used in hourly and daily ATC calculations, at least once per calendar month for TTCs used in monthly ATC calculations, and within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a autotransformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage; provided such outage is expected to last 24 hours or longer in duration per the specifications in R5. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 | 2013-09-27 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-028 | MOD-028-2 | 8. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | M8. Each Transmission Operator shall provide evidence (such as written documentation) that TTCs have been calculated using the process described in R6. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | No Parts for 8. |  | M8. Each Transmission Operator shall provide evidence (such as written documentation) that TTCs have been calculated using the process described in R6. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000
Inactive | MOD | MOD-028 | MOD-028-2 | 9. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | M9. Each Transmission Operator shall have evidence including a copy of the latest calculated TTC values along with a dated copy of email notices or other equivalent evidence to show that it provided its Transmission Service Provider with the most current values for TTC in accordance with R7. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | No Parts for 9. |  | M9. Each Transmission Operator shall have evidence including a copy of the latest calculated TTC values along with a dated copy of email notices or other equivalent evidence to show that it provided its Transmission Service Provider with the most current values for TTC in accordance with R7. | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000
Inactive | MOD | MOD-028 | MOD-028-2 | 10. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | The Transmission Service Provider shall demonstrate compliance with R8 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R8 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-028-2 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R8 to calculate its firm ETC. (R8) | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | No Parts for 10. |  | The Transmission Service Provider shall demonstrate compliance with R8 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R8 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-028-2 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R8 to calculate its firm ETC. (R8) | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000
Inactive | MOD | MOD-028 | MOD-028-2 | 11. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | M11. The Transmission Service Provider shall demonstrate compliance with R9 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R9 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-028-2 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R8 to calculate its non-firm ETC. (R9) M12. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates firm ATCs, as required in R10. Such documentation must show that only the variables allowed in R10 were used to calculate firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R10) M13. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates non-firm ATCs, as required in R11. Such documentation must show that only the variables allowed in R11 were used to calculate non-firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R11) | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-028 | MOD-028-2 | No Parts for 11. |  | M11. The Transmission Service Provider shall demonstrate compliance with R9 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R9 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-028-2 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R8 to calculate its non-firm ETC. (R9) M12. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates firm ATCs, as required in R10. Such documentation must show that only the variables allowed in R10 were used to calculate firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R10) M13. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates non-firm ATCs, as required in R11. Such documentation must show that only the variables allowed in R11 were used to calculate non-firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R11) | Operations Planning | 2012-02-09 | 2012-08-24 | 2013-07-18 | 2013-09-27 | 2013-10-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM12-19-000
Inactive | MOD | MOD-029 | MOD-029-1 | 1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.1. | Includes at least: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.2. | Models all system Elements as in-service for the assumed initial conditions. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.5. | Uses Load forecast by Balancing Authority. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.6. | Uses Transmission Facility additions and retirements. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.7. | Uses Generation Facility additions and retirements. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.8. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2. | The Transmission Operator shall use the following process to determine TTC: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.1. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.1.3. | Uncontrolled separation shall not occur. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 |  | 2010-02-08 |  |  |  | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | 3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | No Parts for 3. |  |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-029 | MOD-029-1 | 4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1 | No Parts for 4. |  |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-029 | MOD-029-1 | 5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1 | No Parts for 5. |  |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-029 | MOD-029-1 | 6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1 | No Parts for 6. |  |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-029 | MOD-029-1 | 7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1 | No Parts for 7. |  |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-029 | MOD-029-1 | 8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1 | No Parts for 8. |  |  |  | 2008-08-26 | 2008-08-29 | 2009-11-24 | 2010-02-08 | [5 empty] | 2010-09-16 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-029 | MOD-029-1a | 1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.1. | Includes at least: | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.2. | Models all system Elements as in-service for the assumed initial conditions. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.5. | Uses Load forecast by Balancing Authority. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.6. | Uses Transmission Facility additions and retirements. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.7. | Uses Generation Facility additions and retirements. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.8. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | M1. Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2. | The Transmission Operator shall use the following process to determine TTC: | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.1. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.1.3. | Uncontrolled separation shall not occur. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. | M2. Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 | 2010-09-16 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | 3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology with paths with ratings established prior to January 1, 1994 shall provide evidence the path and its rating were established prior to January 1, 1994. (R2.7) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | No Parts for 3. |  | Each Transmission Operator that uses the Rated System Path Methodology with paths with ratings established prior to January 1, 1994 shall provide evidence the path and its rating were established prior to January 1, 1994. (R2.7) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-029 | MOD-029-1a | 4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology shall produce as evidence the study reports, as required in R.2.8, for each path for which it determined TTC for the period examined. (R2) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-1a | No Parts for 4. |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce as evidence the study reports, as required in R.2.8, for each path for which it determined TTC for the period examined. (R2) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-029 | MOD-029-1a | 5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: See standard for formula. | M5. Each Transmission Operator shall provide evidence that it used the lesser of the calculated TTC or the SOL as the TTC, by producing: 1) all values calculated pursuant to R2 for each ATC Path, 2) Any corresponding SOLs for those ATC Paths, and 3) the TTC set by the Transmission Operator and given to the Transmission Service Provider for use in R7and R8 for each ATC Path. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1a | No Parts for 5. |  | M5. Each Transmission Operator shall provide evidence that it used the lesser of the calculated TTC or the SOL as the TTC, by producing: 1) all values calculated pursuant to R2 for each ATC Path, 2) Any corresponding SOLs for those ATC Paths, and 3) the TTC set by the Transmission Operator and given to the Transmission Service Provider for use in R7and R8 for each ATC Path. (R3) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-029 | MOD-029-1a | 6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: See standard for formula. ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service serving Load (i.e., secondary service), to include losses, and load growth not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFNF is the non-firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using non-firm transmission service as specified in the ATCID. | M6. Each Transmission Operator shall provide evidence (such as logs or data) that it provided the TTC and its study report to the Transmission Service Provider within seven calendar days of the finalization of the study report. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1a | No Parts for 6. |  | M6. Each Transmission Operator shall provide evidence (such as logs or data) that it provided the TTC and its study report to the Transmission Service Provider within seven calendar days of the finalization of the study report. (R4) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-029 | MOD-029-1a | 7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: See standard for formula. : Lower] [Time Horizon: Operations Planning] ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF are changes to firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm Available Transfer Capability as determined by the Transmission Service Provider and specified in their ATCID | M7. The Transmission Service Provider shall demonstrate compliance with R5 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R5 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-029-1 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R5 to calculate its firm ETC. (R5) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1a | No Parts for 7. |  | M7. The Transmission Service Provider shall demonstrate compliance with R5 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R5 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-029-1 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R5 to calculate its firm ETC. (R5) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-029 | MOD-029-1a | 8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: See standard for formula. ATCNF = TTC – ETCF – ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF are changes to non-firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm Available Transfer Capability as determined by the Transmission Service Provider and specified in its ATCID. | M8. The Transmission Service Provider shall demonstrate compliance with R5 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R6 and with data used to calculate this specified value for the designated time period. The data used must meet the requirements specified in the MOD-029 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R6 to calculate its non-firm ETC. (R6) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-1a | No Parts for 8. |  | M8. The Transmission Service Provider shall demonstrate compliance with R5 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R6 and with data used to calculate this specified value for the designated time period. The data used must meet the requirements specified in the MOD-029 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R6 to calculate its non-firm ETC. (R6) | Operations Planning | 2009-11-05 | 2009-12-02 | 2010-09-16 | 2010-09-16 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-5-000
Inactive | MOD | MOD-029 | MOD-029-2a | 1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.1. | Includes at least: | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.2. | Models all system Elements as in-service for the assumed initial conditions. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.5. | Uses Load forecast by Balancing Authority. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.6. | Uses Transmission Facility additions and retirements. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.7. | Uses Generation Facility additions and retirements. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.8. | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 1.2. DO NOT USE | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | Each Transmission Operator that uses the Rated System Path Methodology shall produce any Transmission model it used to calculate TTC for purposes of calculating ATC for each ATC Path, as required in R1, for the time horizon(s) to be examined. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2. | The Transmission Operator shall use the following process to determine TTC: | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.1. | Except where otherwise specified within MOD-029-2, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.1.3. | Uncontrolled separation shall not occur. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.2. DO NOT USE | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.5. DO NOT USE | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.6. DO NOT USE | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 2.8. | Create a study report that describes the steps above that were undertaken (R2.1 – R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | 3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology with paths with ratings established prior to January 1, 1994 shall provide evidence the path and its rating were established prior to January 1, 1994. (R2.7) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | No Parts for 3. |  | Each Transmission Operator that uses the Rated System Path Methodology with paths with ratings established prior to January 1, 1994 shall provide evidence the path and its rating were established prior to January 1, 1994. (R2.7) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-029 | MOD-029-2a | 4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. | Each Transmission Operator that uses the Rated System Path Methodology shall produce as evidence the study reports, as required in R.2.8, for each path for which it determined TTC for the period examined. (R2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-029 | MOD-029-2a | No Parts for 4. |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce as evidence the study reports, as required in R.2.8, for each path for which it determined TTC for the period examined. (R2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-029 | MOD-029-2a | 5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [See standard for additional information.] ETCF = NLF + NITSF + GFF + PTPF + RORF + OSF Where: NLF is the firm capacity set aside to serve peak Native Load forecast commitments for the time period being calculated, to include losses, and Native Load growth, not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. NITSF is the firm capacity reserved for Network Integration Transmission Service serving Load, to include losses, and Load growth, not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFF is the firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the firm capacity reserved for Roll-over rights for contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service as specified in the ATCID. | Each Transmission Operator shall provide evidence that it used the lesser of the calculated TTC or the SOL as the TTC, by producing: 1) all values calculated pursuant to R2 for each ATC Path, 2) Any corresponding SOLs for those ATC Paths, and 3) the TTC set by the Transmission Operator and given to the Transmission Service Provider for use in R7and R8 for each ATC Path. (R3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-2a | No Parts for 5. |  | Each Transmission Operator shall provide evidence that it used the lesser of the calculated TTC or the SOL as the TTC, by producing: 1) all values calculated pursuant to R2 for each ATC Path, 2) Any corresponding SOLs for those ATC Paths, and 3) the TTC set by the Transmission Operator and given to the Transmission Service Provider for use in R7and R8 for each ATC Path. (R3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-029 | MOD-029-2a | 6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [See standard for additional information.] ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service serving Load (i.e., secondary service), to include losses, and load growth not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFNF is the non-firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using non-firm transmission service as specified in the ATCID. | Each Transmission Operator shall provide evidence (such as logs or data) that it provided the TTC and its study report to the Transmission Service Provider within seven calendar days of the finalization of the study report. (R4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-2a | No Parts for 6. |  | Each Transmission Operator shall provide evidence (such as logs or data) that it provided the TTC and its study report to the Transmission Service Provider within seven calendar days of the finalization of the study report. (R4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-029 | MOD-029-2a | 7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [See standard for additional information.] ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm Available Transfer Capability as determined by the Transmission Service Provider and specified in their ATCID. | The Transmission Service Provider shall demonstrate compliance with R5 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R5 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-029-2 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R5 to calculate its firm ETC. (R5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-2a | No Parts for 7. |  | The Transmission Service Provider shall demonstrate compliance with R5 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R5 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in MOD-029-2 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R5 to calculate its firm ETC. (R5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-029 | MOD-029-2a | 8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF – ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm Available Transfer Capability as determined by the Transmission Service Provider and specified in its ATCID. | M8. The Transmission Service Provider shall demonstrate compliance with R5 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R6 and with data used to calculate this specified value for the designated time period. The data used must meet the requirements specified in the MOD-029 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R6 to calculate its non-firm ETC. (R6) M9. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates firm ATCs, as required in R7. Such documentation must show that only the variables allowed in R7 were used to calculate firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R7) M10. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates non-firm ATCs, as required in R8. Such documentation must show that only the variables allowed in R8 were used to calculate non-firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R8) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-029 | MOD-029-2a | No Parts for 8. |  | M8. The Transmission Service Provider shall demonstrate compliance with R5 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the algorithm defined in R6 and with data used to calculate this specified value for the designated time period. The data used must meet the requirements specified in the MOD-029 and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the algorithm in R6 to calculate its non-firm ETC. (R6) M9. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates firm ATCs, as required in R7. Such documentation must show that only the variables allowed in R7 were used to calculate firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R7) M10. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates non-firm ATCs, as required in R8. Such documentation must show that only the variables allowed in R8 were used to calculate non-firm ATCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R8) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-030 | MOD-030-1 | 1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID). [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 1.2.3. | The source/sink or POR/POD identification and mapping to the model. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 2. | The Transmission Operator shall perform the following: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.2. | Results of a first Contingency transfer analyses from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.2.1. | Use first Contingency criteria consistent with those first Contignency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.3. | Any limiting Element/Contingency combination at least within the Transmission model identified in R3.4 and R3.5 that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and -Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or -A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. -The Transmission Operator may utilize distribution factors less than 5% if desired. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.2. | At a minimum, establish the list of Flowgates to create, modify, or delete internal Flowgates definitions at least once per calendar year. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.3. | At a minimum, establish the list of Flowgates to create, modify, or delete external Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.5. | At a minimum, establish the TFC once per calendar year. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 3.3. | Updated at least once per month for AFC calculations for months two through 13. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-1 | 4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows:[Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | No Parts for 4. |  |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-030 | MOD-030-1 | 5. | When calculating AFCs, the Transmission Service Provider shall: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 5.1. | Use the models provided by the Transmission Operator. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 6.7. | The impact of other firm services determined by the Transmission Service Provider. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 7.7. | The impact of other non-firm services determined by the Transmission Service Provider. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | No Parts for 8. |  |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-030 | MOD-030-1 | 9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | No Parts for 9. |  |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-030 | MOD-030-1 | 10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: [Time Horizon: Operations Planning] |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 10.2. | For daily AFC, once per day. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 10.3. | For monthly AFC, once per week. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | 11. | When converting Flowgate AFCs to ATCs (and TFCs to TTCs) for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729) | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-1 | No Parts for 11. |  |  |  | 2008-08-26 | 2008-08-29 | [7 empty] | 2009-11-24 | Filing/Order Docket No. RM08-19-000 Withdrawn. FERC approved NERC's petition to withdraw its request for approval (Order 729)
Inactive | MOD | MOD-030 | MOD-030-2 | 1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 1.2.3. | The source/sink or POR/POD identification and mapping to the model. | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. | M1.Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 2. | The Transmission Operator shall perform the following: | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.1.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.2. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.2.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.2.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.3. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.2. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.3. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.5. | At a minimum, establish the TFC once per calendar year. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. | M2.The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: | M3.The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. | M3.The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. | M3.The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 3.3. | Updated at least once per month for AFC calculations for months two through 13. | M3.The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. | M3.The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. | M3.The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-2 | 4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: [Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | M4.The Transmission Operator shall provide evidence (such as logs and dated requests) that it updated the list of Flowgates within thirty calendar days from a request. (R2.3) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | No Parts for 4. |  | M4.The Transmission Operator shall provide evidence (such as logs and dated requests) that it updated the list of Flowgates within thirty calendar days from a request. (R2.3) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-030 | MOD-030-2 | 5. | When calculating AFCs, the Transmission Service Provider shall: | M5.The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 5.1. | Use the models provided by the Transmission Operator. | M5.The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. | M5.The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. | M5.The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2011-04-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 6.7. | The impact of other firm services determined by the Transmission Service Provider. | M6.The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 7.7. | The impact of other non-firm services determined by the Transmission Service Provider. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): See Standard for Formula. AFCF = TFC – ETCFi – CBMi – TRMi + PostbacksFi + counterflowsFi Where: AFCF is the firm Available Flowgate Capability for the Flowgate for that period. TFC is the Total Flowgate Capability of the Flowgate. ETCFi is the sum of the impacts of existing firm Transmission commitments for the Flowgate during that period. CBMi is the impact of the Capacity Benefit Margin on the Flowgate during that period. TRMi is the impact of the Transmission Reliability Margin on the Flowgate during that period. PostbacksFi are changes to firm AFC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsFi are adjustments to firm AFC as determined by the Transmission Service Provider and specified in their ATCID. | M8.The Transmission Operator shall provide evidence (such as written documentation, logs, models, and data) that the Transmission model used to determine AFCs contains the information specified in R3. (R3) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | No Parts for 8. |  | M8.The Transmission Operator shall provide evidence (such as written documentation, logs, models, and data) that the Transmission model used to determine AFCs contains the information specified in R3. (R3) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-030 | MOD-030-2 | 9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula. | M9.The Transmission Service Provider shall provide evidence (such as written documentation and data) that the modeling of point-to-point reservations was based on the rules described in R4. (R4) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | No Parts for 9. |  | M9.The Transmission Service Provider shall provide evidence (such as written documentation and data) that the modeling of point-to-point reservations was based on the rules described in R4. (R4) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-030 | MOD-030-2 | 10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: See Standard for Formula. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 10.2. | For daily AFC, once per day. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 10.3. | For monthly AFC, once per week. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 | 2010-02-08 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | 11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: See Standard for Formula. | The Transmission Service Provider shall provide evidence (such as written documentation, electronic communications, and data) that all expected generation and Transmission outages, additions, and retirements were included in the AFC calculation as specified in the ATCID. (R5.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-2 | No Parts for 11. |  | The Transmission Service Provider shall provide evidence (such as written documentation, electronic communications, and data) that all expected generation and Transmission outages, additions, and retirements were included in the AFC calculation as specified in the ATCID. (R5.2) | Operations Planning | 2009-02-10 | 2009-03-06 | 2009-11-24 | 2010-02-08 | 2011-04-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-19-000
Inactive | MOD | MOD-030 | MOD-030-3 | 1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.2.3. | The source/sink or POR/POD identification and mapping to the model. | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.2.3. DO NOT USE | The source/sink or POR/POD identification and mapping to the model. | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 2. | The Transmission Operator shall perform the following: | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.1.1. DO NOT USE | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.1.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.2. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.2.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.2.1. DO NOT USE | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.2.2. DO NOT USE | Only the most limiting element in a series configuration needs to be included as a Flowgate. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.2.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.3. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.2. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.3. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.5. | At a minimum, establish the TFC once per calendar year. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations. (R2.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.2. DO NOT USE | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.3. | Updated at least once per month for AFC calculations for months two through 13. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.3. DO NOT USE | Updated at least once per month for AFC calculations for months two through 13. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | MOD | MOD-030 | MOD-030-3 | 4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | The Transmission Operator shall provide evidence (such as logs and dated requests) that it updated the list of Flowgates within thirty calendar days from a request. (R2.3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | No Parts for 4. |  | The Transmission Operator shall provide evidence (such as logs and dated requests) that it updated the list of Flowgates within thirty calendar days from a request. (R2.3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-030 | MOD-030-3 | 5. | When calculating AFCs, the Transmission Service Provider shall | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 5.1. | Use the models provided by the Transmission Operator. | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 5.1. DO NOT USE | Use the models provided by the Transmission Operator. | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.1.2. DO NOT USE | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: (Footnote:A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.2.2. DO NOT USE | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 6.7. | The impact of other firm services determined by the Transmission Service Provider. | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 7.7. | The impact of other non-firm services determined by the Transmission Service Provider. | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): AFCF = TFC – ETCFi – CBMi – TRMi + PostbacksFi + counterflowsFi Where: AFCF is the firm Available Flowgate Capability for the Flowgate for that period. TFC is the Total Flowgate Capability of the Flowgate. ETCFi is the sum of the impacts of existing firm Transmission commitments for the Flowgate during that period. CBMi is the impact of the Capacity Benefit Margin on the Flowgate during that period. TRM¬i is the impact of the Transmission Reliability Margin on the Flowgate during that period. PostbacksF¬i are changes to firm AFC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsFi are adjustments to firm AFC as determined by the Transmission Service Provider and specified in their ATCID. | The Transmission Operator shall provide evidence (such as written documentation, logs, models, and data) that the Transmission model used to determine AFCs contains the information specified in R3. (R3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | No Parts for 8. |  | The Transmission Operator shall provide evidence (such as written documentation, logs, models, and data) that the Transmission model used to determine AFCs contains the information specified in R3. (R3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-030 | MOD-030-3 | 9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): AFCNF = TFC – ETCFi – ETCNFi – CBMSi – TRMUi + PostbacksNFi + counterflows Where: AFCNF is the non-firm Available Flowgate Capability for the Flowgate for that period. TFC is the Total Flowgate Capability of the Flowgate. ETCFi is the sum of the impacts of existing firm Transmission commitments for the Flowgate during that period. ETCNFi is the sum of the impacts of existing non-firm Transmission commitments for the Flowgate during that period. CBMSi is the impact of any schedules during that period using Capacity Benefit Margin. TRMUi is the impact on the Flowgate of the Transmission Reliability Margin that has not been released (unreleased) for sale as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm Available Flowgate Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm AFC as determined by the Transmission Service Provider and specified in their ATCID. | The Transmission Service Provider shall provide evidence (such as written documentation and data) that the modeling of point-to-point reservations was based on the rules described in R4. (R4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | No Parts for 9. |  | The Transmission Service Provider shall provide evidence (such as written documentation and data) that the modeling of point-to-point reservations was based on the rules described in R4. (R4) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-030 | MOD-030-3 | 10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 10.2. | For daily AFC, once per day. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 10.3. | For monthly AFC, once per week. | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | 11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: ATC = min(P) P ={PATC1, PATC2,…PATCn} PATCn = AFCn/DFnp Where: ATC is the Available Transfer Capability. P is the set of partial Available Transfer Capabilities for all “impacted” Flowgates honored by the Transmission Service Provider; a Flowgate is considered “impacted” by a path if the Distribution Factor for that path is greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider on an OTDF Flowgate or PTDF Flowgate. PATCn is the partial Available Transfer Capability for a path relative to a Flowgate n. AFCn is the Available Flowgate Capability of a Flowgate n. DFnp is the distribution factor for Flowgate n relative to path p. | M11. The Transmission Service Provider shall provide evidence (such as written documentation, electronic communications, and data) that all expected generation and Transmission outages, additions, and retirements were included in the AFC calculation as specified in the ATCID. (R5.2) M12. The Transmission Service Provider shall provide evidence (such as logs, electronic communications, and data) that AFCs provided by third parties on external Flowgates were used instead of those calculated by the Transmission Operator. (R5.3) M13. The Transmission Service Provider shall demonstrate compliance with R6 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the requirements defined in R6 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in this standard and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the requirements defined in R6 to calculate its firm ETC. (R6) M14. The Transmission Service Provider shall demonstrate compliance with R7 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the requirements defined in R7 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in the standard and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the requirements in R7 to calculate its non-firm ETC. (R7) M15. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates firm AFCs, as required in R8. Such documentation must show that only the variables allowed in R8 were used to calculate firm AFCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R8) M16. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates non-firm AFCs, as required in R9. Such documentation must show that only the variables allowed in R9 were used to calculate non-firm AFCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R9) M17. The Transmission Service Provider shall provide evidence (such as documentation, dated logs, and data) that it calculated AFC on the frequency defined in R10. (R10) M18. The Transmission Service Provider shall provide evidence (such as documentation and data) when converting Flowgate AFCs to ATCs for ATC Paths, it follows the procedure described in R11. (R11) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000 | [22 empty] | TSP
Inactive | MOD | MOD-030 | MOD-030-3 | No Parts for 11. |  | M11. The Transmission Service Provider shall provide evidence (such as written documentation, electronic communications, and data) that all expected generation and Transmission outages, additions, and retirements were included in the AFC calculation as specified in the ATCID. (R5.2) M12. The Transmission Service Provider shall provide evidence (such as logs, electronic communications, and data) that AFCs provided by third parties on external Flowgates were used instead of those calculated by the Transmission Operator. (R5.3) M13. The Transmission Service Provider shall demonstrate compliance with R6 by recalculating firm ETC for any specific time period as described in (MOD-001 R2), using the requirements defined in R6 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in this standard and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the requirements defined in R6 to calculate its firm ETC. (R6) M14. The Transmission Service Provider shall demonstrate compliance with R7 by recalculating non-firm ETC for any specific time period as described in (MOD-001 R2), using the requirements defined in R7 and with data used to calculate the specified value for the designated time period. The data used must meet the requirements specified in the standard and the ATCID. To account for differences that may occur when recalculating the value (due to mixing automated and manual processes), any recalculated value that is within +/- 15% or 15 MW, whichever is greater, of the originally calculated value, is evidence that the Transmission Service Provider used the requirements in R7 to calculate its non-firm ETC. (R7) M15. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates firm AFCs, as required in R8. Such documentation must show that only the variables allowed in R8 were used to calculate firm AFCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R8) M16. Each Transmission Service Provider shall produce the supporting documentation for the processes used to implement the algorithm that calculates non-firm AFCs, as required in R9. Such documentation must show that only the variables allowed in R9 were used to calculate non-firm AFCs, and that the processes use the current values for the variables as determined in the requirements or definitions. Note that any variable may legitimately be zero if the value is not applicable or calculated to be zero (such as counterflows, TRM, CBM, etc…). The supporting documentation may be provided in the same form and format as stored by the Transmission Service Provider. (R9) M17. The Transmission Service Provider shall provide evidence (such as documentation, dated logs, and data) that it calculated AFC on the frequency defined in R10. (R10) M18. The Transmission Service Provider shall provide evidence (such as documentation and data) when converting Flowgate AFCs to ATCs for ATC Paths, it follows the procedure described in R11. (R11) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-02-01 | Filing/Order Docket No. RM15-13-000
Inactive | MOD | MOD-031 | MOD-031-1 | 1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in their area. The data request shall include:[Please see the standard for more information] | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.1. | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2015-04-27 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2015-04-27 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.3. | A request to provide any or all of the following actual data, as necessary: | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2015-04-27 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.4. | A request to provide any or all of the following forecast data, as necessary: | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2015-04-27 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.5. | A request to provide any or all of the following summary explanations, as necessary,: | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2015-04-27 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | M1. The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | 2. | Each Applicable Entity, identified in the data request, shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | M2. Each Applicable Entity shall have evidence, such as dated e-mails or dated transmittal letters that it provided the requested data in accordance with Requirement R2. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | DP | [7 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031 | MOD-031-1 | No Parts for 2. |  | M2. Each Applicable Entity shall have evidence, such as dated e-mails or dated transmittal letters that it provided the requested data in accordance with Requirement R2. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000
Inactive | MOD | MOD-031 | MOD-031-1 | 3. | The Planning Coordinator or the Balancing Authority shall provide the data collected under Requirement R2 to the applicable Regional Entity within 75 days of receiving a request for such data, unless otherwise agreed upon by the parties. | M3. Each Planning Coordinator or Balancing Authority, shall have evidence, such as dated e-mails or dated transmittal letters that it provided the data requested by the applicable Regional Entity in accordance with Requirement R3. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-1 | No Parts for 3. |  | M3. Each Planning Coordinator or Balancing Authority, shall have evidence, such as dated e-mails or dated transmittal letters that it provided the data requested by the applicable Regional Entity in accordance with Requirement R3. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000
Inactive | MOD | MOD-031 | MOD-031-1 | 4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric Sysytem, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; and • shall not be required to alter the format in which it maintains or uses the data. | M4. Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | DP | [7 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031 | MOD-031-1 | 4.1. | If the Applicable Entity does not provide data requested under this requirement because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | M4. Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | Long-Term Planning | 2014-05-07 | 2014-05-13 | 2015-02-19 | 2015-04-27 | 2016-07-01 | 2015-04-27 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM14-12-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.1. | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-02-18 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-02-18 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.3. | A request to provide any or all of the following actual data, as necessary: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-02-18 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.4. | A request to provide any or all of the following forecast data, as necessary: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-02-18 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.5. | A request to provide any or all of the following summary explanations, as necessary,: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-02-18 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | 2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | M2. Each Applicable Entity shall have evidence, such as dated e-mails or dated transmittal letters that it provided the requested data in accordance with Requirement R2. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | DP | [7 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031 | MOD-031-2 | No Parts for 2. |  | M2. Each Applicable Entity shall have evidence, such as dated e-mails or dated transmittal letters that it provided the requested data in accordance with Requirement R2. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000
Inactive | MOD | MOD-031 | MOD-031-2 | 3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. | M3. Each Planning Coordinator or Balancing Authority, shall have evidence, such as dated e-mails or dated transmittal letters that it provided the data requested by the applicable Regional Entity in accordance with Requirement R3. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | [9 empty] | PA | PC
Inactive | MOD | MOD-031 | MOD-031-2 | No Parts for 3. |  | M3. Each Planning Coordinator or Balancing Authority, shall have evidence, such as dated e-mails or dated transmittal letters that it provided the data requested by the applicable Regional Entity in accordance with Requirement R3. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000
Inactive | MOD | MOD-031 | MOD-031-2 | 4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall not be required to alter the format in which it maintains or uses the data; • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements | M4. Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | DP | [7 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031 | MOD-031-2 | 4.1. | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | M4. Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | Long-Term Planning | 2015-11-05 | 2015-11-13 | 2016-02-18 | 2016-02-18 | 2016-10-01 | 2016-02-18 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD16-1-000 | BA | DP | [7 empty] | LSE | PA | PC |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.1. | A list of Transmission Planners, Balancing Authorities, and Distribution Providers that are required to provide the data (“Applicable Entities”). | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.3. | A request to provide any or all of the following actual data, as necessary: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.4. | A request to provide any or all of the following forecast data, as necessary: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.5. | A request to provide any or all of the following summary explanations, as necessary,: | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | Each Applicable Entity shall have evidence, such as dated e-mails or dated transmittal letters that it provided the requested data in accordance with Requirement R2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP | [8 empty] | PA | PC |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | No Parts for 2. |  | Each Applicable Entity shall have evidence, such as dated e-mails or dated transmittal letters that it provided the requested data in accordance with Requirement R2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. | Each Planning Coordinator or Balancing Authority, shall have evidence, such as dated e-mails or dated transmittal letters that it provided the data requested by the applicable Regional Entity in accordance with Requirement R3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | [9 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | No Parts for 3. |  | Each Planning Coordinator or Balancing Authority, shall have evidence, such as dated e-mails or dated transmittal letters that it provided the data requested by the applicable Regional Entity in accordance with Requirement R3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall not be required to alter the format in which it maintains or uses the data; • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements | Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP | [8 empty] | PA | PC |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-031 | MOD-031-3 | 4.1. | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP | [8 empty] | PA | PC |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1. | Each Planning Coordinator and each of its Transmission Planners shall jointly develop steady-state, dynamics, and short circuit modeling data requirements and reporting procedures for the Planning Coordinator’s planning area that include: [Please see the standard for more information] | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 |  | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.1. | The data listed in Attachment 1. | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.2. | Specifications of the following items consistent with procedures for building the Interconnection-wide case(s): | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.2.1. | Data format; | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.2.2. | Level of detail to which equipment shall be modeled; | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.2.3. | Case types or scenarios to be modeled; and | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.2.4. | A schedule for submission of data at least once every 13 calendar months. | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 1.3. | Specifications for distribution or posting of the data requirements and reporting procedures so that they are available to those entities responsible for providing the data. | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X |  |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 2. | Each Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. | M2. Each registered entity identified in Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted the required modeling data to its Transmission Planner(s) and Planning Coordinator(s); or written confirmation that the data has not changed. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 |  | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO | GO-2 |  |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | No Parts for 2. |  | M2. Each registered entity identified in Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted the required modeling data to its Transmission Planner(s) and Planning Coordinator(s); or written confirmation that the data has not changed. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 |  | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes.
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 3. | Upon receipt of written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2, including the technical basis or reason for the technical concerns, each notified Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider shall respond to the notifying Planning Coordinator or Transmission Planner as follows: [Please see the standard for more information] | M3. Each registered entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 |  | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO | GO-2 |  |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 3.1. | Provide either updated data or an explanation with a technical basis for maintaining the current data; | M3. Each registered entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  |  |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 3.2. | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. | M3. Each registered entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 | 2015-07-01 | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  |  |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | 4. | Each Planning Coordinator shall make available models for its planning area reflecting data provided to it under Requirement R2 to the Electric Reliability Organization (ERO) or its designee to support creation of the Interconnection-wide case(s) that includes the Planning Coordinator’s planning area. | M4. Each Planning Coordinator shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted models for its planning area reflecting data provided to it under Requirement R2 when requested by the ERO or its designee. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 |  | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes. | [10 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-032 | MOD-032-1 | No Parts for 4. |  | M4. Each Planning Coordinator shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted models for its planning area reflecting data provided to it under Requirement R2 when requested by the ERO or its designee. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2015-07-01 |  | X | MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, MOD-032-1, Requirements R2, R3, and R4 shall become effective on the first day of the first calendar quarter that is 24 months after the date the standard is adopted by the NERC Board of Trustees or as otherwise provided for in that jurisdiction. |  | 2028-03-31 | Filing/Order Docket No. RD14-5-000 Please see the implementation plan for specific compliance dates and timeframes.
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1. | Each Planning Coordinator and each of its Transmission Planners shall jointly develop steady-state, dynamics, and short circuit modeling data requirements and reporting procedures for the Planning Coordinator’s planning area that include: | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.1. | The data listed in Attachment 1, including the entity responsible for each required item. | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.2. | Specifications of the following items consistent with procedures for building the Interconnection-wide case(s): | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.2.1. | Data format; | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.2.2. | Level of detail to which equipment shall be modeled; | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.2.3. | Case types or scenarios to be modeled; and | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.2.4. | A schedule for submission of data at least once every 13 calendar months. | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.3. | Specifications for distribution or posting of the data requirements and reporting procedures so that they are available to those entities responsible for providing the data. | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.4. | Specifications of the following items for dynamic model submissions: | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.4.1. | Required submission of: • standard library models incorporated within the software(s) utilized to create the Interconnection-wide case(s); • user-defined models; or • both standard library models and user-defined models. | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.4.2. | Where user-defined models are accepted, usability requirements for any submitted user-defined models including, at a minimum, requirements to provide model documentation and instructions for model set up and use. | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 1.4.2.1. | Each Planning Coordinator and Transmission Planner shall provide their user-defined model requirements within 90 calendar days of receiving a written request for such data from other Planning Coordinators and Transmission Planners within the Interconnection. | M1. Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC | [9 empty] | TP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 2. | Each Balancing Authority, Distribution Provider, Generator Owner, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. | M2. Each functional entity identified in Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted the required modeling data to its Transmission Planner(s) and Planning Coordinator(s); or written confirmation that the data has not changed. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 2.1. | If a functional entity is required to provide data for one or more of the following and is unable to gather such data, the functional entity shall provide an estimate of the data, an explanation of the limitations of the estimated data, and the method used for estimation; • Aggregate DER data; or • Data for an IBR that is not a DER and does not meet the criteria that would require the owner to register with NERC for mandatory Reliability Standards compliance purposes. | M2. Each functional entity identified in Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted the required modeling data to its Transmission Planner(s) and Planning Coordinator(s); or written confirmation that the data has not changed. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 2.2. | If a functional entity is required to provide dynamic models, the functional entity shall provide the models accepted by the Transmission Planner under MOD-026, where such models are available. | M2. Each functional entity identified in Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted the required modeling data to its Transmission Planner(s) and Planning Coordinator(s); or written confirmation that the data has not changed. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 2.3. | If a functional entity provides a model that is included on the Unacceptable Models List maintained by the ERO in accordance with the process described in the MOD-032 Supporting Document, the functional entity shall also provide a technical rationale justifying the use of that model. | M2. Each functional entity identified in Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted the required modeling data to its Transmission Planner(s) and Planning Coordinator(s); or written confirmation that the data has not changed. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 3. | Upon receipt of written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2, including the technical basis or reason for the technical concerns, each notified Balancing Authority, Distribution Provider, Generator Owner, Resource Planner, Transmission Owner, or Transmission Service Provider shall respond to the notifying Planning Coordinator or Transmission Planner as follows: | M3. Each functional entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 3.1. | Provide either updated data or an explanation with a technical basis for maintaining the current data that is responsive to the technical concern. | M3. Each functional entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 3.2. | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. | M3. Each functional entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | BA | DP |  |  | GO | [10 empty] | RP |  |  |  | TO |  |  | TSP
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | 4. | Each Planning Coordinator shall make available models for its planning area reflecting data provided to it under Requirement R2 to the Electric Reliability Organization (ERO) or its designee to support creation of the Interconnection-wide case(s) that includes the Planning Coordinator’s planning area. | Each Planning Coordinator shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted models for its planning area reflecting data provided to it under Requirement R2 when requested by the ERO or its designee. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin | [10 empty] | PA | PC
Subject to Future Enforcement | MOD | MOD-032 | MOD-032-2 | No Parts for 4. |  | Each Planning Coordinator shall provide evidence, such as email records or postal receipts showing recipient and date, that it has submitted models for its planning area reflecting data provided to it under Requirement R2 when requested by the ERO or its designee. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 |  | X |  |  |  | Filing/Order Docket No. RD26-1-000 Additional Effective Date Details Requirements R2, R3, and R4 - April 1, 2029 Entities shall not be required to comply with Requirements R2, R3, and R4 relating to revised Planning Coordin
Inactive | MOD | MOD-033 | MOD-033-1 | 1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes:[Please see the standard for more information] | M1. Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-1 | 1.1. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; | M1. Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 | 2014-05-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-1 | 1.2. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; | M1. Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 | 2014-05-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-1 | 1.3. | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and | M1. Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 | 2014-05-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-1 | 1.4. | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. | M1. Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 | 2014-05-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-1 | 2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real-time data (including disturbance data recordings) necessary for actual system response validation. | M2. Each Reliability Coordinator and Transmission Operator shall provide evidence, such as email notices or postal receipts showing recipient and date that it has distributed the requested data or written response that it does not have the data, to any Planning Coordinator performing validation under Requirement R1 within 30 days of a written request in accordance with Requirement R2; or a statement by the Reliability Coordinator or Transmission Operator that it has not received notification regarding data necessary for validation by any Planning Coordinator. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | MOD | MOD-033 | MOD-033-1 | No Parts for 2. |  | M2. Each Reliability Coordinator and Transmission Operator shall provide evidence, such as email notices or postal receipts showing recipient and date that it has distributed the requested data or written response that it does not have the data, to any Planning Coordinator performing validation under Requirement R1 within 30 days of a written request in accordance with Requirement R2; or a statement by the Reliability Coordinator or Transmission Operator that it has not received notification regarding data necessary for validation by any Planning Coordinator. | Long-Term Planning | 2014-02-06 | 2014-02-25 | 2014-05-01 | 2014-05-01 | 2017-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-5-000
Inactive | MOD | MOD-033 | MOD-033-2 | 1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes:[Please see the standard for more information] | Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-2 | 1.1. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; | Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-2 | 1.2. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; | Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-2 | 1.3. | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and | Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-2 | 1.4. | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. | Each Planning Coordinator shall provide evidence that it has a documented validation process according to Requirement R1 as well as evidence that demonstrates the implementation of the required components of the process. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | MOD | MOD-033 | MOD-033-2 | 2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real-time data (including disturbance data recordings) necessary for actual system response validation. | M2. Each Reliability Coordinator and Transmission Operator shall provide evidence, such as email notices or postal receipts showing recipient and date that it has distributed the requested data or written response that it does not have the data, to any Planning Coordinator performing validation under Requirement R1 within 30 days of a written request in accordance with Requirement R2; or a statement by the Reliability Coordinator or Transmission Operator that it has not received notification regarding data necessary for validation by any Planning Coordinator. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | MOD | MOD-033 | MOD-033-2 | No Parts for 2. |  | M2. Each Reliability Coordinator and Transmission Operator shall provide evidence, such as email notices or postal receipts showing recipient and date that it has distributed the requested data or written response that it does not have the data, to any Planning Coordinator performing validation under Requirement R1 within 30 days of a written request in accordance with Requirement R2; or a statement by the Reliability Coordinator or Transmission Operator that it has not received notification regarding data necessary for validation by any Planning Coordinator. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | 1. | Each Planning Coordinator shall implement a documented Model Validation process for planning System models developed in accordance with Reliability Standard MOD 032, [1] representing its portion of the existing System, that includes the following attributes: [1] Such planning System models will thus include registered IBRs and aggregated DERs, as well as IBRs that are not DERs and that do not meet the criteria that would require the owner(s) to register with NERC for mandatory Reliability Standards compliance purposes, that are present in the existing System. | M1. Acceptable evidence may include, but is not limited to, a copy of the documented Model Validation process and documentation that demonstrates its implementation in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | [5 empty] | Filing/Order Docket No. RD26-2-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | 1.1. | Comparison of the power flow simulation performance of the steady state planning System model to actual System behavior, represented by state estimator case(s) or other Real-time data sources, at least once every 24 calendar months; | M1. Acceptable evidence may include, but is not limited to, a copy of the documented Model Validation process and documentation that demonstrates its implementation in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | 2026-04-01 |  |  |  |  | Filing/Order Docket No. RD26-2-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | 1.2. | Comparison of the dynamic local event simulation performance of the dynamic planning System model to actual System behavior, represented by Real-time data sources such as Disturbance data recording(s), at least once every 24 calendar months (using a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison) and completing each comparison within 24 calendar months of the dynamic local event. If no dynamic local event occurs within this 24 calendar months period, use the next dynamic local event that occurs | M1. Acceptable evidence may include, but is not limited to, a copy of the documented Model Validation process and documentation that demonstrates its implementation in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | 2026-04-01 |  |  |  |  | Filing/Order Docket No. RD26-2-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | 1.3. | Guidelines to determine unacceptable differences in performance under Parts 1.1 and 1.2 including those for generating facilities in the planning System model; and | M1. Acceptable evidence may include, but is not limited to, a copy of the documented Model Validation process and documentation that demonstrates its implementation in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | 2026-04-01 |  |  |  |  | Filing/Order Docket No. RD26-2-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | 1.4. | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. | M1. Acceptable evidence may include, but is not limited to, a copy of the documented Model Validation process and documentation that demonstrates its implementation in accordance with Requirement R1. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | 2026-04-01 |  |  |  |  | Filing/Order Docket No. RD26-2-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | 2. | Each Reliability Coordinator and Transmission Operator shall, within 30 calendar days of a written request, provide actual System behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing Model Validation under Requirement R1. [Violation Risk Factor: Lower] [Time Horizon: Long term Planning] | M2. Acceptable evidence may include, but is not limited to, a copy of the dated communication(s) in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | [5 empty] | Filing/Order Docket No. RD26-2-000 | [13 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | MOD | MOD-033 | MOD-033-3 | No Parts for 2. |  | M2. Acceptable evidence may include, but is not limited to, a copy of the dated communication(s) in accordance with Requirement R2. | Long-Term Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2026-04-01 | [5 empty] | Filing/Order Docket No. RD26-2-000
Inactive | NUC | NUC-001 | NUC-001-1 | 1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 1. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 2. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 3. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 4.2. | Operate the electric system to meet the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 5. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 6. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 7. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | No Parts for 8. |  |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-1 | 9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.1. | Administrative elements: |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.1.1. | Definitions of key terms used in the agreement. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.1.2. | Names of the responsible entities, organizational relationships, andresponsibilities related to the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.1.3. | A requirement to review the agreement(s) at least every three years. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.1.4. | A dispute resolution mechanism. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.2. | Technical requirements and analysis: |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.2.1. | Identification of parameters, limits, configurations, and operatingscenarios included in the NPIRs and, as applicable, procedures forproviding any specific data not provided within the agreement. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.2.2. | Identification of facilities, components, and configuration restrictionsthat are essential for meeting the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3. | Operations and maintenance coordination: |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.5. | Provision to consider nuclear plant coping times required by the NPLRs and their relation to the coordination of grid and nuclear plant restoration following a nuclear plant loss of Off-site Power. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.4. | Communications and training: |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 |  | 2008-11-26 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-1 | 9.4.5. | Provisions for personnel training, as related to NPIRs. |  |  | 2007-05-02 | 2007-11-19 | 2008-10-16 | 2008-11-26 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt [Risk Factor: Lower] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 1. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Risk Factor: Medium] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 2. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 3. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 4.2. | Operate the electric system to meet the NPIRs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 5. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 6. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 7. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | No Parts for 8. |  |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000
Inactive | NUC | NUC-001 | NUC-001-2 | 9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.1. | Administrative elements: |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.1.1. | Definitions of key terms used in the agreement. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.1.3. | A requirement to review the agreement(s) at least every three years. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.1.4. | A dispute resolution mechanism. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.2. | Technical requirements and analysis: |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3. | Operations and maintenance coordination: |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.4. | Communications and training: |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2 | 9.4.5. | Provisions for personnel training, as related to NPIRs. |  |  | 2009-08-05 | 2009-08-14 | 2010-01-21 | 2010-01-21 | 2010-04-01 | 2010-04-01 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM08-3-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt | M1. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide a copy of the transmittal and receipt of transmittal of the proposed NPIRs to the responsible Transmission Entities. (Requirement 1) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 1. |  | M1. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide a copy of the transmittal and receipt of transmittal of the proposed NPIRs to the responsible Transmission Entities. (Requirement 1) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | M2. The Nuclear Plant Generator Operator and each Transmission Entity shall each have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. (Requirement 2 and 9) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 2. |  | M2. The Nuclear Plant Generator Operator and each Transmission Entity shall each have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. (Requirement 2 and 9) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | M3. Each Transmission Entity responsible for planning analyses in accordance with the Agreement shall, upon request of the Compliance Enforcement Authority, provide a copy of the planning analyses results transmitted to the Nuclear Plant Generator Operator, showing incorporation of the NPIRs. The Compliance Enforcement Authority shall refer to the Agreements developed in accordance with this standard for specific requirements. (Requirement 3) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 3. |  | M3. Each Transmission Entity responsible for planning analyses in accordance with the Agreement shall, upon request of the Compliance Enforcement Authority, provide a copy of the planning analyses results transmitted to the Nuclear Plant Generator Operator, showing incorporation of the NPIRs. The Compliance Enforcement Authority shall refer to the Agreements developed in accordance with this standard for specific requirements. (Requirement 3) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 4.2. | Operate the electric system to meet the NPIRs. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | M5. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, demonstrate or provide evidence that the Nuclear Power Plant is being operated consistent with the Agreements developed in accordance with this standard. (Requirement 5) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 5. |  | M5. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, demonstrate or provide evidence that the Nuclear Power Plant is being operated consistent with the Agreements developed in accordance with this standard. (Requirement 5) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | M6. The Transmission Entities and Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide evidence of the coordination between the Transmission Entities and the Nuclear Plant Generator Operator regarding outages and maintenance activities which affect the NPIRs. (Requirement 6) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 6. |  | M6. The Transmission Entities and Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide evidence of the coordination between the Transmission Entities and the Nuclear Plant Generator Operator regarding outages and maintenance activities which affect the NPIRs. (Requirement 6) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | M7. The Nuclear Plant Generator Operator shall provide evidence that it informed the applicable Transmission Entities of changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that would impact the ability of the Transmission Entities to meet the NPIRs. (Requirement 7) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 7. |  | M7. The Nuclear Plant Generator Operator shall provide evidence that it informed the applicable Transmission Entities of changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that would impact the ability of the Transmission Entities to meet the NPIRs. (Requirement 7) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | M8. The Transmission Entities shall each provide evidence that it informed the Nuclear Plant Generator Operator of changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that would impact the ability of the Nuclear Plant Generator Operator to meet the NPIRs. (Requirement 8) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | No Parts for 8. |  | M8. The Transmission Entities shall each provide evidence that it informed the Nuclear Plant Generator Operator of changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that would impact the ability of the Nuclear Plant Generator Operator to meet the NPIRs. (Requirement 8) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.1. | Administrative elements: |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.1.1. | Definitions of key terms used in the agreement. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.1.3. | A requirement to review the agreement(s) at least every three years. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.1.4. | A dispute resolution mechanism. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.2. | Technical requirements and analysis: |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3. | Operations and maintenance coordination: |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.4. | Communications and training: |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1 | 9.4.5. | Provisions for personnel training, as related to NPIRs. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-12-31 | Approved by the Standards Committee | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 1. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 3. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 4.2. | Operate the electric system to meet the NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 5. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 6. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 7. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | No Parts for 8. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.1. | Administrative elements: (Retirement approved by FERC effective January 21, 2014.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.1.1. | Definitions of key terms used in the agreement. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.1.3. | A requirement to review the agreement(s) at least every three years. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.1.4. | A dispute resolution mechanism. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.2. | Technical requirements and analysis: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3. | Operations and maintenance coordination: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and underfrequency and undervoltage load shedding programs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.4. | Communications and training: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-2.1(i) | 9.4.5. | Provisions for personnel training, as related to NPIRs. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 1. | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | M1. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide a copy of the transmittal and receipt of transmittal of the proposed NPIRs to the responsible Transmission Entities. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 1. |  | M1. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide a copy of the transmittal and receipt of transmittal of the proposed NPIRs to the responsible Transmission Entities. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs (Footnote: Agreements may include mutually agreed upon procedures or protocols in effect between entities or between departments of a vertically integrated system.) | M2. The Nuclear Plant Generator Operator and each Transmission Entity shall each have a copy of the currently effective Agreement(s) which document how the Nuclear Plant Generator Operator and the applicable Transmission Entities address and implement the NPIRs available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 2. |  | M2. The Nuclear Plant Generator Operator and each Transmission Entity shall each have a copy of the currently effective Agreement(s) which document how the Nuclear Plant Generator Operator and the applicable Transmission Entities address and implement the NPIRs available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | M3. Each Transmission Entity responsible for planning analyses in accordance with the Agreement shall, upon request of the Compliance Enforcement Authority, provide a copy of the planning analyses results transmitted to the Nuclear Plant Generator Operator, showing incorporation of the NPIRs. The Compliance Enforcement Authority shall refer to the Agreements developed in accordance with this standard for specific requirements. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 3. |  | M3. Each Transmission Entity responsible for planning analyses in accordance with the Agreement shall, upon request of the Compliance Enforcement Authority, provide a copy of the planning analyses results transmitted to the Nuclear Plant Generator Operator, showing incorporation of the NPIRs. The Compliance Enforcement Authority shall refer to the Agreements developed in accordance with this standard for specific requirements. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 4.2. | Operate the electric system to meet the NPIRs. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | M5. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, demonstrate or provide evidence that the nuclear power plant is being operated consistent with the NPIRs. | Operations Planning, Real-Time Operations | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 5. |  | M5. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, demonstrate or provide evidence that the nuclear power plant is being operated consistent with the NPIRs. | Operations Planning, Real-Time Operations | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | M6. The Transmission Entities and Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide evidence of the coordination between the Transmission Entities and the Nuclear Plant Generator Operator regarding outages and maintenance activities which affect the NPIRs. | Operations Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 6. |  | M6. The Transmission Entities and Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide evidence of the coordination between the Transmission Entities and the Nuclear Plant Generator Operator regarding outages and maintenance activities which affect the NPIRs. | Operations Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | M7. The Nuclear Plant Generator Operator shall provide evidence that it informed the applicable Transmission Entities of changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Transmission Entities to meet the NPIRs. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | [6 empty] | GOP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 7. |  | M7. The Nuclear Plant Generator Operator shall provide evidence that it informed the applicable Transmission Entities of changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Transmission Entities to meet the NPIRs. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | M8. The Transmission Entities shall each provide evidence that the entities informed the Nuclear Plant Generator Operator of changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Nuclear Plant Generator Operator to meet the NPIRs. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  |  |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | No Parts for 8. |  | M8. The Transmission Entities shall each provide evidence that the entities informed the Nuclear Plant Generator Operator of changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Nuclear Plant Generator Operator to meet the NPIRs. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000
Inactive | NUC | NUC-001 | NUC-001-3 | 9. | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.1. | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.2. | Technical requirements and analysis: | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC |  | RP |  |  |  | TO | TOP |  | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3. | Operations and maintenance coordination | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.6. | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s pla | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC | [6 empty] | RSG | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.4. | Communications and training Administrative elements: | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2014-11-04 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.4.1. | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001 | NUC-001-3 | 9.4.5. | Provisions for personnel training, as related to NPIRs | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2014-08-14 | 2014-09-15 | 2014-11-04 | 2014-11-04 | 2016-01-01 | 2016-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-13-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | M1. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide a copy of the transmittal and receipt of transmittal of the proposed NPIRs to the responsible Transmission Entities. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 1. |  | M1. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide a copy of the transmittal and receipt of transmittal of the proposed NPIRs to the responsible Transmission Entities. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs | M2. The Nuclear Plant Generator Operator and each Transmission Entity shall each have a copy of the currently effective Agreement(s) which document how the Nuclear Plant Generator Operator and the applicable Transmission Entities address and implement the NPIRs available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 2. |  | M2. The Nuclear Plant Generator Operator and each Transmission Entity shall each have a copy of the currently effective Agreement(s) which document how the Nuclear Plant Generator Operator and the applicable Transmission Entities address and implement the NPIRs available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | M3. Each Transmission Entity responsible for planning analyses in accordance with the Agreement shall, upon request of the Compliance Enforcement Authority, provide a copy of the planning analyses results transmitted to the Nuclear Plant Generator Operator, showing incorporation of the NPIRs. The Compliance Enforcement Authority shall refer to the Agreements developed in accordance with this standard for specific requirements. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 3. |  | M3. Each Transmission Entity responsible for planning analyses in accordance with the Agreement shall, upon request of the Compliance Enforcement Authority, provide a copy of the planning analyses results transmitted to the Nuclear Plant Generator Operator, showing incorporation of the NPIRs. The Compliance Enforcement Authority shall refer to the Agreements developed in accordance with this standard for specific requirements. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 4.2. | Operate the electric system to meet the NPIRs. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | M4. Each Transmission Entity responsible for operating the electric system in accordance with the Agreement shall demonstrate or provide evidence of the following, upon request of the Compliance Enforcement Authority: • The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) • The electric system was operated to meet the NPIRs. (Requirement 4.2) • The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs | Operations Planning, Real-Time Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | M5. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, demonstrate or provide evidence that the nuclear power plant is being operated consistent with the NPIRs. | Operations Planning, Real-Time Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 5. |  | M5. The Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, demonstrate or provide evidence that the nuclear power plant is being operated consistent with the NPIRs. | Operations Planning, Real-Time Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | M6. The Transmission Entities and Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide evidence of the coordination between the Transmission Entities and the Nuclear Plant Generator Operator regarding outages and maintenance activities which affect the NPIRs. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 6. |  | M6. The Transmission Entities and Nuclear Plant Generator Operator shall, upon request of the Compliance Enforcement Authority, provide evidence of the coordination between the Transmission Entities and the Nuclear Plant Generator Operator regarding outages and maintenance activities which affect the NPIRs. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | M7. The Nuclear Plant Generator Operator shall provide evidence that it informed the applicable Transmission Entities of changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Transmission Entities to meet the NPIRs. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 7. |  | M7. The Nuclear Plant Generator Operator shall provide evidence that it informed the applicable Transmission Entities of changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Transmission Entities to meet the NPIRs. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | M8. The Transmission Entities shall each provide evidence that the entities informed the Nuclear Plant Generator Operator of changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Nuclear Plant Generator Operator to meet the NPIRs. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  |  |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | No Parts for 8. |  | M8. The Transmission Entities shall each provide evidence that the entities informed the Nuclear Plant Generator Operator of changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the Nuclear Plant Generator Operator to meet the NPIRs. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.1. | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.2. | Technical requirements and analysis: | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3. | Operations and maintenance coordination | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.6. | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.4. | Communications and training Administrative elements: | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.4.1. | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001 | NUC-001-4 | 9.4.5. | Provisions for personnel training, as related to NPIRs | M9. The Nuclear Plant Generator Operator shall have a copy of the Agreement(s) addressing the elements in Requirement 9 available for inspection upon request of the Compliance Enforcement Authority. Each Transmission Entity shall have a copy of the Agreement(s) addressing the elements in Requirement 9 for which it is responsible available for inspection upon request of the Compliance Enforcement Authority. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP |  |  |  | PA | PC |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | PER | PER-001 | PER-001-0 | 1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-001 | PER-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM06-16-000
Inactive | PER | PER-001 | PER-001-0.1 | 1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-9-000 | BA | [19 empty] | TOP
Inactive | PER | PER-001 | PER-001-0.1 | No Parts for 1. |  |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-9-000
Inactive | PER | PER-001 | PER-001-0.2 | 1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | The Transmission Operator and Balancing Authority provide documentation that operating personnel have the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. These responsibilities and authorities are understood by the operating personnel. Documentation shall include: | Real-Time Operations | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | PER | PER-001 | PER-001-0.2 | No Parts for 1. |  | The Transmission Operator and Balancing Authority provide documentation that operating personnel have the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. These responsibilities and authorities are understood by the operating personnel. Documentation shall include: | Real-Time Operations | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | PER | PER-002 | PER-002-0 | 1. | Each Transmission Operator and Balancing Authority shall be staffed with adequately trained operating personnel. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PER | PER-002 | PER-002-0 | 2. | Each Transmission Operator and Balancing Authority shall have a training program for all operating personnel that are in: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 2.1. | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 2.2. | Positions directly responsible for complying with NERC standards. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 3. | For personnel identified in Requirement R2, the Transmission Operator and Balancing Authority shall provide a training program meeting the following criteria: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 3.1. | A set of training program objectives must be defined, based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements. These objectives shall reference the knowledge and competencies needed to apply those standards, procedures, and requirements to normal, emergency, and restoration conditions for the Transmission Operator and Balancing Authority operating positions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 3.2. | The training program must include a plan for the initial and continuing training of Transmission Operator and Balancing Authority operating personnel. That plan shall address knowledge and competencies required for reliable system operations. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 3.3. | The training program must include training time for all Transmission Operator and Balancing Authority operating personnel to ensure their operating proficiency. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 3.4. | Training staff must be identified, and the staff must be competent in both knowledge of system operations and instructional capabilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | 4. | For personnel identified in Requirement R2, each Transmission Operator and Balancing Authority shall provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | PER | PER-002 | PER-002-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PER | PER-003 | PER-003-0 | 1. | Each Transmission Operator, Balancing Authority, and Reliability Coordinator shall staff all operating positions that meet both of the following criteria with personnel that are NERC-certified for the applicable functions: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-09-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-003 | PER-003-0 | 1.1. | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-09-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-003 | PER-003-0 | 1.2. | Positions directly responsible for complying with NERC standards. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-09-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate: Note: Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1. | Areas of Competency |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2011-09-15 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.1. | Resource and demand balancing |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.2. | Transmission operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.3. | Emergency preparedness and operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.4. | System operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.5. | Protection and control |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.6. | Voltage and reactive |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.7. | Interchange scheduling and coordination |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 1.1.8. | Interconnection reliability operations and coordination |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [13 empty] | RC
Inactive | PER | PER-003 | PER-003-1 | 2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: Note: Non-NERC certified personnel performing any reliability-related task of an operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.1. | Areas of Competency |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2011-09-15 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.1.1. | Transmission operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.1.2. | Emergency preparedness and operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.1.3. | System operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.1.4. | Protection and control |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.1.5. | Voltage and reactive |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 2.2. | Certificates: • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2011-09-15 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | [20 empty] | TOP
Inactive | PER | PER-003 | PER-003-1 | 3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: Note: Non-NERC certified personnel performing any reliability-related task of an operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Inactive | PER | PER-003 | PER-003-1 | 3.1. | Areas of Competency |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2011-09-15 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Inactive | PER | PER-003 | PER-003-1 | 3.1.1. | Resources and demand balancing |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Inactive | PER | PER-003 | PER-003-1 | 3.1.2. | Emergency preparedness and operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Inactive | PER | PER-003 | PER-003-1 | 3.1.3. | System operations |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Inactive | PER | PER-003 | PER-003-1 | 3.1.4. | Interchange scheduling and coordination |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2012-10-01 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Inactive | PER | PER-003 | PER-003-1 | 3.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator |  | Real-Time Operations | 2011-02-17 | 2011-04-29 | 2011-09-15 | 2011-09-15 | 2012-10-01 | 2011-09-15 |  |  |  | 2019-06-30 | Filing/Order Docket No. RD11-7-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate (Footnote: Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. The NERC certificates referenced in this standard pertain to those certificates identified in the NERC System Operator Certification Program Manual. | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | [5 empty] | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1. | Areas of Competency | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2018-11-21 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.1. | Resource and demand balancing | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.2. | Transmission operations | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.3. | Emergency preparedness and operations | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.4. | System operations | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.5. | Protection and control | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.6. | Voltage and reactive | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.7. | Interchange scheduling and coordination | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 1.1.8. | Interconnection reliability operations and coordination | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates. (Footnote: 1 Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. The NERC certificates referenced in this standard pertain to those certificates identified in the NERC System Operator Certification Program Manual.) | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | [5 empty] | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.1. | Areas of Competency | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2018-11-21 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.1.1. | Transmission operations | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.1.2. | Emergency preparedness and operations | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.1.3. | System operations | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.1.4. | Protection and control | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.1.5. | Voltage and reactive | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 2.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | M2. Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Long-Term Planning, Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2018-11-21 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (Footnote: 1 Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. The NERC certificates referenced in this standard pertain to those certificates identified in the NERC System Operator Certification Program Manual.) | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | [5 empty] | Filing/Order Docket No. RM18-16-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3.1. | Areas of Competency | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2018-11-21 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3.1.1. | Resources and demand balancing | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3.1.2. | Emergency preparedness and operations | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3.1.3. | System operations | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3.1.4. | Interchange scheduling and coordination | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2019-07-01 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | BA
Mandatory Subject to Enforcement | PER | PER-003 | PER-003-2 | 3.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | M3. Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M3.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | Real-Time Operations | 2018-05-10 | 2018-07-23 | 2018-11-21 | 2018-11-21 | 2019-07-01 | 2018-11-21 |  |  |  |  | Filing/Order Docket No. RM18-16-000 | BA
Inactive | PER | PER-004 | PER-004-0 | 1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | Not specified. | Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-0 | No Parts for 1. |  | Not specified. | Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable
Inactive | PER | PER-004 | PER-004-0 | 2. | All Reliability Coordinator operating personnel shall each complete a minimum of five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. |  | Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-0 | No Parts for 2. |  |  | Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable
Inactive | PER | PER-004 | PER-004-0 | 3. | Reliability Coordinator operating personnel shall have a comprehensive understanding of the Reliability Coordinator Area and interactions with neighboring Reliability Coordinator Areas. |  | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-0 | No Parts for 3. |  |  | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable
Inactive | PER | PER-004 | PER-004-0 | 4. | Reliability Coordinator operating personnel shall have an extensive understanding of the Balancing Authorities, Transmission Operators, and Generation Operators within the Reliability Coordinator Area, including the operating staff, operating practices and procedures, restoration priorities and objectives, outage plans, equipment capabilities, and operational restrictions. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-0 | No Parts for 4. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable
Inactive | PER | PER-004 | PER-004-0 | 5. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-0 | No Parts for 5. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PER-004-0 was never enforceable
Inactive | PER | PER-004 | PER-004-1 | 1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-1 | No Parts for 1. |  |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PER | PER-004 | PER-004-1 | 2. | All Reliability Coordinator operating personnel shall each complete a minimum of five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-1 | No Parts for 2. |  |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PER | PER-004 | PER-004-1 | 3. | Reliability Coordinator operating personnel shall have a comprehensive understanding of the Reliability Coordinator Area and interactions with neighboring Reliability Coordinator Areas. |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-1 | No Parts for 3. |  |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PER | PER-004 | PER-004-1 | 4. | Reliability Coordinator operating personnel shall have an extensive understanding of the Balancing Authorities, Transmission Operators, and Generation Operators within the Reliability Coordinator Area, including the operating staff, operating practices and procedures, restoration priorities and objectives, outage plans, equipment capabilities, and operational restrictions. |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-1 | No Parts for 4. |  |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PER | PER-004 | PER-004-1 | 5. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-1 | No Parts for 5. |  |  | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PER | PER-004 | PER-004-2 | 1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. |  | Real-Time Operations | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2011-04-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RM09-25-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-2 | No Parts for 1. |  |  | Real-Time Operations | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2011-04-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RM09-25-000
Inactive | PER | PER-004 | PER-004-2 | 2. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. |  | Real-Time Operations | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2011-04-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RM09-25-000 | [13 empty] | RC
Inactive | PER | PER-004 | PER-004-2 | No Parts for 2. |  |  | Real-Time Operations | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2011-04-01 |  |  |  |  | 2019-06-30 | Filing/Order Docket No. RM09-25-000
Inactive | PER | PER-005 | PER-005-1 | 1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall use a systematic approach to training to establish a training program for the BES company-specific reliability-related tasks performed by its System Operators and shall implement the program. | M1. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence of using a systematic approach to training to establish and implement a training program, as specified in R1. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 1.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall create a list of BES company-specific reliability-related tasks performed by its System Operators. | M1. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence of using a systematic approach to training to establish and implement a training program, as specified in R1. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 | 2013-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 1.1.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall update its list of BES company-specific reliability-related tasks performed by its System Operators each calendar year to identify new or modified tasks for inclusion in training. | M1. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence of using a systematic approach to training to establish and implement a training program, as specified in R1. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 | 2013-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 1.2. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall design and develop learning objectives and training materials based on the task list created in R1.1. | M1. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence of using a systematic approach to training to establish and implement a training program, as specified in R1. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 | 2013-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 1.3. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall deliver the training established in R1.2. | M1. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence of using a systematic approach to training to establish and implement a training program, as specified in R1. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 | 2013-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 1.4. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall conduct an annual evaluation of the training program established in R1, to identify any needed changes to the training program and shall implement the changes identified. | M1. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence of using a systematic approach to training to establish and implement a training program, as specified in R1. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 | 2013-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 2. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform each assigned task identified in R1.1 at least one time. [Time Horizon: Long-term Planning] | M2. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence to show that it verified that each of its System Operators is capable of performing each assigned task identified in R1.1, as specified in R2. This evidence can be documents such as training records showing successful completion of tasks with the employee name and date; supervisor check sheets showing the employee name, date, and task completed; or the results of learning assessments. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 2.1. | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. | M2. Each Reliability Coordinator, Balancing Authority and Transmission Operator shall have available for inspection evidence to show that it verified that each of its System Operators is capable of performing each assigned task identified in R1.1, as specified in R2. This evidence can be documents such as training records showing successful completion of tasks with the employee name and date; supervisor check sheets showing the employee name, date, and task completed; or the results of learning assessments. | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2013-04-01 | 2013-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 3. | At least every 12 months each Reliability Coordinator, Balancing Authority and Transmission Operator shall provide each of its System Operators with at least 32 hours of emergency operations training applicable to its organization that reflects emergency operations topics, which includes system restoration using drills, exercises or other training required to maintain qualified personnel. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] |  | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2011-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005 | PER-005-1 | 3.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator that has operational authority or control over Facilities with established IROLs or has established operating guides or protection systems to mitigate IROL violations shall provide each System Operator with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES during normal and emergency conditions. |  | Long-Term Planning | 2009-02-10 | 2009-09-30 | 2010-11-18 | 2011-01-25 | 2011-04-01 | 2014-04-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM09-25-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 1.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 1.1.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 1.2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 1.3. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 1.4. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 2. | Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: | M2. Each Transmission Owner shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its applicable personnel, as specified in Requirement R2. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD14-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 2.1. | Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. | M2. Each Transmission Owner shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its applicable personnel, as specified in Requirement R2. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 2.1.1. | Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. | M2. Each Transmission Owner shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its applicable personnel, as specified in Requirement R2. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 2.2. | Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. | M2. Each Transmission Owner shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its applicable personnel, as specified in Requirement R2. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 2.3. | Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. | M2. Each Transmission Owner shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its applicable personnel, as specified in Requirement R2. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 2.4. | Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | M2. Each Transmission Owner shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its applicable personnel, as specified in Requirement R2. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. | M3. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection evidence to show that it verified the capabilities of each of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. This evidence may be documents such as records showing capability to perform BES company-specific Real-time reliability-related tasks with the employee name and date; supervisor check sheets showing the employee name, date, and BES company-specific Real-time reliability-related task completed; or the results of learning assessments. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 3.1 . | Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | M3. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection evidence to show that it verified the capabilities of each of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. This evidence may be documents such as records showing capability to perform BES company-specific Real-time reliability-related tasks with the employee name and date; supervisor check sheets showing the employee name, date, and BES company-specific Real-time reliability-related task completed; or the results of learning assessments. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. | M4. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection training records that provide evidence that personnel identified in Requirement R1 or Requirement R2 completed training that includes the use of simulation technology, as specified in Requirement R4. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 4.1. | A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | M4. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection training records that provide evidence that personnel identified in Requirement R1 or Requirement R2 completed training that includes the use of simulation technology, as specified in Requirement R4. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. | M5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence that Operations Support Personnel completed training in accordance with its systematic approach. This evidence may be documents such as training records showing successful completion of training. Documentation of training shall include employee name and date of training. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 5.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | M5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence that Operations Support Personnel completed training in accordance with its systematic approach. This evidence may be documents such as training records showing successful completion of training. Documentation of training shall include employee name and date of training. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 6. | Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. | M6. Each Generator Operator shall have available for inspection evidence that its applicable personnel completed training in accordance with its systematic approach. This evidence may be documents such as training records showing successful completion of training. Documentation of training shall include employee name and date of training. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD14-7-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | PER | PER-005 | PER-005-2 | 6.1. | Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | M6. Each Generator Operator shall have available for inspection evidence that its applicable personnel completed training in accordance with its systematic approach. This evidence may be documents such as training records showing successful completion of training. Documentation of training shall include employee name and date of training. | Long-Term Planning | 2014-02-06 | 2014-03-07 | 2014-06-19 | 2014-06-19 | 2016-07-01 | 2014-06-19 |  |  |  |  | Filing/Order Docket No. RD14-7-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | PER | PER-006 | PER-006-1 | 1. | Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | M1. Each Generator Operator shall have available for inspection, evidence that the applicable personnel completed training. This evidence may be documents such as training records showing successful completion of training that includes training materials, the name of the person, and date of training. | Long-Term Planning | 2016-08-11 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | PER | PER-006 | PER-006-1 | No Parts for 1. |  | M1. Each Generator Operator shall have available for inspection, evidence that the applicable personnel completed training. This evidence may be documents such as training records showing successful completion of training that includes training materials, the name of the person, and date of training. | Long-Term Planning | 2016-08-11 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000
Inactive | PRC | PRC-001 | PRC-001-0 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable
Inactive | PRC | PRC-001 | PRC-001-0 | 2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | 2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-0 | 2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | 3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | 3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-0 | 3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | 4. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable
Inactive | PRC | PRC-001 | PRC-001-0 | 5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | 5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-0 | 5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | 6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable | BA | [19 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-001-0 was never enforceable
Inactive | PRC | PRC-001 | PRC-001-1 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PRC | PRC-001 | PRC-001-1 | 2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | 2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1 | 2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | 3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | 3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1 | 3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | 4. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PRC | PRC-001 | PRC-001-1 | 5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | 5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1 | 5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | 6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | PRC | PRC-001 | PRC-001-1.1 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 3, 3.1, and 3.2. |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | No Parts for 1. |  | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 3, 3.1, and 3.2. |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee
Inactive | PRC | PRC-001 | PRC-001-1.1 | 2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Special Protection Systems in its area. (Requirement 6 Part 1) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Special Protection Systems in its area. (Requirement 6 Part 1) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-05-28 | Approved by the Standards Committee | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Special Protection Systems in its area. (Requirement 6 Part 1) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-05-28 | Approved by the Standards Committee | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Special Protection Systems. (Requirement 6 Part 2) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Special Protection Systems. (Requirement 6 Part 2) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-05-28 | Approved by the Standards Committee | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Special Protection Systems. (Requirement 6 Part 2) |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-05-28 | Approved by the Standards Committee | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  | Long-Term Planning | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | No Parts for 4. |  |  | Long-Term Planning | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee
Inactive | PRC | PRC-001 | PRC-001-1.1 | 5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: |  | Long-Term Planning | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | Long-Term Planning | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-05-28 | Approved by the Standards Committee | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | Long-Term Planning | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 | 2013-04-01 |  |  |  | 2015-05-28 | Approved by the Standards Committee | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | 6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee | BA | [19 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1 | No Parts for 6. |  |  |  | 2012-04-11 |  | 2012-02-03 | 2013-04-01 | 2013-04-01 |  |  |  |  | 2015-05-28 | Approved by the Standards Committee
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 3, 3.1, and 3.2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | No Parts for 1. |  | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 3, 3.1, and 3.2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Remedial Action Schemes in its area. (Requirement 6 Part 1) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Remedial Action Schemes in its area. (Requirement 6 Part 1) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 2.2. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Remedial Action Schemes in its area. (Requirement 6 Part 1) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Remedial Action Schemes. (Requirement 6 Part 2) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Remedial Action Schemes. (Requirement 6 Part 2) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Remedial Action Schemes. (Requirement 6 Part 2) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | No Parts for 4. |  |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | [19 empty] | TO
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | 6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Remedial Action Scheme in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000 | BA | [19 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(i) | No Parts for 6. |  |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 3, 3.1, and 3.2. |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | No Parts for 1. |  | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 3, 3.1, and 3.2. |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Special Protection Systems in its area. (Requirement 6 Part 1) |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Special Protection Systems in its area. (Requirement 6 Part 1) |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. | Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, documentation, electronic logs, computer printouts, or computer demonstration or other equivalent evidence that will be used to confirm that it monitors the Special Protection Systems in its area. (Requirement 6 Part 1) |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Special Protection Systems. (Requirement 6 Part 2) |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. • Requirement R3.1 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Special Protection Systems. (Requirement 6 Part 2) |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | M3. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, phone records, electronic-notifications or other equivalent evidence that will be used to confirm that it notified affected Transmission Operator and Balancing Authorities of changes in status of one of its Special Protection Systems. (Requirement 6 Part 2) |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | No Parts for 4. |  |  | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others:[See standard for additional information.] |  |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | 6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. |  |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000 | BA | [19 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-1.1(ii) | No Parts for 6. |  |  |  | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  | X |  |  | 2017-03-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-001 | PRC-001-2 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 2, 2.1, and 2.2. | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-2 | No Parts for 1. |  | M1. Each Generator Operator and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, revised fault analysis study, letters of agreement on settings, notifications of changes, or other equivalent evidence that will be used to confirm that there was coordination of new protective systems or changes as noted in Requirements 2, 2.1, and 2.2. | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | PRC | PRC-001 | PRC-001-2 | 2. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-2 | 2.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [6 empty] | GOP
Inactive | PRC | PRC-001 | PRC-001-2 | 2.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-2 | 3. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | PRC | PRC-001 | PRC-001-2 | No Parts for 3. |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | PRC | PRC-002 | PRC-002-0 | 1. | The Regional Reliability Organization shall develop comprehensive requirements for the installation of Disturbance monitoring equipment to ensure data is available to determine system performance and the causes of System Disturbances. The comprehensive requirements shall include all of the following: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.1. | Type of data recording capability (e.g., sequence-of-event, Fault recording, dynamic Disturbance recording). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.2. | Equipment characteristics including but not limited to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.2.1. | Recording duration requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.2.2. | Time synchronization requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.2.3. | Data format requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.2.4. | Event triggering requirements |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.3. | Monitoring, recording, and reporting capabilities of the equipment. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.3.1. | Voltage. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.3.2. | Current. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.3.3. | Frequency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.3.4. | MW and/or MVAR, as appropriate. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.4. | Data retention capabilities (e.g., length of time data is to be available for retrieval). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.5. | Regional coverage requirements (e.g., by voltage, geographic area, electric area or subarea). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.6. | Installation requirements: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.6.1. | Substations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.6.2. | Transmission lines. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.6.3. | Generators. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.7. | Responsibility for maintenance and testing. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 1.8. | Requirements for periodic (at least every five years) updating, review, and approval of the Regional requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | 2. | The Regional Reliability Organization shall provide its requirements for the installation of Disturbance monitoring equipment to other Regional Reliability Organizations and NERC on request (30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 PRC-002-0 was never enforceable
Inactive | PRC | PRC-002 | PRC-002-1 | 1. | The Regional Reliability Organization shall establish the following installation requirements for sequence of event recording: | M1. The Regional Reliability Organization’s requirements for the installation of Disturbance Monitoring Equipment shall address Requirements 1 through 3. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 1.1. | Location, monitoring and recording requirements, including the following: | M1. The Regional Reliability Organization’s requirements for the installation of Disturbance Monitoring Equipment shall address Requirements 1 through 3. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 1.1.1. | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). | M1. The Regional Reliability Organization’s requirements for the installation of Disturbance Monitoring Equipment shall address Requirements 1 through 3. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 1.1.2. | Devices to be monitored. | M1. The Regional Reliability Organization’s requirements for the installation of Disturbance Monitoring Equipment shall address Requirements 1 through 3. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2. | The Regional Reliability Organization shall establish the following installation requirements for fault recording: | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1. | Location, monitoring and recording requirements, including the following: | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.1. | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.2. | Elements to be monitored at each location. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.3. | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.3.1. | Three phase to neutral voltages. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.3.2. | Three phase currents and neutral currents. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.3.3. | Polarizing currents and voltages, if used. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.3.4. | Frequency. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.1.3.5. | Megawatts and megavars. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.2. | Technical requirements, including the following: | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.2.1. | Recording duration requirements. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.2.2. | Minimum sampling rate of 16 samples per cycle. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 2.2.3. | Event triggering requirements. | M2. The Regional Reliability Organization’s Disturbance monitoring data reporting requirements shall include all elements identified in Requirements 4. |  | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3. | The Regional Reliability Organization shall establish the following installation requirements for dynamic Disturbance recording: | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.1. | Location, monitoring and recording requirements including the following: | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.1.1. | Criteria for equipment location giving consideration to the following: - Site(s) in or near major load centers - Site(s) in or near major generation clusters - Site(s) in or near major voltage sensitive areas - Site(s) on both sides of major transmission interfaces - A major transmission junction - Elements associated with Interconnection Reliability Operating Limits - Major EHV interconnections between control areas - Coordination with neighboring regions within the interconnection | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.1.2. | Elements and number of phases to be monitored at each location. | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.1.3. | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.1.3.1. | Voltage, current and frequency. | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.1.3.2. | Megawatts and megavars. | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.2. | Technical requirements, including the following: | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.2.1. | Capability for continuous recording for devices installed after January 1, 2009. | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 3.2.2. | Each device shall sample data at a rate of at least 960 samples per second and shall record the RMS value of electrical quantities at a rate of at least 6 records per second. | M3. The Regional Reliability Organization shall have evidence it provided its Regional Disturbance monitoring and reporting requirements as required in Requirement 5. | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4. | The Regional Reliability Organization shall establish requirements for facility owners to report Disturbance data recorded by their DME installations. The Disturbance data reporting requirements shall include the following: | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4.1. | Criteria for events that require the collection of data from DMEs. | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4.2. | List of entities that must be provided with recorded Disturbance data. | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4.3. | Timetable for response to data request. | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4.4. | Provision for reporting Disturbance data in a format which is capable of being viewed, read and analyzed with a generic COMTRADE1 analysis tool, | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4.5. | Naming of data files in conformance with the IEEE C37.232 Recommended Practice for Naming Time Sequence Data Files2. | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 4.6. | Data content requirements and guidelines. | M4. The Regional Reliability Organization shall have evidence it conducted a review at least once every five years of its regional requirements for Disturbance monitoring and reporting as required in Requirement 6. | Long-Term Planning | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | 5. | The Regional Reliability Organization shall provide its requirements (and any revisions to those requirements) including those for DME installation and Disturbance data reporting to the affected Transmission Owners and Generator Owners within 30 calendar |  | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | No Parts for 5. |  |  | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information.
Inactive | PRC | PRC-002 | PRC-002-1 | 6. | The Regional Reliability Organization shall periodically (at least every five years) review, update and approve its Regional requirements for Disturbance monitoring and reporting. |  | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information. | [16 empty] | RRO
Inactive | PRC | PRC-002 | PRC-002-1 | No Parts for 6. |  |  | Real-Time Operations | 2006-08-02 | 2006-08-28 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 This Standard was not approved by FERC in Order 693. See Standards Under Development page or Reliability Standards Development Plan for more information.
Inactive | PRC | PRC-002 | PRC-002-2 | 1. | Each Transmission Owner shall: | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 |  | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | M2. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | No Parts for 2. |  | M2. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000
Inactive | PRC | PRC-002 | PRC-002-2 | 3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 3.2. | Each phase current and the residual or neutral current for the following BES Elements: | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 3.2.2. | Transmission Lines. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 4.2. | A minimum recording rate of 16 samples per cycle. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 4.3 . | Trigger settings for at least the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 4.3 . 1. | Neutral (residual) overcurrent. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 4.3 . 2. | Phase undervoltage or overcurrent. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 5. | Each Responsible Entity shall: | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 |  | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.1. | Generating resource(s) with: | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.2.1. | One BES Element; and | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.2.2. | One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2016-07-01 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. | M5. The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-07-01 | 2015-11-24 | X | Entities shall be 100 percent compliant on the first day of the first calendar quarter six (6) months after the date that the standard is approved by an applicable governmental authority or as otherwise provided for in a jurisdiction where approval by an applicable governmental authority is required for a standard to go into effect. Where approval by an applicable governmental authority is not required, the standard shall become effective on the first day of the first calendar quarter that is six (6) months after the date the standard is adopted by the NERC Board of Trustees, or as otherwise provided for in that jurisdiction. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [10 empty] | PA | PC |  | RC
Inactive | PRC | PRC-002 | PRC-002-2 | 6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 6.1. | One phase-to-neutral or positive sequence voltage. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-2 | 7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-2 | 7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-2 | 7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-2 | 7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-2 | 8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 8.1. | Triggered record lengths of at least three minutes. | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 8.2. | At least one of the following three triggers: • Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 9.1. | Input sampling rate of at least 960 samples per second. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 9.2. | Output recording rate of electrical quantities of at least 30 times per second. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Responsible Entity, Regional Entity, or NERC in accordance with the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 |  | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2021-01-01 | 2021-01-01 | X | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | 12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: • Restore the recording capability, or • Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-10-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-2 | No Parts for 12. |  | The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-09-17 | 2015-11-23 | 2016-10-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-4-000
Inactive | PRC | PRC-002 | PRC-002-3 | 1. | Each Transmission Owner shall: | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-3, Attachment 1. | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | No Parts for 2. |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-002 | PRC-002-3 | 3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 3.2. | Each phase current and the residual or neutral current for the following BES Elements: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 3.2.2. | Transmission Lines. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 4.2. | A minimum recording rate of 16 samples per cycle. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 4.3. | Trigger settings for at least the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 4.3.1. | Neutral (residual) overcurrent. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 4.3.2. | Phase undervoltage or overcurrent. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5. | Each Reliability Coordinator shall: | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.1. | Generating resource(s) with: | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.1.1 | Gross individual nameplate rating greater than or equal to 500 MVA. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.1.2 | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.2.1. | One BES Element; and | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 6.1. | One phase-to-neutral or positive sequence voltage. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-3 | 7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-3 | 7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-3 | 7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-3 | 7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-3 | 8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 8.1. | Triggered record lengths of at least three minutes. | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 8.2. | At least one of the following three triggers: · Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz · Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec · Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 9.1. | Input sampling rate of at least 960 samples per second. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 9.2. | Output recording rate of electrical quantities of at least 30 times per second. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | 12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: · Restore the recording capability, or · Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-3 | No Parts for 12. |  | The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 |  |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-002 | PRC-002-4 | 1. | Each Transmission Owner shall: | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-4, Attachment 1. | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 1.2. | Notify the other owners of BES Elements directly connected1 to those BES buses, that SER or FR data is required for those BES Elements, only if the Transmission Owner who identified the BES buses in Part 1.1 does not have SER or FR data. This notification is required within 90 calendar days of completion of Part 1.1. | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners in accordance with Part 1.2. | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns directly connected to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | M2. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | No Parts for 2. |  | M2. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000
Inactive | PRC | PRC-002 | PRC-002-4 | 3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns directly connected to the BES buses identified in Requirement R1: | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 3.2. | Each phase current and the residual or neutral current for the following BES Elements: | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 3.2.1. | Transformers that have a low-side operating voltage of 100 kV or above. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 3.2.2. | Transmission Lines. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30 cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 4.2. | A minimum recording rate of 16 samples per cycle. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 4.3. | Trigger settings for at least the following: | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 4.3.1. | Neutral (residual) overcurrent. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 4.3.2. | Phase undervoltage or overcurrent | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 5. | Each Reliability Coordinator shall: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.1. | Generating resource(s) with: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.2.1. | One BES Element; and | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.3. | Notify all owners of identified BES Elements, within 90 calendar days of completion of Part 5.1, that their respective BES Elements require DDR data. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 5.4. | Re-evaluate all BES Elements within its Reliability Coordinator Area at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-4 | 6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 6.1. | One phase-to-neutral or positive sequence voltage. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-4 | 7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-4 | 7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-4 | 7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-4 | 7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-4 | 8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of the Reliability Standard PRC-002-2 2 and is not capable of continuous recording, triggered records must meet the following: | M8. Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 8.1. | Triggered record lengths of at least three minutes. | M8. Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 8.2. | At least one of the following three triggers: • Off nominal frequency trigger set at: Low High Eastern Interconnection <59.75 Hz >61.0 Hz Western Interconnection <59.55 Hz >61.0 Hz ERCOT Interconnection <59.35 Hz >61.0 Hz Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: Eastern Interconnection < -0.03125 Hz/sec >0.125 Hz/sec Western Interconnection < -0.05625 Hz/sec >0.125 Hz/sec ERCOT Interconnection < -0.08125 Hz/sec >0.125 Hz/sec Hydro-Quebec Interconnection < -0.18125 Hz/sec >0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | M8. Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: | M9. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 9.1. | Input sampling rate of at least 960 samples per second. | M9. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 9.2. | Output recording rate of electrical quantities of at least 30 times per second. | M9. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: | M10. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | M10. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | M10. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 11.1. | Data will be retrievable for the period of 10 calendar days, inclusive of the day the data was recorded. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 11.2. | Data subject to Part 11.1 will be provided within | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 12. | Each Transmission Owner and Generator Owner shall, within 90 calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: • Restore the recording capability, or • Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | M12. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | No Parts for 12. |  | M12. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000
Inactive | PRC | PRC-002 | PRC-002-4 | 13. | Each Transmission Owner and Generator Owner shall: | M13. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 |  |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 13.1. | Within three (3) calendar years of completing a re-evaluation or receiving notification under Requirement R1, Part 1.3, have SER or FR data as applicable for BES Elements directly connected to the identified BES buses. | M13. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-4 | 13.2. | Within three (3) calendar years of receiving notification under Requirement R5, Part 5.4, have DDR data for BES Elements identified during the re-evaluation. | M13. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | Long-Term Planning | 2023-02-16 | 2023-03-10 | 2023-04-14 | 2023-04-14 | 2024-04-01 | 2024-04-01 |  |  |  | 2025-03-31 | Filing/Order Docket No. RD23-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 1. | Each Transmission Owner shall: | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-5, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-5, Attachment 1. | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-5, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 1.2. | Notify the other owners of BES Elements directly connected2 to those BES buses, that SER or FR data is required for those BES Elements, only if the Transmission Owner who identified the BES buses in Part 1.1 does not have SER or FR data. This notification is required within 90 calendar days of completion of Part 1.1. | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-5, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners in accordance with Part 1.2. | M1. The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-5, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns directly connected to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | M2. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | No Parts for 2. |  | M2. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of SER data for circuit breaker position as specified in Requirement R2. Evidence may include, but is not limited to: (1) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns directly connected to the BES buses identified in Requirement R1: | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 3.2. | Each phase current and the residual or neutral current for the following BES Elements: | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 3.2.1. | Transformers that have a low-side operating voltage of 100 kV or above. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 3.2.2. | Transmission Lines. | M3. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30 cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 4.2. | A minimum recording rate of 16 samples per cycle. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 4.3. | Trigger settings for at least the following: | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 4.3.1. | Neutral (residual) overcurrent. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 4.3.2. | Phase undervoltage or overcurrent. | M4. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5. | Each Reliability Coordinator shall: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.1. | Synchronous generating resource(s) with: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.2.1. | One BES Element; and | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.3. | Notify all owners of identified BES Elements, within 90 calendar days of completion of Part 5.1, that their respective BES Elements require DDR data. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 5.4. | Re-evaluate all BES Elements within its Reliability Coordinator Area at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3. | M5. The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 6.1. | One phase-to-neutral or positive sequence voltage. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 6.3. | Real Power and Reactive Power flows expressed on a three-phase basis corresponding to all circuits where current measurements are required. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | M6. The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 7.3. | Real Power and Reactive Power flows expressed on a three-phase basis corresponding to all circuits where current measurements are required. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | M7. The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of the Reliability Standard PRC-002-23 and is not capable of continuous recording, triggered records must meet the following: | M8. Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 8.1. | Triggered record lengths of at least three minutes. | M8. Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 8.2. | At least one of the following three triggers: • Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec >0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec >0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec >0.125 Hz/sec o Quebec Interconnection < -0.18125 Hz/sec >0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | M8. Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: | M9. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 9.1. | Input sampling rate of at least 960 samples per second. | M9. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 9.2. | Output recording rate of electrical quantities of at least 30 times per second. | M9. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: | M10. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | M10. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | M10. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11.1. | Data will be retrievable for the period of 10 calendar days, inclusive of the day the data was recorded. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11.2. | Data subject to Part 11.1 will be provided within 30 calendar days of a request unless an extension is granted by the requestor. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11.4. | FR data will be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11.5. | DDR data will be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 11.6. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | M11. The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration, or settings; or (3) actual data recordings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 12. | Each Transmission Owner and Generator Owner shall, upon the discovery of a failure of the recording capability for the SER, FR or DDR data: • Restore the recording capability within 90 calendar days, or • Submit a Corrective Action Plan (CAP) to the Regional Entity within 90 calendar days and then implement it according to CAP timeline. | M12. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | No Parts for 12. |  | M12. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R12. Evidence may include, but is not limited to: (1) dated reports of discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated CAP transmittals to the Regional Entity and evidence that it implemented the CAP. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 13. | Each Transmission Owner and Generator Owner shall: | M13. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | [5 empty] | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 13.1. | Within three (3) calendar years of completing a re-evaluation or receiving notification under Requirement R1, Part 1.3, have SER or FR data as applicable for BES Elements directly connected to the identified BES buses. | M13. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002 | PRC-002-5 | 13.2. | Within three (3) calendar years of receiving notification under Requirement R5, Part 5.4, have DDR data for BES Elements identified during the re-evaluation. | M13. The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 |  |  |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 1. | Each Transmission Owner and Generator Owner shall provide Sequence of Event (SOE) recording capability by installing Sequence of Event recorders or as part of another device, such as a Supervisory Control And Data Acquisition (SCADA) Remote Terminal Unit (RTU), a generator plant Digital (or Distributed) Control System (DCS) or part of Fault recording equipment. This capability shall: | M1. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Sequence of Event recording capability in accordance with 1.1 and 1.2. (R1) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 1.1. | Be provided at all substations and at locations where circuit breaker operation affects continuity of service to radial Loads greater than 300MW, or the operation of which drops 50MVA Nameplate Rating or greater of Generation, or the operation of which creates a Generation/Load island. Be provided at generating units above 50MVA Nameplate Rating or series of generating units utilizing a control scheme such that the loss of 1 unit results in a loss of greater than 50MVA Nameplate Capacity, and at Generating Plants above 300MVA Name Plate Capacity. | M1. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Sequence of Event recording capability in accordance with 1.1 and 1.2. (R1) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 1.2. | Monitor the following at each location listed in 1.1: | M1. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Sequence of Event recording capability in accordance with 1.1 and 1.2. (R1) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 1.2.1. | Transmission and Generator circuit breaker positions | M1. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Sequence of Event recording capability in accordance with 1.1 and 1.2. (R1) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 1.2.2. | Protective Relay tripping for all Protection Groups that operate to trip circuit breakers identified in 1.2.1. | M1. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Sequence of Event recording capability in accordance with 1.1 and 1.2. (R1) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 1.2.3. | Teleprotection keying and receive | M1. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Sequence of Event recording capability in accordance with 1.1 and 1.2. (R1) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2. | Each Transmission Owner shall provide Fault recording capability for the following Elements at facilities where Fault recording equipment is required to be installed as per R3: | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2.1. | All transmission lines. | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2.2. | Autotransformers or phase-shifters connected to busses. | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2.3. | Shunt capacitors, shunt reactors. | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2.4. | Individual generator line interconnections. | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2.5. | Dynamic VAR Devices. | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 2.6. | HVDC terminals. | M2. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 2.1 to 2.6. (R2) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 3. | Each Transmission Owner shall have Fault recording capability that determines the Current Zero Time for loss of Bulk Electric System (BES) transmission Elements. | M3. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability that determined the Current Zero Time for loss of Bulk Electric System (BES) transmission Elements in accordance with R3. | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [19 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | No Parts for 3. |  | M3. Each Transmission Owner shall have, and provide upon request, evidence that it provided Fault recording capability that determined the Current Zero Time for loss of Bulk Electric System (BES) transmission Elements in accordance with R3. | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 4. | Each Generator Owner shall provide Fault recording capability for Generating Plants at and above 200 MVA Capacity and connected through a generator step up (GSU) transformer to a Bulk Electric System Element unless Fault recording capability is already provided by the Transmission Owner. | M4. Each Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability for its Generating Plants at and above 200 MVA Capacity in accordance with R4. | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | No Parts for 4. |  | M4. Each Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability for its Generating Plants at and above 200 MVA Capacity in accordance with R4. | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 5. | Each Transmission Owner and Generator Owner shall record for Faults, sufficient electrical quantities for each monitored Element to determine the following: | M5. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it records for Faults, sufficient electrical quantities for each monitored Element to determine the parameters listed in 5.1 to 5.5. (R5) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 5.1. | Three phase-to-neutral voltages. (Common bus-side voltages may be used for lines.) | M5. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it records for Faults, sufficient electrical quantities for each monitored Element to determine the parameters listed in 5.1 to 5.5. (R5) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 5.2. | Three phase currents and neutral currents. | M5. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it records for Faults, sufficient electrical quantities for each monitored Element to determine the parameters listed in 5.1 to 5.5. (R5) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 5.3. | Polarizing currents and voltages, if used. | M5. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it records for Faults, sufficient electrical quantities for each monitored Element to determine the parameters listed in 5.1 to 5.5. (R5) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 5.4. | Frequency. | M5. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it records for Faults, sufficient electrical quantities for each monitored Element to determine the parameters listed in 5.1 to 5.5. (R5) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 5.5. | Real and reactive power. | M5. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it records for Faults, sufficient electrical quantities for each monitored Element to determine the parameters listed in 5.1 to 5.5. (R5) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6. | Each Transmission Owner and Generator Owner shall provide Fault recording with the following capabilities: | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.1. | Each Fault recorder record duration shall be a minimum of one (1) second. | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.2. | Each Fault recorder shall have a minimum recording rate of 16 samples per cycle. | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.3. | Each Fault recorder shall be set to trigger for at least the following: | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.3.1. | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or Protective Relay tripping for all Protection Groups. | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.3.2. | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.3.3. | Monitored phase undervoltage set at 0.85 pu or greater. | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 6.4. | Document additional triggers and deviations from the settings in 6.3.2 and 6.3.3 when local conditions dictate. | M6. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided Fault recording capability in accordance with 6.1 to 6.4. (R6) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7. | Each Reliability Coordinator shall establish its area’s requirements for Dynamic Disturbance Recording (DDR) capability that: | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.1. | Provides a minimum of 1 DDR per 3,000 MW of peak Load. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2. | Records dynamic disturbance information with consideration of the following facilities/locations: | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.1. | Major Load centers. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.2. | Major Generation clusters. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.3. | Major voltage sensitive areas. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.4. | Major transmission interfaces. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.5. | Major transmission junctions. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.6. | Elements associated with Interconnection Reliability Operating Limits (IROLs). | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 7.2.7. | Major EHV interconnections between operating areas. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it established its area’s requirements for Dynamic Disturbance Recording (DDR) capability in accordance with 7.1 and .2. (R7) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 8. | Each Reliability Coordinator shall specify that DDRs installed, after the approval of this standard, function as continuous recorders. | M8. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs installed after the approval of this standard function as continuous recorders. (R8) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | No Parts for 8. |  | M8. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs installed after the approval of this standard function as continuous recorders. (R8) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9. | Each Reliability Coordinator shall specify that DDRs are installed with the following capabilities: | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.1. | A minimum recording time of sixty (60) seconds per trigger event. | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.2. | A minimum data sample rate of 960 samples per second, and a minimum data storage rate for RMS quantities of six (6) data points per second. | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.3. | Each DDR shall be set to trigger for at least one of the following (based on manufacturers’ equipment capabilities): | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.3.1. | Rate of change of Frequency. | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.3.2. | Rate of change of Power. | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.3.3. | Delta Frequency (recommend 20 mHz change). | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 9.3.4. | Oscillation of Frequency. | M9. Each Reliability Coordinator shall have, and provide upon request, evidence that it developed DDR setting triggers to include the parameters listed in 9.1 to 9.3. (R9) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 10. | Each Reliability Coordinator shall establish requirements such that the following quantities are monitored or derived where DDRs are installed: | M10. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs monitor the Elements listed in 10.1 through 10.5. (R10) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 10.1. | Line currents for most lines such that normal line maintenance activities do not interfere with DDR functionality. | M10. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs monitor the Elements listed in 10.1 through 10.5. (R10) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 10.2. | Bus voltages such that normal bus maintenance activities do not interfere with DDR functionality. | M10. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs monitor the Elements listed in 10.1 through 10.5. (R10) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 10.3. | As a minimum, one phase current per monitored Element and two phase-to-neutral voltages of different Elements. One of the monitored voltages shall be of the same phase as the monitored current. | M10. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs monitor the Elements listed in 10.1 through 10.5. (R10) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 10.4. | Frequency. | M10. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs monitor the Elements listed in 10.1 through 10.5. (R10) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 10.5. | Real and reactive power. | M10. Each Reliability Coordinator shall have, and provide upon request, evidence that DDRs monitor the Elements listed in 10.1 through 10.5. (R10) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 11. | Each Reliability Coordinator shall document additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10, and report this to the Regional Entity (RE) upon request. |  | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | No Parts for 11. |  |  | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 12. | Each Reliability Coordinator shall specify its DDR requirements including the DDR setting triggers established in R9 to the Transmission Owners and Generator Owners. | Each Reliability Coordinator shall have, and provide upon request, evidence that it specified its DDR requirements which included the DDR setting triggers established in R9 to the Transmission Owners and Generator Owners in the Reliability Coordinator’s area. (R12) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [13 empty] | RC
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | No Parts for 12. |  | Each Reliability Coordinator shall have, and provide upon request, evidence that it specified its DDR requirements which included the DDR setting triggers established in R9 to the Transmission Owners and Generator Owners in the Reliability Coordinator’s area. (R12) | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 13. | Each Transmission Owner and Generator Owner that receives a request from the Reliability Coordinator to install a DDR shall acquire and install the DDR in accordance with R12. Reliability Coordinators, Transmission Owners, and Generator Owners shall mutually agree on an implementation schedule. |  | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | No Parts for 13. |  |  | Long-Term Planning, Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14. | Each Transmission Owner and Generator Owner shall establish a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that includes: [See standard for list of inclusions] | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.1. | Maintenance and testing intervals and their basis. | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.2. | Summary of maintenance and testing procedures. | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.3. | Monthly verification of communication channels used for accessing records remotely (if the entity relies on remote access and the channel is not monitored to a control center staffed around the clock, 24 hours a day, 7 days a week (24/7)). | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.4. | Monthly verification of time synchronization (if the loss of time synchronization is not monitored to a 24/7 control center). | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.5. | Monthly verification of active analog quantities. | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.6. | Verification of DDR and DFR settings in the software every six (6) years. | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 14.7. | A requirement to return failed units to service within 90 days. If a DME device will be out of service for greater than 90 days the owner shall keep a record of efforts aimed at restoring the DME to service. | M14. Each Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it has a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that meets the requirements in 14.1 through 14.7. (R14) | Operations Planning | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 15. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall share data within 30 days upon request. Each Reliability Coordinator, Transmission Owner, and Generator Owner shall provide recorded disturbance data from DMEs within 30 days of receipt of the request in each of the following cases: | M15. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided recorded disturbance data from DMEs within 30 days of the receipt of the request from the entities listed in 15.1 and 15.2. (R15) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 15.1. | NERC, Regional Entity, Reliability Coordinator. | M15. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided recorded disturbance data from DMEs within 30 days of the receipt of the request from the entities listed in 15.1 and 15.2. (R15) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 15.2. | Request from other Transmission Owners, Generator Owners within NPCC. | M15. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it provided recorded disturbance data from DMEs within 30 days of the receipt of the request from the entities listed in 15.1 and 15.2. (R15) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 16. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall submit the data files conforming to the following format requirements: | M16. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it submitted the data files in a format that meets the requirements in 16.1 through 16.3. (R16) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 16.1. | The data files shall be capable of being viewed, read, and analyzed with a generic COMTRADE analysis tool as per the latest revision of IEEE Standard C37.111. | M16. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it submitted the data files in a format that meets the requirements in 16.1 through 16.3. (R16) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 16.2. | Disturbance Data files shall be named in conformance with the latest revision of IEEE Standard C37.232. | M16. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it submitted the data files in a format that meets the requirements in 16.1 through 16.3. (R16) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 16.3. | Fault Recorder and DDR Files shall contain all monitored channels. SOE records shall contain station name, date, time resolved to milliseconds, SOE point name, status. | M16. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it submitted the data files in a format that meets the requirements in 16.1 through 16.3. (R16) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall maintain, record and provide to the Regional Entity (RE), upon request, the following data on the DMEs installed to meet this standard: | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 |  |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.1. | Type of DME. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2013-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.2. | Make and model of equipment. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.3. | Installation location. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 | [6 empty] | GOP | [6 empty] | RC | [6 empty] | TOP
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.4. | Operational Status.Operational Status. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.5. | Date last tested. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.6. | Monitored Elements. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.7. | All identified channels. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002 | PRC-002-NPCC-01 | 17.8. | Monitored electrical quantities. | M17. Each Reliability Coordinator, Transmission Owner and Generator Owner shall have, and provide upon request, evidence that it maintained a record of and provided to NPCC when requested, the data on DMEs installed meeting the requirements 17.1 through 17.8. (R17) | Operations Assessment | 2010-11-04 | 2011-05-31 | 2011-10-20 | 2011-10-20 | 2013-10-20 | 2011-10-20 |  |  |  | 2016-07-01 | Filing/Order Docket No. RD11-8-000 |  |  |  |  | GO | [8 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-003 | PRC-003-0 | 1. | Each Regional Reliability Organization shall have a procedure for the monitoring, review, analysis, and correction of all transmission protection system misoperations. Each Regional Reliability Organization’s procedure shall include the following elements: |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | 1.1. | Requirements for monitoring and analysis of all transmission protective device misoperations. |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | 1.2. | Description of the data reporting requirements (periodicity and format) for those misoperations that adversely affects the reliability of the Bulk Electric Systems as specified by the Regional Reliability Organization. |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | 1.3. | Process for review, follow up, and documentation of corrective action plans for misoperations. |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | 1.4. | Identification of the Regional Reliability Organization group responsible for the procedure and the process for Regional Reliability Organization approval of the procedure. |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | 1.5. | Regional Reliability Organization definition of misoperations. |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | 2. | Each Regional Reliability Organization shall maintain documentation of its procedure and provide it to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable) | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-003-1 (PRC-003-0 was never enforceable)
Inactive | PRC | PRC-003 | PRC-003-1 | 1. | Each Regional Reliability Organization shall establish, document and maintain its procedures for, review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations. These procedures shall include the following elements: | M1. The Regional Reliability Organization shall have procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | 1.1. | The Protection Systems to be reviewed and analyzed for Misoperations (due to theirpotential impact on BES reliability). | M1. The Regional Reliability Organization shall have procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | 1.2. | Data reporting requirements (periodicity and format) for Misoperations. | M1. The Regional Reliability Organization shall have procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | 1.3. | Process for review, analysis follow up, and documentation of Corrective Action Plans for Misoperations. | M1. The Regional Reliability Organization shall have procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | 1.4. | Identification of the Regional Reliability Organization group responsible for the procedures and the process for approval of the procedures. | M1. The Regional Reliability Organization shall have procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in R1. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | 2. | Each Regional Reliability Organization shall maintain and periodically update documentation of its procedures for review, analysis, reporting, and mitigation of transmission and generation Protection System Misoperations. | M2. The Regional Reliability Organization shall have evidence it maintained and periodically updated its procedures for review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in Requirement 2. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | No Parts for 2. |  | M2. The Regional Reliability Organization shall have evidence it maintained and periodically updated its procedures for review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations as defined in Requirement 2. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-003 | PRC-003-1 | 3. | Each Regional Reliability Organization shall distribute procedures in Requirement 1 and any changes to those procedures, to the affected Transmission Owners, Distribution Providers that own transmission Protection Systems, and Generator Owners within 30 calendar days of approval of those procedures. | M3. The Regional Reliability Organization shall have evidence it provided its procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations to the affected Transmission Owners, Distribution Providers that own transmission Protection Systems, and Generator Owners as defined in Requirement 3. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-003 | PRC-003-1 | No Parts for 3. |  | M3. The Regional Reliability Organization shall have evidence it provided its procedures for the review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations to the affected Transmission Owners, Distribution Providers that own transmission Protection Systems, and Generator Owners as defined in Requirement 3. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2016-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-004 | PRC-004-0 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall analyze all protection system misoperations and shall take corrective actions to avoid future misoperations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-08-01 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-08-01 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-004 | PRC-004-0 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall provide to its affected Regional Reliability Organization and NERC on request (within 30 calendar days) documentation of the misoperations analyses and corrective actions according to the Regional Reliability Organization’s procedures of Reliability Standard PRC-003-0_R1. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-08-01 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-08-01 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-004 | PRC-004-1 | 1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for Reliability Standard PRC-003 Requirement 1. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-1 | No Parts for 1. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-004 | PRC-004-1 | 2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-004 | PRC-004-1 | 3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Reliability Organization, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-1 | No Parts for 3. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-004 | PRC-004-1a | 1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for Reliability Standard PRC-003 Requirement 1. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RD11-5-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-1a | No Parts for 1. |  |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RD11-5-000
Inactive | PRC | PRC-004 | PRC-004-1a | 2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RD11-5-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-1a | No Parts for 2. |  |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RD11-5-000
Inactive | PRC | PRC-004 | PRC-004-1a | 3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Reliability Organization, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-1a | No Parts for 3. |  |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RD11-5-000
Inactive | PRC | PRC-004 | PRC-004-2 | 1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | [5 empty] | 2011-09-25 | Filing/Order Docket No. RD10-15-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2 | No Parts for 1. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | [5 empty] | 2011-09-25 | Filing/Order Docket No. RD10-15-000
Inactive | PRC | PRC-004 | PRC-004-2 | 2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | [5 empty] | 2011-09-25 | Filing/Order Docket No. RD10-15-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-2 | No Parts for 2. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | [5 empty] | 2011-09-25 | Filing/Order Docket No. RD10-15-000
Inactive | PRC | PRC-004 | PRC-004-2 | 3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | [5 empty] | 2011-09-25 | Filing/Order Docket No. RD10-15-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2 | No Parts for 3. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | [5 empty] | 2011-09-25 | Filing/Order Docket No. RD10-15-000
Inactive | PRC | PRC-004 | PRC-004-2.1a | 1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | M1. The Transmission Owner, and any Distribution Provider that owns a transmission Protection System shall each have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM12-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2.1a | No Parts for 1. |  | M1. The Transmission Owner, and any Distribution Provider that owns a transmission Protection System shall each have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM12-16-000
Inactive | PRC | PRC-004 | PRC-004-2.1a | 2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | M2. The Generator Owner shall have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-2.1a | No Parts for 2. |  | M2. The Generator Owner shall have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM12-16-000
Inactive | PRC | PRC-004 | PRC-004-2.1a | 3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | M3. Each Transmission Owner, and any Distribution Provider that owns a transmission Protection System, and each Generator Owner shall have evidence it provided documentation of its Protection System Misoperations, analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM12-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2.1a | No Parts for 3. |  | M3. Each Transmission Owner, and any Distribution Provider that owns a transmission Protection System, and each Generator Owner shall have evidence it provided documentation of its Protection System Misoperations, analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM12-16-000
Inactive | PRC | PRC-004 | PRC-004-2.1(i)a | 1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | M1. The Transmission Owner, and any Distribution Provider that owns a transmission Protection System shall each have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2.1(i)a | No Parts for 1. |  | M1. The Transmission Owner, and any Distribution Provider that owns a transmission Protection System shall each have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-2.1(i)a | 2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. • For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | M2. The Generator Owner shall have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-2.1(i)a | No Parts for 2. |  | M2. The Generator Owner shall have evidence it analyzed its Protection System Misoperations and developed and implemented Corrective Action Plans to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-2.1(i)a | 3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. • For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | M3. Each Transmission Owner, and any Distribution Provider that owns a transmission Protection System, and each Generator Owner shall have evidence it provided documentation of its Protection System Misoperations, analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2.1(i)a | No Parts for 3. |  | M3. Each Transmission Owner, and any Distribution Provider that owns a transmission Protection System, and each Generator Owner shall have evidence it provided documentation of its Protection System Misoperations, analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-2a | 1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2012-04-01 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RD11-5-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2a | No Parts for 1. |  |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2012-04-01 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RD11-5-000
Inactive | PRC | PRC-004 | PRC-004-2a | 2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2012-04-01 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RD11-5-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-2a | No Parts for 2. |  |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2012-04-01 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RD11-5-000
Inactive | PRC | PRC-004 | PRC-004-2a | 3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2012-04-01 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-2a | No Parts for 3. |  |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2012-04-01 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RD11-5-000
Inactive | PRC | PRC-004 | PRC-004-3 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2015-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2015-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2015-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2015-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 | 2015-05-13 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000
Inactive | PRC | PRC-004 | PRC-004-3 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000
Inactive | PRC | PRC-004 | PRC-004-3 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000
Inactive | PRC | PRC-004 | PRC-004-3 | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3 | No Parts for 6. |  | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2014-08-14 | 2014-09-15 | 2015-05-13 | 2015-05-13 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-000
Inactive | PRC | PRC-004 | PRC-004-3(i) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-3(i) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-3(i) | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-3(i) | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-3(i) | No Parts for 6. |  | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-4 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 |  | 2015-05-29 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 |  | 2015-05-29 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 |  | 2015-05-29 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 |  | 2015-05-29 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 |  | 2015-05-29 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-4 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-4 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-4 | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4 | No Parts for 6. |  | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-004 | PRC-004-4(i) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2016-07-01 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2016-07-01 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2016-07-01 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 | 2015-12-04 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning, Real-Time Operations | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning, Real-Time Operations | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-4(i) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning, Real-Time Operations | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning, Real-Time Operations | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-4(i) | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | No Parts for 5. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-4(i) | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-4(i) | No Parts for 6. |  | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-12-04 | 2015-12-04 | 2016-07-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-5 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | No Parts for 3. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000
Inactive | PRC | PRC-004 | PRC-004-5 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000
Inactive | PRC | PRC-004 | PRC-004-5 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000
Inactive | PRC | PRC-004 | PRC-004-5 | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5 | No Parts for 6. |  | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RD15-5-000
Inactive | PRC | PRC-004 | PRC-004-5(i) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | No Parts for 3. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-5(i) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | No Parts for 4. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it performed at least one investigative action according to Requirement R4 every two full calendar quarters until a cause is identified or a declaration is made. Acceptable evidence for Requirement R4 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-5(i) | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it developed a CAP and an evaluation of the CAP’s applicability to other Protection Systems and locations, or a declaration in accordance with Requirement R5. Acceptable evidence for Requirement R5 may include, but is not limited to the following dated documentation (electronic or hardcopy format): CAP and evaluation, or declaration. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Inactive | PRC | PRC-004 | PRC-004-5(i) | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-5(i) | No Parts for 6. |  | M6. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables. Acceptable evidence for Requirement R6 may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. | Long-Term Planning, Operations Planning | 2015-06-22 | 2015-07-07 | 2015-11-19 | 2015-11-19 | 2017-04-02 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-14-001, RD15-3-001 and RD15-5-001
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified whether its Protection System component(s) caused a Misoperation within the allotted time period. Acceptable evidence for Requirement R3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, DME records, test results, or transmittals. | Operations Assessment | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 4. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | No Parts for 4. |  | Reserved |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | M2.2 Each Transmission Owner shall have available for inspection training materials, as specified in Requirement R2 part 2.2. | Long-Term Planning, Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | No Parts for 5. |  | M2.2 Each Transmission Owner shall have available for inspection training materials, as specified in Requirement R2 part 2.2. | Long-Term Planning, Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | 6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | M2.3 Each Transmission Owner shall have available for inspection training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R2 part 2.3. | Long-Term Planning, Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004 | PRC-004-6 | No Parts for 6. |  | M2.3 Each Transmission Owner shall have available for inspection training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R2 part 2.3. | Long-Term Planning, Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-10-15 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 1. | System Operators and System Protection personnel of the Transmission Owners and Generator Owners shall analyze all Protection System and RAS operations. | M1. Transmission Owners and Generation Owners shall have evidence that they reported and analyzed all Protection System and RAS operations. M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | Long-Term Planning, Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 1.1. | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. | M1. Transmission Owners and Generation Owners shall have evidence that they reported and analyzed all Protection System and RAS operations. M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | Long-Term Planning, Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 1.2. | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. | M1. Transmission Owners and Generation Owners shall have evidence that they reported and analyzed all Protection System and RAS operations. M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | Long-Term Planning, Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2. | Transmission Owners and Generator Owners shall perform the following actions for each Misoperation of the Protection System or RAS. It is not intended that Requirements R2.1 through R2.4 apply to Protection System and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with NERC Reliability Standards. If the Transmission Owner or Generator Owner later finds the Protection System or RAS operation to be incorrect through System Protection personnel analysis, the requirements of R2.1 through R2.4 become applicable at the time the Transmission Owner or Generator Owner identifies the Misoperation: |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO | TOP
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.1. | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.2. | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. [Time Horizon: Same-day Operations] |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.2.1. | Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated. |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.2.2. | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.3. | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO | TOP
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.3.1. | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [19 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.3.2. | When FERAS is not available, then |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [15 empty] | TOP
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.3.2.1. | The Generator Owners shall adjust generation to a reliable operating level, or |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.3.2.2. | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [20 empty] | TOP
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.4. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.4.1. | Transmission Owners or Generator Owners shall repair or replace any Protection System or RAS that misoperated with FEPS and FERAS within 20 business days of the date of the Misoperation identification, or |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 2.4.2. | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. [Time Horizon: Operations Assessment] |  | Long-Term Planning, Same-Day Operations | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 3. | Transmission Owners and Generation Owners shall submit Misoperation incident reports to WECC within 10 business days for the following. [Time Horizon: Operations Assessment] | M3. Transmission Owners and Generation Owners shall have evidence that they reported the following within 10 business days. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 3.1. | Identification of a Misoperation of a Protection System and/or RAS, | M3. Transmission Owners and Generation Owners shall have evidence that they reported the following within 10 business days. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-1 | 3.2. | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. | M3. Transmission Owners and Generation Owners shall have evidence that they reported the following within 10 business days. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-10-01 | 2011-06-27 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 1. | System Operators and System Protection personnel of the Transmission Owners and Generator Owners shall analyze all Protection System and RAS operations. | Transmission Owners and Generation Owners shall have evidence that they reported and analyzed all Protection System and RAS operations. M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 1.1. | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. | Transmission Owners and Generation Owners shall have evidence that they reported and analyzed all Protection System and RAS operations. M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 1.2. | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. | Transmission Owners and Generation Owners shall have evidence that they reported and analyzed all Protection System and RAS operations. M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2. | Transmission Owners and Generator Owners shall perform the following actions for each Misoperation of the Protection System or RAS. It is not intended that Requirements R2.1 through R2.4 apply to Protection System and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with NERC Reliability Standards. If the Transmission Owner or Generator Owner later finds the Protection System or RAS operation to be incorrect through System Protection personnel analysis, the requirements of R2.1 through R2.4 become applicable at the time the Transmission Owner or Generator Owner identifies the Misoperation: | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.1. | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.2. | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.2.1. | Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.2.2. | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.3. | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.3.1. | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.3.2. | When FERAS is not available, then | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.3.2.1. | The Generator Owners shall adjust generation to a reliable operating level, or | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.3.2.2. | Transmission Operators shall adjust the SOL and operate the facilities within established limits. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.4. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.4.1. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 2.4.2. | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. | Transmission Owners and Generation Owners shall have evidence for the following. M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | Operations Assessment, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 3. | Transmission Owners and Generation Owners shall submit Misoperation incident reports to WECC within 10 business days for the following. | M3. Transmission Owners and Generation Owners shall have evidence that they reported the following within 10 business days. M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 3.1. | Identification of a Misoperation of a Protection System and/or RAS, | M3. Transmission Owners and Generation Owners shall have evidence that they reported the following within 10 business days. M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-004 | PRC-004-WECC-2 | 3.2. | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. | M3. Transmission Owners and Generation Owners shall have evidence that they reported the following within 10 business days. M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2021-01-01 | Filing/Order Docket No. RM15-13-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1. | The Transmission Owner, Generator Owner and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program in place. The program(s) shall include: | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.1. | Transmission protection system identification shall include but are not limited to: | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.1.1. | Relays. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.1.2. | Instrument transformers. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.1.3. | Communications systems, where appropriate. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.1.4. | Batteries. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.2. | Documentation of maintenance and testing intervals and their basis. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.3. | Summary of testing procedure. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.4. | Schedule for system testing. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.5. | Schedule for system maintenance. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 1.6. | Date last tested/maintained. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program as defined in Reliability Standard PRC-005-0_R1. | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall provide documentation of its transmission protection system program and its implementation to the appropriate Regional Reliability Organization and NERC on request (within 30 calendar days). | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have evidence it provided documentation of its transmission protection system maintenance and testing program and the implementation of its program as defined in Reliability Standard PRC-005-0_R2. |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable) |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-0 | No Parts for 2. |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall have evidence it provided documentation of its transmission protection system maintenance and testing program and the implementation of its program as defined in Reliability Standard PRC-005-0_R2. |  | 2005-02-08 | [8 empty] | 2006-05-01 | Replaced with PRC-005-1 (PRC-005-0 was never enforceable)
Inactive | PRC | PRC-005 | PRC-005-1 | 1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1 | 1.1. | Maintenance and testing intervals and their basis. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1 | 1.2. | Summary of maintenance and testing procedures. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1 | 2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1 | 2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1 | 2.2. | Date each Protection System device was last tested/maintained. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-25 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1.1b | 1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | M1. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have an associated Protection System maintenance and testing program as defined in Requirement 1. | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM12-16-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1.1b | 1.1. | Maintenance and testing intervals and their basis. | M1. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have an associated Protection System maintenance and testing program as defined in Requirement 1. | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM12-16-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1.1b | 1.2. | Summary of maintenance and testing procedures. | M1. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have an associated Protection System maintenance and testing program as defined in Requirement 1. | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM12-16-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1.1b | 2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Entity on request (within 30 calendar days). The documentation of the program implementation shall include: | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have evidence it provided documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in Requirement 2. | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM12-16-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1.1b | 2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have evidence it provided documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in Requirement 2. | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM12-16-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1.1b | 2.2. | Date each Protection System device was last tested/maintained. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have evidence it provided documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in Requirement 2. | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM12-16-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1a | 1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-13 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1a | 1.1. | Maintenance and testing intervals and their basis. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  | 2012-03-13 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1a | 1.2. | Summary of maintenance and testing procedures. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  | 2012-03-13 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1a | 2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  |  | 2012-03-13 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1a | 2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  | 2012-03-13 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1a | 2.2. | Date each Protection System device was last tested/maintained. |  |  | 2011-02-17 | 2011-04-15 | 2011-09-26 | 2011-09-26 | 2011-09-26 | 2011-09-26 |  |  |  | 2012-03-13 | Filing/Order Docket No. RD11-5-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1b | 1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: |  |  | 2009-11-05 | 2009-11-17 | 2012-02-03 | 2012-03-14 | 2012-03-14 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000, RM06-16-007, RM10-5-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1b | 1.1. | Maintenance and testing intervals and their basis. |  |  | 2009-11-05 | 2009-11-17 | 2012-02-03 | 2012-03-14 | 2012-03-14 | 2012-03-14 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000, RM06-16-007, RM10-5-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1b | 1.2. | Summary of maintenance and testing procedures. |  |  | 2009-11-05 | 2009-11-17 | 2012-02-03 | 2012-03-14 | 2012-03-14 | 2012-03-14 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000, RM06-16-007, RM10-5-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1b | 2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: |  |  | 2009-11-05 | 2009-11-17 | 2012-02-03 | 2012-03-14 | 2012-03-14 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000, RM06-16-007, RM10-5-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1b | 2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  |  | 2009-11-05 | 2009-11-17 | 2012-02-03 | 2012-03-14 | 2012-03-14 | 2012-03-14 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000, RM06-16-007, RM10-5-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-1b | 2.2. | Date each Protection System device was last tested/maintained. |  |  | 2009-11-05 | 2009-11-17 | 2012-02-03 | 2012-03-14 | 2012-03-14 | 2012-03-14 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000, RM06-16-007, RM10-5-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 | 2014-02-24 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | 1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 | 2014-02-24 |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performancebased maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performancebased maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000
Inactive | PRC | PRC-005 | PRC-005-2 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall have evidence that it has maintained its Protection System Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall have evidence that it has maintained its Protection System Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000
Inactive | PRC | PRC-005 | PRC-005-2 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000
Inactive | PRC | PRC-005 | PRC-005-2 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2012-11-07 | 2013-02-26 | 2013-12-19 | 2014-02-24 | 2015-04-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RM13-7-000
Inactive | PRC | PRC-005 | PRC-005-2(i) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. The PSMP shall: | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | 1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-2(i) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-2(i) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-2(i) | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(i) | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. The PSMP shall: | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each protection Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, and Table 3. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv
Inactive | PRC | PRC-005 | PRC-005-2(ii) | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-2(ii) | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Entities with newly classified “Remedial Action Scheme” (RAS) resulting from the application of the revised definition must be fully compliant with all Reliability Standards applicable RAS twenty-four (24) months from the Effectiv
Inactive | PRC | PRC-005 | PRC-005-3 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | 1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000
Inactive | PRC | PRC-005 | PRC-005-3 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System and Automatic Reclosing Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System and Automatic Reclosing Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000
Inactive | PRC | PRC-005 | PRC-005-3 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System and Automatic Reclosing Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System and Automatic Reclosing Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000
Inactive | PRC | PRC-005 | PRC-005-3 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2013-11-07 | 2014-02-14 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RM14-8-000
Inactive | PRC | PRC-005 | PRC-005-3(i) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | 1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-3(i) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System and Automatic Reclosing Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System and Automatic Reclosing Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-3(i) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System and Automatic Reclosing Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System and Automatic Reclosing Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-3(i) | 5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(i) | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-06 | [7 empty] | 2015-12-31 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System and Automatic Reclosing Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System and Automatic Reclosing Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. (Part 1.2) | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include but is not limited to Component lists, dated maintenance records, and dated analysis records and results. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System and Automatic Reclosing Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System and Automatic Reclosing Components included within its time-based program in accordance with Requirement R3. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System and Automatic Reclosing Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System and Automatic Reclosing Components included in its performance-based program in accordance with Requirement R4. The evidence may include but is not limited to dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-3(ii) | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-3(ii) | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include but is not limited to work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 Retired by PRC-005-6; PRC-005-3(ii) was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-4 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. (Part 1.2) | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. (Part 1.2) | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | 1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. (Part 1.2) | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include, but is not limited to, Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include, but is not limited to, Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-4 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time-based program in accordance with Requirement R3. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time-based program in accordance with Requirement R3. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-4 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included in its performance-based program in accordance with Requirement R4. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included in its performance-based program in accordance with Requirement R4. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-4 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include, but is not limited to, work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-4 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include, but is not limited to, work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2014-11-13 | 2014-12-18 | [7 empty] | 2015-12-31 | Retired by PRC-005-6; PRC-005-4 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-5 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time‐based, performance‐based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time‐based program as described in Table 1‐4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐ 2, and Table 5. (Part 1.2) | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time‐based, performance‐based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time‐based program as described in Table 1‐4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐ 2, and Table 5. (Part 1.2) | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | 1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented Protection System Maintenance Program in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time‐based, performance‐based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time‐based program as described in Table 1‐4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐ 2, and Table 5. (Part 1.2) | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance‐based maintenance intervals shall have evidence that its current performance‐based maintenance program(s) is in accordance with Requirement R2, which may include, but is not limited to, Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance‐based maintenance intervals shall have evidence that its current performance‐based maintenance program(s) is in accordance with Requirement R2, which may include, but is not limited to, Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-5 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time‐based maintenance program(s) shall have evidence that it has maintained its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time‐based program in accordance with Requirement R3. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check‐off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time‐based maintenance program(s) shall have evidence that it has maintained its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time‐based program in accordance with Requirement R3. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check‐off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-5 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance‐based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included in its performance‐based program in accordance with Requirement R4. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check‐off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance‐based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the Protection System Maintenance Program for the Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included in its performance‐based program in accordance with Requirement R4. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check‐off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable.
Inactive | PRC | PRC-005 | PRC-005-5 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include, but is not limited to, work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-005 | PRC-005-5 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include, but is not limited to, work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2015-05-07 | 2015-11-13 | 2015-12-18 | [6 empty] | 2015-12-31 | Approved by Board of Trustees; replaced and retired by PRC-005-6; PRC-005-5 was never enforceable.
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented PSMP in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. (Part 1.2) | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented PSMP in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. (Part 1.2) | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 | 2015-12-18 | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | M1. Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented PSMP in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. (Part 1.2) | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 | 2015-12-18 | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include, but is not limited to, Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals shall have evidence that its current performance-based maintenance program(s) is in accordance with Requirement R2, which may include, but is not limited to, Component lists, dated maintenance records, and dated analysis records and results. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details.
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time-based program in accordance with Requirement R3. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall have evidence that it has maintained its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time-based program in accordance with Requirement R3. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details.
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the PSMP for the Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included in its performance-based program in accordance with Requirement R4. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | No Parts for 4. |  | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance intervals in accordance with Requirement R2 shall have evidence that it has implemented the PSMP for the Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included in its performance-based program in accordance with Requirement R4. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details.
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include, but is not limited to, work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details. |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005 | PRC-005-6 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence that it has undertaken efforts to correct identified Unresolved Maintenance Issues in accordance with Requirement R5. The evidence may include, but is not limited to, work orders, replacement Component orders, invoices, project schedules with completed milestones, return material authorizations (RMAs) or purchase orders. | Operations Planning | 2015-11-05 | 2015-11-13 | 2015-12-18 | 2015-12-18 | 2016-01-01 |  | X |  |  |  | Filing/Order Docket No. RD16-2-000 Due to the complex compliance requirements, please refer to the implementation plan for the phased-in details.
Inactive | PRC | PRC-006 | PRC-006-0 | 1. | Each Regional Reliability Organization shall develop, coordinate, and document an UFLS program, which shall include the following: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.1. | Requirements for coordination of UFLS programs within the subregions, Regional Reliability Organization and, where appropriate, among Regional Reliability Organizations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2. | Design details shall include, but are not limited to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.1. | Frequency set points. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.2. | Size of corresponding load shedding blocks (% of connected loads.) |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.3. | Intentional and total tripping time delays. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.4. | Generation protection. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.5. | Tie tripping schemes. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.6. | Islanding schemes. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.7. | Automatic load restoration schemes. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.2.8. | Any other schemes that are part of or impact the UFLS programs. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.3. | A Regional Reliability Organization UFLS program database. This database shall be updated as specified in the Regional Reliability Organization program (but at least every five years) and shall include sufficient information to model the UFLS program in dynamic simulations of the interconnected transmission systems. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.4. | Assessment and documentation of the effectiveness of the design and implementation of the Regional UFLS program. This assessment shall be conducted periodically and shall (at least every five years or as required by changes in system conditions) include, but not be limited to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.4.1. | A review of the frequency set points and timing, and |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 1.4.2. | Dynamic simulation of possible Disturbance that cause the Region or portions of the Region to experience the largest imbalance between Demand (Load) and generation. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | 2. | The Regional Reliability Organization shall provide documentation of its UFLS program and its database information to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-006 | PRC-006-0 | 3. | The Regional Reliability Organization shall provide documentation of the assessment of its UFLS program to NERC on request (within 30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-006 | PRC-006-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for E.B.1. |  |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per E.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: [See standard for additional information.] |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.2.1. | Those islands selected by applying the criteria in Requirement E.B.1, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | M1. Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 1. |  | M1. Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 2.1. | Those islands selected by applying the criteria in Requirement R1, and | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | M5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 5. |  | M5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 6. |  | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, emails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 7. |  | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, emails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 8. |  | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for application per Requirement R9. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 9. |  | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for application per Requirement R9. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application per Requirement R10. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [19 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 10. |  | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application per Requirement R10. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 11.1. | The performance of the UFLS equipment, | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 11.2. | The effectiveness of the UFLS program. | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. |  | Long-Term Planning, Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 12. |  |  | Long-Term Planning, Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | M13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Long-Term Planning, Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for 13. |  | M13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Long-Term Planning, Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | 14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following: | M14. Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 14.1. | UFLS program, including a schedule for implementation | M14. Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 14.2. | UFLS design assessment | M14. Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | 14.3. | Format and schedule of UFLS data submittal | M14. Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3. | Each Planning Coordinator shall develop a UFLS program, including a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1A, either for 30 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1A, either for 30 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3.3.1. | Individual generating unit greater than 50 MVA (gross nameplate rating) directly connected to the BES |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3.3.2. | Generating plants/facilities greater than 50 MVA (gross aggregate nameplate rating) directly connected to the BES |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 50 MVA gross nameplate rating. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2. The simulation shall model each of the following: |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.12. | Each Planning Coordinator, in whose islanding event assessment (per E.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. |  | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | No Parts for E.B.12. |  |  | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.4.1. | Underfrequency trip settings of individual generating units that are part of plants/facilities with a capacity of 50 MVA or more individually or cumulatively (gross nameplate rating), directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1A, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.4.2. | Overfrequency trip settings of individual generating units that are part of plants/facilities with a capacity of 50 MVA or more individually or cumulatively (gross nameplate rating), directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 - Attachment 2A, and |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.A.4.3. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | Long-Term Planning | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2013-10-01 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: |  | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.11.1. | The performance of the UFLS equipment, E.B. |  | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-1 | E.B.11.2. | The effectiveness of the UFLS program |  | Operations Assessment | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2013-10-01 | 2012-07-10 |  |  |  | 2015-09-30 | Filing/Order Docket No. RM11-20-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for D.B.1. |  |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: |  | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.11.1. | The performance of the UFLS equipment, |  | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.11.2. | The effectiveness of the UFLS program |  | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. |  | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for D.B.12. |  |  | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | M1. Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 1. |  | M1. Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [See Standard for additional information.] | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 2.1. | Those islands selected by applying the criteria in Requirement R1, and | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, an | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessmen | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. |  | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 5. |  |  | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 6. |  | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 7. |  | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 8. |  | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning, Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation , including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 9. |  | Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation , including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 10. |  | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 11.1. | The performance of the UFLS equipment, | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 11.2. | The effectiveness of the UFLS program. | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | M12. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 12. |  | M12. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | No Parts for 13. |  | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-2 | 14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC | [7 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | 14.1. | UFLS program, including a schedule for implementation | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC | [7 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | 14.2. | UFLS design assessment | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC | [7 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | 14.3. | Format and schedule of UFLS data submittal | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning, Operations Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC | [7 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-2 | 15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-2 | 15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2014-11-13 | 2014-12-15 | 2015-03-04 | 2015-03-04 | 2015-10-01 | 2015-03-04 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from each of these extreme events: • Loss of the entire capability of a generating station. • Loss of all transmission circuits emanating from a generating station, switching station, substation or dc terminal. • Loss of all transmission circuits on a common right-of-way. • Three-phase fault with failure of a circuit breaker to operate and correct operation of a breaker failure protection system and its associated breakers. • Three-phase fault on a circuit breaker, with normal fault clearing. • The operation or partial operation of a RAS for an event or condition for which it was not intended to operate. | M.D.A.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and | M.D.A.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and | M.D.A.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus | M.D.A.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; | M.D.A.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.4.1. | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and | M.D.A.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.4.2. | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and | M.D.A.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.A.4.3. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | M.D.A.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria, developed as part of the joint regional review with other Planning Coordinators in the WECC Regional Entity area to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement D.B.1. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for D.B.1. |  | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria, developed as part of the joint regional review with other Planning Coordinators in the WECC Regional Entity area to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement D.B.1. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: | M.D.B.11 Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a coordinated event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement D.B.11. | Long-Term Planning, Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.11.1. | The performance of the UFLS equipment, | M.D.B.11 Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a coordinated event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement D.B.11. | Long-Term Planning, Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.11.2. | The effectiveness of the UFLS program | M.D.B.11 Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a coordinated event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement D.B.11. | Long-Term Planning, Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. | M.D.B.12. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a UFLS design assessment per Requirements D.B.12 and D.B.4 if UFLS program deficiencies are identified in D.B.11. | Long-Term Planning, Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for D.B.12. |  | M.D.B.12. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a UFLS design assessment per Requirements D.B.12 and D.B.4 if UFLS program deficiencies are identified in D.B.11. | Long-Term Planning, Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: | M.D.B.2 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a region-wide coordinated UFLS program that meet the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and | M.D.B.2 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a region-wide coordinated UFLS program that meet the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. | M.D.B.2 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a region-wide coordinated UFLS program that meet the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | M.D.B.3 Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | M.D.B.4 Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 1. |  | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 2.1. | Those islands selected by applying the criteria in Requirement R1, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following:  Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES  Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES  Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | M5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 5. |  | M5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. |  |  | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 6. |  |  |  | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 7. |  | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 8. |  | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 9. |  | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [19 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 10. |  | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 11.1. | The performance of the UFLS equipment, | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 11.2. | The effectiveness of the UFLS program. | M11. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | M12. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 12. |  | M12. Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | No Parts for 13. |  | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000
Inactive | PRC | PRC-006 | PRC-006-3 | 14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 14.1. | UFLS program, including a schedule for implementation | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 14.2. | UFLS design assessment | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 14.3. | Format and schedule of UFLS data submittal | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | M15. Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | M15. Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-3 | 15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | M15. Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2017-08-10 | 2017-09-05 | 2017-09-05 | 2017-10-01 | 2017-10-01 | 2017-10-01 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD15-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from each of these extreme events: • Loss of the entire capability of a generating station. • Loss of all transmission circuits emanating from a generating station, switching station, substation or dc terminal. • Loss of all transmission circuits on a common right-of-way. • Three-phase fault with failure of a circuit breaker to operate and correct operation of a breaker failure protection system and its associated breakers. • Three-phase fault on a circuit breaker, with normal fault clearing. • The operation or partial operation of a RAS for an event or condition for which it was not intended to operate. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.4.1. | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1A, and | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.4.2. | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 - Attachment 1A, and | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.A.4.3. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria, developed as part of the joint regional review with other Planning Coordinators in the WECC Regional Entity area to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement D.B.1 | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for D.B.1. |  | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria, developed as part of the joint regional review with other Planning Coordinators in the WECC Regional Entity area to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement D.B.1 | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a coordinated event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement D.B.11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.11.1. | The performance of the UFLS equipment, | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a coordinated event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement D.B.11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.11.2. | The effectiveness of the UFLS program | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a coordinated event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement D.B.11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a UFLS design assessment per Requirements D.B.12 and D.B.4 if UFLS program deficiencies are identified in D.B.11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for D.B.12. |  | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it participated in a UFLS design assessment per Requirements D.B.12 and D.B.4 if UFLS program deficiencies are identified in D.B.11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a region-wide coordinated UFLS program that meet the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a region-wide coordinated UFLS program that meet the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a region-wide coordinated UFLS program that meet the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its adoption of a UFLS program, coordinated across the WECC Regional Entity area, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.B.3 Parts D.B.3.1 through D.B.3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its participation in a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area that demonstrates it meets Requirement D.B.4 Parts D.B.4.1 through D.B.4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 1. |  | Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 2.1. | Those islands selected by applying the criteria in Requirement R1, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following:  Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES  Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES  Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 5. |  | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 6. |  | Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 7. |  | Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 8. |  | Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 9. |  | Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [19 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 10. |  | Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 11.1. | The performance of the UFLS equipment, | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 11.2. | The effectiveness of the UFLS program. | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 12. |  | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | No Parts for 13. |  | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | PRC | PRC-006 | PRC-006-4 | 14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 14.1. | UFLS program, including a schedule for implementation | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 14.2. | UFLS design assessment | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 14.3. | Format and schedule of UFLS data submittal | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-4 | 15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | [7 empty] | 2021-03-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.A.3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from each of these extreme events: • Loss of the entire capability of a generating station. • Loss of all transmission circuits emanating from a generating station, switching station, substation or dc terminal. • Loss of all transmission circuits on a common right-of-way. • Three-phase fault with failure of a circuit breaker to operate and correct operation of a breaker failure protection system and its associated breakers. • Three-phase fault on a circuit breaker, with normal fault clearing. • The operation or partial operation of a RAS for an event or condition for which it was not intended to operate. | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC | [7 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.A.3. |  | Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement D.A.3 Parts D.A.3.1 through D.A.3.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.A.4.1 | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006 - Attachment 1A, and | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.A.4.2 | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006 - Attachment 1A,and | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.A.4.3 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement D.A.4 Parts D.A.4.1 through D.A.4.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.1. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate:[VRF: Medium][Time Horizon: Operations Assessment] |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.11.1. | The performance of the UFLS equipment, |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.11.2. | The effectiveness of the UFLS program |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with all other Planning Coordinators in the Western Interconnection to consider the identified deficiencies within two years of event actuation. [VRF: Medium][Time Horizon: Operations Assessment] |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.12. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a Western Interconnection-wide coordinated UFLS program including: | Each Planning Coordinator will have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a Western Interconnection-wide coordinated UFLS program meeting the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and | Each Planning Coordinator will have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a Western Interconnection-wide coordinated UFLS program meeting the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.2.2. | Any portions of the BES designed to detach from the Western Interconnection (planned islands) as a result of the operation of a relay scheme or Remedial Action Scheme. | Each Planning Coordinator will have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s), from the regional review (per D.B.1), as a basis for designing a Western Interconnection-wide coordinated UFLS program meeting the criteria in Requirement D.B.2 Parts D.B.2.1 and D.B.2.2. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the Western Interconnection, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | M1. Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 1. |  | M1. Each Planning Coordinator shall have evidence such as reports, or other documentation of its criteria to select portions of the Bulk Electric System that may form islands including how system studies and historical events were considered to develop the criteria per Requirement R1. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 2.1. | Those islands selected by applying the criteria in Requirement R1, and | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | M2. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, or other documentation supporting its identification of an island(s) as a basis for designing a UFLS program that meet the criteria in Requirement R2, Parts 2.1 through 2.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | M3. Each Planning Coordinator shall have evidence such as reports, memorandums, e-mails, program plans, or other documentation of its UFLS program, including the notification of the UFLS entities of implementation schedule, that meet the criteria in Requirement R3, Parts 3.1 through 3.3. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | M4. Each Planning Coordinator shall have dated evidence such as reports, dynamic simulation models and results, or other dated documentation of its UFLS design assessment that demonstrates it meets Requirement R4, Parts 4.1 through 4.7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | M5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 5. |  | M5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall have dated evidence such as joint UFLS program design documents, reports describing a joint UFLS design assessment, letters that include recommendations, or other dated documentation demonstrating that it coordinated its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island per Requirement R5. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 6. |  | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 7. |  | Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 8. |  | Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 9. |  | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. [VRF: High][Time Horizon: Long-term Planning] | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [19 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 10. |  | M10. Each Transmission Owner shall have dated evidence such as relay settings, tripping logic or other dated documentation that it provided automatic switching of its existing capacitor banks, Transmission Lines, and reactors in order to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, per Requirement R10. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 11.1. | The performance of the UFLS equipment, | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 11.2. | The effectiveness of the UFLS program. | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted an event assessment of the performance of the UFLS equipment and the effectiveness of the UFLS program per Requirement R11. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 12. |  | Each Planning Coordinator shall have dated evidence such as reports, data gathered from an historical event, or other dated documentation to show that it conducted a UFLS design assessment per Requirements R12 and R4 if UFLS program deficiencies are identified in R11. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | M13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for 13. |  | M13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall have dated evidence such as a joint assessment report, independent assessment reports and letters describing likely reasons for differences in conclusions and recommendations, or other dated documentation demonstrating it coordinated its event assessment (per Requirement R11) with all other Planning Coordinator(s) whose areas or portions of whose areas were also included in the same islanding event per Requirement R13. | Operations Assessment | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 14.1. | UFLS program, including a schedule for implementation | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 14.2. | UFLS design assessment | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 14.3. | Format and schedule of UFLS data submittal | Each Planning Coordinator shall have dated evidence of responses, such as e-mails and letters, to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program per Requirement R14. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | 15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall have a dated Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, that was developed within the time frame identified in Part 15.1 or 15.2. | Long-Term Planning | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RD21-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.10. | Reserved |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.10. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.7. | Reserved |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.7. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.5. | Reserved. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.5. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.6. | Reserved. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.6. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.8. | Reserved. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.8. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | D.B.9. | Reserved. |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-5 | No Parts for D.B.9. |  |  |  | 2020-08-20 | 2020-10-27 | 2020-12-23 | 2020-12-23 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RD21-1-000
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 1. | Each Planning Coordinator shall establish requirements for entities aggregating their UFLS programs for each anticipated island and requirements for compensatory load shedding based on islanding criteria (required by the NERC PRC Standard on UFLS). | M1 Each Planning Coordinator shall have evidence such as reports, system studies and/or real time power flow data captured from actual system events and other dated documentation that demonstrates it meets Requirement R1. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 1. |  | M1 Each Planning Coordinator shall have evidence such as reports, system studies and/or real time power flow data captured from actual system events and other dated documentation that demonstrates it meets Requirement R1. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 2. | Each Planning Coordinator shall, within 30 days of completion of its system studies required by the NERC PRC Standard on UFLS, identify to the Regional Entity the generation facilities within its Planning Coordinator Area necessary to support the UFLS program performance characteristics. | M2. Each Planning Coordinator shall have evidence such as dated documentation that demonstrates that it meets requirement R2. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 2. |  | M2. Each Planning Coordinator shall have evidence such as dated documentation that demonstrates that it meets requirement R2. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 3. | Each Planning Coordinator shall provide to the Transmission Owner, Distribution Provider, and Generator Owner within 30 days upon written request the requirements for entities aggregating the UFLS programs and requirements for compensatory load shedding program derived from each Planning Coordinator’s system studies as determined by Requirement R1. | M3 Each Planning Coordinator shall have evidence such as dated documentation that demonstrates that it meets Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 3. |  | M3 Each Planning Coordinator shall have evidence such as dated documentation that demonstrates that it meets Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 4. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program reflecting normal operating conditions excluding outages for its Facilities based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3, or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island identified in Requirement R1 and acting as a single entity, provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load, based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3. | M4 Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall have evidence such as documentation or reports containing the location and amount of load to be tripped, and the corresponding frequency thresholds, on those circuits included in its UFLS program to achieve the individual and cumulative percentages identified in Requirement R4. (Attachment C Tables 1-3). | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 4. |  | M4 Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall have evidence such as documentation or reports containing the location and amount of load to be tripped, and the corresponding frequency thresholds, on those circuits included in its UFLS program to achieve the individual and cumulative percentages identified in Requirement R4. (Attachment C Tables 1-3). | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 5. | Each Distribution Provider or Transmission Owner that must arm its load to trip on underfrequency in order to meet its requirements as specified and by doing so exceeds the tolerances and/or deviates from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Requirement R4 above, as applicable depending on its total peak net Load shall: | M5 Each Distribution Provider or Transmission Owner shall have evidence such as reports, analysis, system studies and dated documentation that demonstrates that it meets Requirement R5. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 5.1. | Inform its Planning Coordinator of the need to exceed the stated tolerances or the number of stages as shown in UFLS Attachment C, Table 1 if applicable and | M5 Each Distribution Provider or Transmission Owner shall have evidence such as reports, analysis, system studies and dated documentation that demonstrates that it meets Requirement R5. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 | 2016-01-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 5.2. | Provide its Planning Coordinator with a technical study that demonstrates that the Distribution Providers or Transmission Owners specific deviations from the requirements of UFLS Attachment C, Table 1 will not have a significant adverse impact on the bulk power system. | M5 Each Distribution Provider or Transmission Owner shall have evidence such as reports, analysis, system studies and dated documentation that demonstrates that it meets Requirement R5. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 | 2016-01-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 5.3. | Inform its Planning Coordinator of the need to exceed the stated tolerances of UFLS Attachment C, Table 2 or Table 3, and in the case of Attachment C, Table 2 only, the need to deviate from providing two stages of UFLS, if applicable, and | M5 Each Distribution Provider or Transmission Owner shall have evidence such as reports, analysis, system studies and dated documentation that demonstrates that it meets Requirement R5. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 | 2020-03-31 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 5.4. | Provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. | M5 Each Distribution Provider or Transmission Owner shall have evidence such as reports, analysis, system studies and dated documentation that demonstrates that it meets Requirement R5. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 | 2016-01-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 6. | Each Distribution Provider and Transmission Owner in the Québec Interconnection portion of NPCC shall implement an automatic UFLS program for its Facilities based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4 or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island, identified in Requirement R1, an aggregated automatic UFLS program that sheds Load based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4. | Each Distribution Provider and Transmission Owner in the Québec Interconnection shall have evidence such as documentation or reports containing the location and amount of load to be tripped and the corresponding frequency thresholds on those circuits included in its UFLS program to achieve the load values identified in Table 4 of Requirement R6. (Attachment C Table 4). | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 6. |  | Each Distribution Provider and Transmission Owner in the Québec Interconnection shall have evidence such as documentation or reports containing the location and amount of load to be tripped and the corresponding frequency thresholds on those circuits included in its UFLS program to achieve the load values identified in Table 4 of Requirement R6. (Attachment C Table 4). | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 7. | Each Distribution Provider and Transmission Owner shall set each underfrequency relay that is part of its region’s UFLS program with the following minimum time delay: | Each Distribution Provider and Transmission Owner shall have evidence such as documentation or reports that their underfrequency relays have been set with the minimum time delay, in accordance with Requirement R7. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 7.1. | Eastern Interconnection – 100 ms | Each Distribution Provider and Transmission Owner shall have evidence such as documentation or reports that their underfrequency relays have been set with the minimum time delay, in accordance with Requirement R7. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 | 2016-01-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 7.2. | Québec Interconnection – 200 ms | Each Distribution Provider and Transmission Owner shall have evidence such as documentation or reports that their underfrequency relays have been set with the minimum time delay, in accordance with Requirement R7. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2016-01-01 | 2016-01-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 8. | Each Planning Coordinator shall develop and review once per calendar year settings for inhibit thresholds (such as but not limited to voltage, current and time) to be utilized within its region's UFLS program. | M8 Each Planning Coordinator shall have evidence such as reports, system studies or analysis that demonstrates that it meets Requirement R8. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 8. |  | M8 Each Planning Coordinator shall have evidence such as reports, system studies or analysis that demonstrates that it meets Requirement R8. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 9. | Each Planning Coordinator shall provide each Transmission Owner and Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 30 days of the initial determination of those inhibit thresholds and within 30 days of any changes to those thresholds. | M9 Each Planning Coordinator shall provide evidence such as letters, emails, or other dated documentation that demonstrates that it meets Requirement R9. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 9. |  | M9 Each Planning Coordinator shall provide evidence such as letters, emails, or other dated documentation that demonstrates that it meets Requirement R9. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 10. | Each Distribution Provider and Transmission Owner shall implement the inhibit threshold settings based on the notification provided by the Planning Coordinator in accordance with Requirement R9. | M10 Each Distribution Provider and Transmission Owner shall provide evidence such as test reports, data sheets or other documentation that demonstrates that it meets Requirement R10. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 10. |  | M10 Each Distribution Provider and Transmission Owner shall provide evidence such as test reports, data sheets or other documentation that demonstrates that it meets Requirement R10. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 11. | Each Distribution Provider and Transmission Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with R9. | M11 Each Distribution Provider and Transmission Owner shall provide evidence such as letters, emails or other dated documentation that demonstrates that it meets Requirement R11. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 11. |  | M11 Each Distribution Provider and Transmission Owner shall provide evidence such as letters, emails or other dated documentation that demonstrates that it meets Requirement R11. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 12. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage coincident with their integrated hourly peak net Load during the previous year, as determined by measuring actual metered Load through the switches that would be opened by the UFLS relays. | M12 Each Distribution Provider and Transmission Owner shall provide evidence such as reports, spreadsheets or other dated documentation submitted to its Planning Coordinator that indicates the frequency set point, the net amount of load shed and the percentage of its peak load at each stage of its UFLS program coincident with the integrated hourly peak of the previous year that demonstrates that it meets Requirement R12. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 12. |  | M12 Each Distribution Provider and Transmission Owner shall provide evidence such as reports, spreadsheets or other dated documentation submitted to its Planning Coordinator that indicates the frequency set point, the net amount of load shed and the percentage of its peak load at each stage of its UFLS program coincident with the integrated hourly peak of the previous year that demonstrates that it meets Requirement R12. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 13. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, below the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, except as otherwise exempted in Requirements R16 and R19. | M13 Each Generator Owner shall provide evidence such as reports, data sheets, spreadsheets or other documentation that demonstrates that it meets Requirement R13. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 13. |  | M13 Each Generator Owner shall provide evidence such as reports, data sheets, spreadsheets or other documentation that demonstrates that it meets Requirement R13. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 14. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay to its Planning Coordinator within 45 days of the Planning Coordinator’s request. | M14 Each Generator Owner shall provide evidence such as emails, letters or other dated documentation that demonstrates that it meets Requirement R14. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 14. |  | M14 Each Generator Owner shall provide evidence such as emails, letters or other dated documentation that demonstrates that it meets Requirement R14. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 15. | Each Generator Owner with a new generating unit, scheduled to be in service on or after the effective date of this Standard, or an existing generator increasing its net capability by greater than 10% shall: | M15 Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R15. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 15.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 1. | M15 Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R15. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 15.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1. | M15 Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R15. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 16. | Each Generator Owner of existing non-nuclear units in service prior to the effective date of this standard that have underfrequency protections set to trip above the appropriate curve in Figure 1 shall: | Each Generator Owner with existing non-nuclear units in service prior to the effective date of this Standard which have underfrequency tripping that is not compliant with Requirement R13 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R16. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 16.1. | Set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. | Each Generator Owner with existing non-nuclear units in service prior to the effective date of this Standard which have underfrequency tripping that is not compliant with Requirement R13 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R16. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 16.2. | Transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. | Each Generator Owner with existing non-nuclear units in service prior to the effective date of this Standard which have underfrequency tripping that is not compliant with Requirement R13 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R16. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2015-07-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 16.3. | Have compensatory load shedding, as provided by a Distribution Provider or Transmission Owner that is adequate to compensate for the loss of their generator due to early tripping. | Each Generator Owner with existing non-nuclear units in service prior to the effective date of this Standard which have underfrequency tripping that is not compliant with Requirement R13 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R16. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 17. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall apply the criteria described in Attachment A to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall provide evidence such as emails, memorandum or other documentation that demonstrates that it followed the methodology described in Attachment A and meets Requirement R17. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 17. |  | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall provide evidence such as emails, memorandum or other documentation that demonstrates that it followed the methodology described in Attachment A and meets Requirement R17. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 18. | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the New York ISO shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the New York ISO shall provide evidence such as emails, memorandum, or other documentation that demonstrates that it followed the methodology described in Attachment B and meets Requirement R18. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 18. |  | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the New York ISO shall provide evidence such as emails, memorandum, or other documentation that demonstrates that it followed the methodology described in Attachment B and meets Requirement R18. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 19. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 1, based on their licensing design basis, shall: | Each Generator Owner of nuclear units that have been specifically identified by NPCC as having generator trip settings above the generator trip curve in Figure 1 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R19. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 19.1. | Set the underfrequency protection to operate at as low a frequency as possible in accordance with the plant design and licensing limitations but not greater than 57.8Hz. | Each Generator Owner of nuclear units that have been specifically identified by NPCC as having generator trip settings above the generator trip curve in Figure 1 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R19. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 19.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. | Each Generator Owner of nuclear units that have been specifically identified by NPCC as having generator trip settings above the generator trip curve in Figure 1 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R19. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 19.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. | Each Generator Owner of nuclear units that have been specifically identified by NPCC as having generator trip settings above the generator trip curve in Figure 1 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R19. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2015-07-01 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 20. | The Planning Coordinator shall update its UFLS program database as specified by the NERC PRC Standard on UFLS. This database shall include the following information: | M20 Each Planning Coordinator shall provide evidence such as spreadsheets, system studies, or other documentation that demonstrates that it meets the requirements of Requirement R20. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 20.1. | For each UFLS relay, including those used for compensatory load shedding, the amount and location of load shed at peak, the corresponding frequency threshold and time delay settings. | M20 Each Planning Coordinator shall provide evidence such as spreadsheets, system studies, or other documentation that demonstrates that it meets the requirements of Requirement R20. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 20.2. | The buses at which the Load is modeled in the NPCC library power flow case. | M20 Each Planning Coordinator shall provide evidence such as spreadsheets, system studies, or other documentation that demonstrates that it meets the requirements of Requirement R20. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 20.3. | A list of all generating units that may be tripped for underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, including the frequency trip threshold and time delay for each protection system. | M20 Each Planning Coordinator shall provide evidence such as spreadsheets, system studies, or other documentation that demonstrates that it meets the requirements of Requirement R20. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 20.4. | The location and amount of additional elements to be switched for voltage control that are coordinated with UFLS program tripping. | M20 Each Planning Coordinator shall provide evidence such as spreadsheets, system studies, or other documentation that demonstrates that it meets the requirements of Requirement R20. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 20.5. | A list of all UFLS relay inhibit functions along with the corresponding settings and locations of these relays. | M20 Each Planning Coordinator shall provide evidence such as spreadsheets, system studies, or other documentation that demonstrates that it meets the requirements of Requirement R20. | Long-Term Planning, Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 | 2013-04-29 | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 21. | Each Planning Coordinator shall notify each Distribution Provider, Transmission Owner, and Generator Owner within its Planning Coordinator area of changes to load distribution needed to satisfy UFLS program performance characteristics as specified by the NERC PRC Standard on UFLS. | Each Planning Coordinator shall provide evidence such as emails, memorandum or other dated documentation that it meets Requirement R21. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 21. |  | Each Planning Coordinator shall provide evidence such as emails, memorandum or other dated documentation that it meets Requirement R21. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 22. | Each Distribution Provider, Transmission Owner and Generator Owner shall implement the load distribution changes based on the notification provided by the Planning Coordinator in accordance with Requirement R21. | Each Distribution Provider, Transmission Owner and Generator Owner shall provide evidence such as reports, spreadsheets or other documentation that demonstrates that it meets Requirement R22. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 22. |  | Each Distribution Provider, Transmission Owner and Generator Owner shall provide evidence such as reports, spreadsheets or other documentation that demonstrates that it meets Requirement R22. | Long-Term Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | 23. | Each Distribution Provider, Transmission Owner and Generator Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with Requirement R21. | Each Distribution Provider, Transmission Owner and Generator Owner shall provide evidence such as letters, emails or other dated documentation that demonstrates it meets Requirement 23. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31 |  |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-NPCC-1 | No Parts for 23. |  | Each Distribution Provider, Transmission Owner and Generator Owner shall provide evidence such as letters, emails or other dated documentation that demonstrates it meets Requirement 23. | Operations Planning | 2012-02-09 | 2012-05-04 | 2013-02-21 | 2013-04-29 | 2015-07-01 |  | X |  |  | 2020-03-31
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 1. | Each Planning Coordinator in the Eastern Interconnection portion of NPCC shall design an UFLS program, pertaining to islands wholly within the NPCC Region, having performance characteristics that prevents the frequency from remaining below 59.5 Hz for more than 30 seconds in accordance with Figure 1. | Each Planning Coordinator shall have evidence such as reports, system studies and/or real-time power flow data captured from actual system events and other dated documentation that demonstrates it meets Requirement R1. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 1. |  | Each Planning Coordinator shall have evidence such as reports, system studies and/or real-time power flow data captured from actual system events and other dated documentation that demonstrates it meets Requirement R1. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 2. | Each Planning Coordinator shall provide UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS, to Distribution Providers, Generator Owners, and Transmission Owners within 30 calendar days of receipt of a request. | Each Planning Coordinator shall have evidence such as dated documentation that demonstrates that it meets requirement R2. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 2. |  | Each Planning Coordinator shall have evidence such as dated documentation that demonstrates that it meets requirement R2. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 3. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program, reflecting normal operating conditions, excluding outages. The automatic UFLS program shall be implemented on an island basis for each identified island per the NERC continent-wide PRC-006 Standard on UFLS as follows: • The UFLS program shall be implemented by each Distribution Provider and Transmission Owner according to the frequency thresholds, nominal operating times, and load shedding amounts specified in Attachment C, Tables 1-3; or • The UFLS program shall be implemented collectively by multiple Distribution Providers or Transmission Owners, as long as they reside in the same UFLS island identified by the Planning Coordinator per Requirement R2. These multiple Distribution Providers or Transmission Owners, via mutual agreement, shall act as a single entity to provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load according to the frequency thresholds, total nominal operating time, and load shedding amounts specified in Attachment C, Tables 1-3. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall have evidence such as documentation or reports containing the location and amount of load to be tripped in their respective areas, and the corresponding frequency thresholds, on those circuits included in its UFLS program identified in Requirement R3. (Attachment C, Tables 1-3). | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2021-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 3. |  | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall have evidence such as documentation or reports containing the location and amount of load to be tripped in their respective areas, and the corresponding frequency thresholds, on those circuits included in its UFLS program identified in Requirement R3. (Attachment C, Tables 1-3). | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2021-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 4. | Each Distribution Provider or Transmission Owner in the Eastern Interconnection portion of NPCC that does not meet the UFLS program parameters specified in Attachment C, Table 1-3, and each Distribution Provider or Transmission Owner in the Quebec Interconnection that does not meet the UFLS program parameters specified by its Planning Coordinator shall: • Within 30 calendar days of determining that it does not meet the specified parameters, notify its Planning Coordinator that it does not meet the UFLS program parameters; and • Within the following 180 calendar days from notification of the Planning Coordinator, (1) develop a Corrective Action Plan and a schedule for implementation that is mutually agreed upon with its Planning Coordinator or (2) provide its Planning Coordinator with a technical study that demonstrates that the deviations from the program parameters will not result in failure of UFLS performance criteria being met for any island. The technical study must be acceptable to the Planning Coordinator prior to implementing deviations from program parameters and shall demonstrate coordination with UFLS programs of all entities residing within the same island(s) identified by the Planning Coordinator in Requirement R2. The technical study shall also demonstrate coordination with other UFLS programs of adjoining Planning Coordinators, or (3) provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. | Each Distribution Provider or Transmission Owner shall have evidence such as reports analysis, system studies and dated documentation that demonstrates that it meets Requirement R4. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 4. |  | Each Distribution Provider or Transmission Owner shall have evidence such as reports analysis, system studies and dated documentation that demonstrates that it meets Requirement R4. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 5. | Each Planning Coordinator shall develop and review settings for inhibit thresholds at least once per five calendar years (such as, but not limited to, voltage, current and time) to be utilized within its region’s UFLS program. | Each Planning Coordinator shall have evidence such as reports, system studies or analysis that demonstrates that it meets Requirement R5. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 5. |  | Each Planning Coordinator shall have evidence such as reports, system studies or analysis that demonstrates that it meets Requirement R5. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 6. | Each Planning Coordinator shall provide each Transmission Owner and Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 30 calendar days of any changes. | Each Planning Coordinator shall provide evidence such as letters, emails or other dated documentation that demonstrates that it meets Requirement R6. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 6. |  | Each Planning Coordinator shall provide evidence such as letters, emails or other dated documentation that demonstrates that it meets Requirement R6. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 7. | Each Distribution Provider and Transmission Owner that receives a notification pursuant to Requirement R6 shall develop and submit an implementation plan with respect to inhibit thresholds for approval by the Planning Coordinator within 90 calendar days of the request from the Planning Coordinator. | Each Distribution Provider and Transmission Owner shall provide evidence such as letters, emails, or other dated documentation that demonstrates that it meets Requirement R7. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 7. |  | Each Distribution Provider and Transmission Owner shall provide evidence such as letters, emails, or other dated documentation that demonstrates that it meets Requirement R7. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 8. | Each Distribution Provider and Transmission Owner shall implement the inhibit thresholds provided by the Planning Coordinator in accordance with Requirement R6 and based on the Planning Coordinator approved implementation plan in accordance with R7. | Each Distribution Provider and Transmission Owner shall provide evidence such as test reports, data sheets, completed work orders, or other documentation that demonstrates that it meets Requirement R8. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 8. |  | Each Distribution Provider and Transmission Owner shall provide evidence such as test reports, data sheets, completed work orders, or other documentation that demonstrates that it meets Requirement R8. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 9. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 calendar months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage. The actual net Load shall be coincident with the entity’s integrated hourly peak net Load during the previous year, as determined by measuring or calculating Load through the switches that would disconnect load if triggered by the UFLS relays. If measured data is unavailable then calculated data may be used. | Each Distribution Provider and Transmission Owner shall provide evidence such as reports, spreadsheets or other dated documentation submitted to its Planning Coordinator that indicates the net amount of load shed and the percentage of its peak load at each stage of its UFLS program to demonstrate that it meets Requirement R9. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 9. |  | Each Distribution Provider and Transmission Owner shall provide evidence such as reports, spreadsheets or other dated documentation submitted to its Planning Coordinator that indicates the net amount of load shed and the percentage of its peak load at each stage of its UFLS program to demonstrate that it meets Requirement R9. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 10. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, on or below the appropriate generator underfrequency trip protection setting threshold curve in Figure 2, except as otherwise exempted in Requirements R13 and R16. | Each Generator Owner shall provide evidence such as reports, data sheets, spreadsheets or other documentation that demonstrates that it meets Requirement R10. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 10. |  | Each Generator Owner shall provide evidence such as reports, data sheets, spreadsheets or other documentation that demonstrates that it meets Requirement R10. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 11. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay within 45 calendar days of the Planning Coordinator’s request. | Each Generator Owner shall provide evidence such as emails, letters or other dated documentation that demonstrates that it meets Requirement R11. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 11. |  | Each Generator Owner shall provide evidence such as emails, letters or other dated documentation that demonstrates that it meets Requirement R11. | Operations Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 12. | Each Generator Owner with a new generating unit, or an existing generator increasing its net capability by greater than 10% shall: | Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R12. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 12.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 2. | Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R12. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 12.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection setting threshold curve in Figure 2. | Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R12. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 13. | For existing non-nuclear units in service prior to July 1, 2015, that have underfrequency protections set to trip above the appropriate curve in Figure 2: | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO | [5 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 13.1. | Each Generator Owner shall set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 13.2. | Each Generator Owner shall transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 13.3. | Each Planning Coordinator in Ontario, Québec and the Maritime Provinces shall arrange for compensatory load shedding, in accordance with Attachment A and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 13.4. | Each Generator Owner in the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator area shall arrange for compensatory load shedding, in accordance with Attachment B and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 14. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall apply the criteria described in Attachment A to determine the compensatory load shedding that is required in Requirement R13.3 for generating units in its respective NPCC area. | Each Planning Coordinator in Ontario, Quebec and Maritime provinces shall provide evidence such as reports, memorandum or other documentation that demonstrates that it followed the methodology described in Attachment A and meets Requirement R14. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 14. |  | Each Planning Coordinator in Ontario, Quebec and Maritime provinces shall provide evidence such as reports, memorandum or other documentation that demonstrates that it followed the methodology described in Attachment A and meets Requirement R14. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 15. | Each Generator Owner, Distribution Provider or Transmission Owner within the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator Area shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R13.4 for generating units in its respective NPCC area. | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the NYISO shall provide evidence such as reports, memorandum, or other documentation that demonstrates that it followed the methodology described in Attachment B and meets Requirement R15. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | No Parts for 15. |  | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the NYISO shall provide evidence such as reports, memorandum, or other documentation that demonstrates that it followed the methodology described in Attachment B and meets Requirement R15. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 16. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 2 based on their licensing design shall: | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 |  | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 16.1. | Set the underfrequency protection to operate at a frequency setting that is as low as possible in accordance with the plant design and licensing limitations but not greater than 57.8 Hz. | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 16.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-NPCC-2 | 16.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | Long-Term Planning | 2019-11-16 | 2019-12-23 | 2020-02-18 | 2020-02-18 | 2020-04-01 | 2020-04-01 | X |  |  |  | Filing/Order Docket No. RD20-1-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 1. | Each Planning Coordinator shall include its SERC subregion as an identified island in the criteria (required by the NERC PRC standard on UFLS) for selecting portions of the BPS that may form islands. | M1. Each Planning Coordinator shall have evidence such as a methodology, procedure, report, or other documentation indicating that its criteria included selection of its SERC subregion(s) as an island per Requirement R1. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 1.1. | A Planning Coordinator may adjust island boundaries to differ from subregional boundaries where necessary for the sole purpose of producing a contiguous subregional island more suitable for simulation. | M1. Each Planning Coordinator shall have evidence such as a methodology, procedure, report, or other documentation indicating that its criteria included selection of its SERC subregion(s) as an island per Requirement R1. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.1. | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.2. | Shed load with a minimum of three frequency set points. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.3. | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.5 Hz. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.3.1. | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2014-04-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.4. | The lowest frequency set point shall be no lower than 58.4 Hz. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.5. | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 2.6. | Time delay (from frequency reaching the set point to the trip signal) shall be at least six cycles. | M2. Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2014-04-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 3. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. |  | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-10-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | No Parts for 3. |  |  | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-10-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 4. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | M4. Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 4.1. | The percent of load shedding to be implemented shall be based on the actual or estimated distribution substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand. | M4. Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 4.2. | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). | M4. Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 4.3. | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. | M4. Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 5. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. |  | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 5.1. | The percent of load shedding to be implemented shall be based on the actual or estimated distribution substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand. |  | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 5.2. | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | Long-Term Planning, Operations Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 | 2015-10-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 6. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, or changes to the percentage of load in the scheme within 18 months of notification by the Planning Coordinator. | M6. Each UFLS entity shall have evidence such as reports or other documentation demonstrating that it has made the appropriate scheme changes within 18 months per Requirement R6. Such evidence is only required if the Planning Coordinator makes changes to the UFLS scheme as specified in Requirement R6. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | No Parts for 6. |  | M6. Each UFLS entity shall have evidence such as reports or other documentation demonstrating that it has made the appropriate scheme changes within 18 months per Requirement R6. Such evidence is only required if the Planning Coordinator makes changes to the UFLS scheme as specified in Requirement R6. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2015-10-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 7. | Each Planning Coordinator shall provide the following information to SERC according to the schedule specified by SERC. | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 7.1. | Underfrequency trip set points (Hz) | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2014-04-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 7.2. | Total clearing time associated with each set point (sec). This includes the time from when frequency reaches the set point and ends when the breaker opens. | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2014-04-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 7.3. | Amount of previous year actual or estimated load associated with each set point, both in percent and in MW. The percentage and the Load demand (MW) shall be based on the time coincident with the previous year actual Peak Demand. | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 8. | Each Generator Owner shall provide the following information within 30 days of a request by SERC to facilitate post-event analysis of frequency disturbances. |  | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 8.1. | Generator protection automatic underfrequency and overfrequency trip set points (Hz). |  | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 8.2. | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2014-04-01 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-01 | 8.3. | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. |  | Long-Term Planning | 2011-11-03 | 2012-02-01 | 2012-12-20 | 2013-02-25 | 2014-04-01 | 2013-02-25 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM12-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 1. | Each Planning Coordinator shall include its SERC subregion as an identified island in the criteria (required by the NERC PRC standard on UFLS) for selecting portions of the BPS that may form islands. | M1. Each Planning Coordinator shall have evidence such as a methodology, procedure, report, or other documentation indicating that its criteria included selection of its SERC subregion(s) as an island per Requirement R1. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 1.1. | A Planning Coordinator may adjust island boundaries to differ from subregional boundaries where necessary for the sole purpose of producing a contiguous subregional island more suitable for simulation. | M1. Each Planning Coordinator shall have evidence such as a methodology, procedure, report, or other documentation indicating that its criteria included selection of its SERC subregion(s) as an island per Requirement R1. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.1. | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. The Peak Demand may be either summer or winter as determined by the Planning Coordinator. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.2. | Shed load with a minimum of three frequency set points. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.3. | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.5 Hz. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.3.1. | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.4. | The lowest frequency set point shall be no lower than 58.4 Hz. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.5. | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 2.6. | Time delay (from frequency reaching the set point to the trip signal) shall be at leastsix cycles. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 3. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. | M3. Each Planning Coordinator shall have evidence such as reports or other documentation that it performed the simulations of its UFLS scheme as required in Requirement R3. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | No Parts for 3. |  | M3. Each Planning Coordinator shall have evidence such as reports or other documentation that it performed the simulations of its UFLS scheme as required in Requirement R3. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 4. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 4.1. | The percent of load shedding to be implemented shall be based on the actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 4.2. | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 4.3. | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 5. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | M5. Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 5.1. | The percent of load shedding to be implemented shall be based on the actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand in the season specified by the Planning Coordinator in R2. | M5. Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 5.2. | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. | M5. Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 6. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, changes to the percentage of load in the scheme, or changes to the peak season selected in R2.1 within 18 months of notification by the Planning Coordinator. | M6. Each UFLS entity shall have evidence such as reports or other documentation demonstrating that it has made the appropriate scheme changes within 18 months per Requirement R6. Such evidence is only required if the Planning Coordinator makes changes to the UFLS scheme as specified in Requirement R6. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | No Parts for 6. |  | M6. Each UFLS entity shall have evidence such as reports or other documentation demonstrating that it has made the appropriate scheme changes within 18 months per Requirement R6. Such evidence is only required if the Planning Coordinator makes changes to the UFLS scheme as specified in Requirement R6. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 7. | Each Planning Coordinator shall provide the following information to SERC according to the schedule specified by SERC. | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 7.1. | Underfrequency trip set points (Hz) | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 7.2. | Total clearing time associated with each set point (sec). This includes the time from when frequency reaches the set point and ends when the breaker opens. | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 7.3. | Amount of previous year actual or estimated load associated with each set point, both in percent and in MW. The percentage and the Load demand (MW) shall be based on the time coincident with the previous year actual Peak Demand. | M7. Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 8. | Each Generator Owner shall provide the following information within 30 days of a request by SERC to facilitate post-event analysis of frequency disturbances. | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 |  |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 8.1. | Generator protection automatic underfrequency and overfrequency trip set points (Hz). | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 8.2. | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SERC-02 | 8.3. | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2017-08-10 | 2017-09-08 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  | 2022-03-31 | Filing/Order Docket No. RD17-9-000 |  | DP | DP-UFLS |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 1. | Intentionally omitted |  |  | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | No Parts for 1. |  |  |  | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.1. | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. The Peak Demand may be either summer or winter as determined by the Planning Coordinator. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.2. | Shed load with a minimum of three frequency set points. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.3. | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.6 Hz. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.3.1. | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.4. | The lowest frequency set point shall be no lower than 58.2 Hz. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.4.1. | At least 30% of peak demand shall be set greater than or equal to 58.4 Hz | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.5. | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 2.6. | Time delay setting shall be at least six cycles (0.1 seconds). | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [7 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 3. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. | Each Planning Coordinator shall have evidence such as reports or other documentation that it performed the simulations of its UFLS scheme as required in Requirement R3. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | No Parts for 3. |  | Each Planning Coordinator shall have evidence such as reports or other documentation that it performed the simulations of its UFLS scheme as required in Requirement R3. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 4. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 4.1. | The percent of load shedding to be implemented shall be based on either: A. The actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. B. The forecasted substation or feeder demand (including losses) of the UFLS entities at the time coincident with the next year’s forecasted Peak Demand in the season specified by the Planning Coordinator in R2. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 4.2. | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 4.3. | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 5. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 5.1. | The percent of load shedding to be implemented shall be based on either: A. The actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. B. The forecasted substation or feeder demand (including losses) of the UFLS entities at the time coincident with the next year’s forecasted Peak Demand in the season specified by the Planning Coordinator in R2. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 5.2. | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | Operations Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 6. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, changes to the percentage of load in the scheme, or changes to the peak season selected in R2.1 within 18 months of notification by the Planning Coordinator. | Each UFLS entity shall have evidence such as reports or other documentation demonstrating that it has made the appropriate scheme changes within 18 months per Requirement R6. Such evidence is only required if the Planning Coordinator makes changes to the UFLS scheme as specified in Requirement R6. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | No Parts for 6. |  | Each UFLS entity shall have evidence such as reports or other documentation demonstrating that it has made the appropriate scheme changes within 18 months per Requirement R6. Such evidence is only required if the Planning Coordinator makes changes to the UFLS scheme as specified in Requirement R6. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 7. | Intentionally omitted |  |  | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | No Parts for 7. |  |  |  | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 8. | Each Generator Owner shall provide the following information within 30 days of a request by SERC or Planning Coordinator to facilitate post-event analysis of frequency disturbances. | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | [5 empty] | Filing/Order Docket No. RD22-1-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 8.1. | Generator protection automatic underfrequency and overfrequency trip set points (Hz). | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 8.2. | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006 | PRC-006-SERC-03 | 8.3. | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | Long-Term Planning | 2021-11-04 | 2021-12-14 | 2022-02-18 | 2022-02-18 | 2022-04-01 | 2022-04-01 |  |  |  |  | Filing/Order Docket No. RD22-1-000 |  | DP | DP-UFLS |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 1. | Each UFLS entity that has a total forecasted peak Load greater than or equal to 100 MW shall develop and implement an automatic UFLS program that meets the following requirements: (please see the standard for the sub-requirements) | Each UFLS entity shall have evidence such as reports, program plans, or other documentation of its UFLS program that demonstrates it meets requirement R1 Parts 1.1 through 1.3. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 1.1. | A minimum of 10% shall be shed at each UFLS step in accordance with the table below. See standard for table. | Each UFLS entity shall have evidence such as reports, program plans, or other documentation of its UFLS program that demonstrates it meets requirement R1 Parts 1.1 through 1.3. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 1.2. | The intentional relay time delay for UFLS shall be less than or equal to 30 cycles. | Each UFLS entity shall have evidence such as reports, program plans, or other documentation of its UFLS program that demonstrates it meets requirement R1 Parts 1.1 through 1.3. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 1.3. | Undervoltage inhibit setting shall be less than or equal to 85 percent of nominal voltage. | Each UFLS entity shall have evidence such as reports, program plans, or other documentation of its UFLS program that demonstrates it meets requirement R1 Parts 1.1 through 1.3. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 2. | Each UFLS entity that has a total forecasted peak Load less than 100 MW shall develop and implement an automatic UFLS program that meets the following requirements: (please see the standard for the sub-requirements) |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 2.1. | A minimum of one UFLS step with the frequency set point as assigned by the Planning Coordinator. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 2.2. | The minimum accumulated Load relief shall be at least 30% of the forecasted peak Load. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 2.3. | The intentional relay time delay for UFLS shall be less than or equal to 30 cycles. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 2.4. | Undervoltage inhibit setting shall be less than or equal to 85 percent of nominal voltage. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 3. | Each UFLS entity electing to use underfrequency islanding schemes shall design those islanding schemes to operate after all 3 steps of UFLS have been exhausted and the frequency continues to fall to 58.5 Hz or below. For islanding schemes designed to operate at or between 58.5 Hz and 58.0 Hz, the minimum time delay shall be 2 seconds. For islanding schemes designed to operate below 58.0 Hz, no time delay is required. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | No Parts for 3. |  |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 4. | The Planning Coordinator shall perform and document a UFLS technical assessment within one year after the occurrence of any of the following situations: • Performance characteristic changes to PRC-006 or the SPP UFLS standard. • Changes to the boundaries of a specified island are identified. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | No Parts for 4. |  |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5. | Each UFLS entity shall maintain and submit the following UFLS data based on the forecasted peak Load to the Planning Coordinator within (30) calendar days upon request from the Planning Coordinator: (please see standard for the sub-requirements) |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.1. | Location of installed UFLS equipment |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.2. | Trip frequency(s) for each location |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.3. | Total relay operating time of each location (time required for the relay to reliably sense the frequency + intentional delay time (if any)) |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.4. | Breaker operating time (nameplate) of each location |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.5. | Percentage and/or MW of bus load to be shed at the location |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.6. | Total amount of load shed by each trip frequency and the total forecasted peak Load |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.7. | Tie tripping schemes and the frequency and time delay at which they operate |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 5.8. | Islanding schemes and the frequency and time delay at which they operate |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 6. | Each Generator Owner shall maintain and submit the following data to the Planning Coordinator within (30) calendar days upon request from the Planning Coordinator: (please see the standard for the sub-requirements) | Each Generator Owner shall have evidence that the information was supplied to the Planning Coordinator per requirement R6. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 6.1. | Location of underfrequency and overfrequency equipment | Each Generator Owner shall have evidence that the information was supplied to the Planning Coordinator per requirement R6. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 6.2. | Trip frequency(s) for each location | Each Generator Owner shall have evidence that the information was supplied to the Planning Coordinator per requirement R6. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 6.3. | Total relay operating time of each location (time required for the relay to reliably sense the frequency + intentional delay time (if any)) | Each Generator Owner shall have evidence that the information was supplied to the Planning Coordinator per requirement R6. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 6.4. | Breaker operating time (nameplate) of each location | Each Generator Owner shall have evidence that the information was supplied to the Planning Coordinator per requirement R6. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 6.5. | MW of generation shed at each location | Each Generator Owner shall have evidence that the information was supplied to the Planning Coordinator per requirement R6. | Long-Term Planning | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 7. | Each Generator Owner shall verify that their generating unit(s) will not trip above the Generator underfrequency curve in Attachment 1 and will not trip below the Generator overfrequency curve in Attachment 2 as a result of the unit(s) frequency protective relay settings. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 7.1. | For generating units with operating characteristics that limit the unit’s ability to perform in accordance with R7, the Generator Owner shall provide to the Planning Coordinator technical evidence demonstrating that the unit cannot operate within the specified frequency range without causing equipment damage or violating manufacturer’s published equipment ratings. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 8. | The Planning Coordinator shall determine if the Generator Owner has provided technical evidence demonstrating that the unit cannot operate within the specified frequency range without causing equipment damage or violating manufacturer’s published equipment ratings. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 8.1. | The Planning Coordinator shall determine if the UFLS program performance is degraded due to the removal of any generation identified in accordance with R7.1 and verified in accordance with R8. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 8.1.1. | If the Planning Coordinator determines the UFLS program is degraded in accordance with R8.1 and that supplementary load shedding is, therefore, required, the Planning Coordinator shall notify the Generator Owner or UFLS entity(s) in accordance with the following:  Where the Generator Owner is a UFLS Entity and has the required amount of supplementary Load available, the Planning Coordinator shall notify the Generator Owner of Load the entity is required to shed (in addition to that required in accordance with R1 and R2)  Where the Generator Owner is not a UFLS Entity, or does not have the required supplementary Load available for shedding, the Planning Coordinator shall notify any other UFLS Entity(s) within the Planning Coordinator Area of Load the entity(s) is required to shed (in addition to that required in accordance with R1 and R2) |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | 9. | The Generator Owner or other UFLS entity(s) shall implement supplementary shedding of Load required by the Planning Coordinator in accordance with R8.1.1. |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000 |  |  |  |  | GO
Inactive | PRC | PRC-006 | PRC-006-SPP-01 | No Parts for 9. |  |  |  | 2012-11-07 | 2013-04-26 | [7 empty] | 2013-11-07 | Filing/Order Docket No. RD13-9-000
Inactive | PRC | PRC-007 | PRC-007-0 | 1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall ensure that its UFLS program is consistent with its Regional Reliability Organization’s UFLS program requirements. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-007 | PRC-007-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-007 | PRC-007-0 | 2. | The Transmission Owner, Transmission Operator, Distribution Provider, and Load-Serving Entity that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide, and annually update, its underfrequency data as necessary for its Regional Reliability Organization to maintain and update a UFLS program database. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-007 | PRC-007-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-007 | PRC-007-0 | 3. | The Transmission Owner and Distribution Provider that owns a UFLS program (as required by its Regional Reliability Organization) shall provide its documentation of that UFLS program to its Regional Reliability Organization on request (30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-007 | PRC-007-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | PRC | PRC-008 | PRC-008-0 | 1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | M1. Each Transmission Owner’s and Distribution Provider’s UFLS equipment maintenance and testing program contains the elements specified in Reliability Standard PRC-008-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-008 | PRC-008-0 | No Parts for 1. |  | M1. Each Transmission Owner’s and Distribution Provider’s UFLS equipment maintenance and testing program contains the elements specified in Reliability Standard PRC-008-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | PRC | PRC-008 | PRC-008-0 | 2. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | M2. Each Transmission Owner and Distribution Provider shall have evidence that it provided the results of its UFLS equipment maintenance and testing program’s implementation to its Regional Reliability Organization and NERC on request (within 30 calendar days). | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-008 | PRC-008-0 | No Parts for 2. |  | M2. Each Transmission Owner and Distribution Provider shall have evidence that it provided the results of its UFLS equipment maintenance and testing program’s implementation to its Regional Reliability Organization and NERC on request (within 30 calendar days). | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-009 | PRC-009-0 | 1. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall analyze and document its UFLS program performance in accordance with its Regional Reliability Organization’s UFLS program. The analysis shall address the performance of UFLS equipment and program effectiveness following system events resulting in system frequency excursions below the initializing set points of the UFLS program. The analysis shall include, but not be limited to: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009 | PRC-009-0 | 1.1. | A description of the event including initiating conditions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009 | PRC-009-0 | 1.2. | A review of the UFLS set points and tripping times. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009 | PRC-009-0 | 1.3. | A simulation of the event. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009 | PRC-009-0 | 1.4. | A summary of the findings. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009 | PRC-009-0 | 2. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide documentation of the analysis of the UFLS program to its Regional Reliability Organization and NERC on request 90 calendar days after the system event. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009 | PRC-009-0 | No Parts for 2. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-010 | PRC-010-0 | 1. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | M1. Each Transmission Owner’s and Distribution Provider’s UVLS program shall include the elements identified in Reliability Standard PRC-010-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010 | PRC-010-0 | 1.1. | This assessment shall include, but is not limited to: | M1. Each Transmission Owner’s and Distribution Provider’s UVLS program shall include the elements identified in Reliability Standard PRC-010-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010 | PRC-010-0 | 1.1.1. | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. | M1. Each Transmission Owner’s and Distribution Provider’s UVLS program shall include the elements identified in Reliability Standard PRC-010-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010 | PRC-010-0 | 1.1.2. | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. | M1. Each Transmission Owner’s and Distribution Provider’s UVLS program shall include the elements identified in Reliability Standard PRC-010-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010 | PRC-010-0 | 1.1.3. | A review of the voltage set points and timing. | M1. Each Transmission Owner’s and Distribution Provider’s UVLS program shall include the elements identified in Reliability Standard PRC-010-0_R1. | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010 | PRC-010-0 | 2. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall provide documentation of its current UVLS program assessment to its Regional Reliability Organization and NERC on request (30 calendar days). |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010 | PRC-010-0 | No Parts for 2. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-010 | PRC-010-1 | 1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: | M1. Acceptable evidence may include, but is not limited to, date‐stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date‐stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | 1.1. | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. | M1. Acceptable evidence may include, but is not limited to, date‐stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date‐stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | 1.2. | The UVLS Program isintegrated through coordination with generator voltage ride‐through capabilities and other protection and controlsystems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | M1. Acceptable evidence may include, but is not limited to, date‐stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date‐stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | 2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. | M2. Acceptable evidence must include date‐stamped documentation on the completion of actions and may include, but is not limited to, identifying the equipment armed with UVLS relays, the UVLS relay settings, associated Load summaries, work management program records, work orders, and maintenance records. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-010 | PRC-010-1 | No Parts for 2. |  | M2. Acceptable evidence must include date‐stamped documentation on the completion of actions and may include, but is not limited to, identifying the equipment armed with UVLS relays, the UVLS relay settings, associated Load summaries, work management program records, work orders, and maintenance records. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000
Inactive | PRC | PRC-010 | PRC-010-1 | 3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: | M3. Acceptable evidence may include, but is not limited to, date‐stamped reports or other documentation detailing the assessment of the UVLS Program. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | 3.1. | The UVLS Program resolvesthe identified undervoltage issuesfor which the UVLS Program is designed. | M3. Acceptable evidence may include, but is not limited to, date‐stamped reports or other documentation detailing the assessment of the UVLS Program. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | 3.2. | The UVLS Program isintegrated through coordination with generator voltage ride‐through capabilities and other protection and controlsystems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | M3. Acceptable evidence may include, but is not limited to, date‐stamped reports or other documentation detailing the assessment of the UVLS Program. | Long-Term Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | 4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate whether its UVLS Program resolved the undervoltage issues associated with the event. | M4. Acceptable evidence may include, but is not limited to, date‐stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | No Parts for 4. |  | M4. Acceptable evidence may include, but is not limited to, date‐stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000
Inactive | PRC | PRC-010 | PRC-010-1 | 5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies in its UVLS Program during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. | Acceptable evidence must include a date‐stamped Corrective Action Plan that addresses identified deficiencies and may also include date‐stamped reports or other documentation supporting the Corrective Action Plan. Evidence should also include date‐stamped communications showing that the Corrective Action Plan and an associated implementation schedule were provided to UVLS entities. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | PRC | PRC-010 | PRC-010-1 | No Parts for 5. |  | Acceptable evidence must include a date‐stamped Corrective Action Plan that addresses identified deficiencies and may also include date‐stamped reports or other documentation supporting the Corrective Action Plan. Evidence should also include date‐stamped communications showing that the Corrective Action Plan and an associated implementation schedule were provided to UVLS entities. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000
Inactive | PRC | PRC-010 | PRC-010-1 | 6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. | Acceptable evidence may include, but is not limited to, date‐stamped spreadsheets, database reports, or other documentation demonstrating a UVLS Program database was updated. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-010 | PRC-010-1 | No Parts for 6. |  | Acceptable evidence may include, but is not limited to, date‐stamped spreadsheets, database reports, or other documentation demonstrating a UVLS Program database was updated. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000
Inactive | PRC | PRC-010 | PRC-010-1 | 7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. | Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating data was provided to the Planning Coordinator as specified. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-010 | PRC-010-1 | No Parts for 7. |  | Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating data was provided to the Planning Coordinator as specified. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000
Inactive | PRC | PRC-010 | PRC-010-1 | 8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. | Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating that the UVLS Program database was provided within 30 calendar days of receipt of a written request. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-010 | PRC-010-1 | No Parts for 8. |  | Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating that the UVLS Program database was provided within 30 calendar days of receipt of a written request. | Operations Planning | 2014-11-13 | 2015-02-06 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM15-12-000
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: | Acceptable evidence may include, but is not limited to, date-stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date-stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 1.1. | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. | Acceptable evidence may include, but is not limited to, date-stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date-stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  |  | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 1.2. | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. | Acceptable evidence may include, but is not limited to, date-stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date-stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  |  | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. | M2. Acceptable evidence must include date‐stamped documentation on the completion of actions and may include, but is not limited to, identifying the equipment armed with UVLS relays, the UVLS relay settings, associated Load summaries, work management program records, work orders, and maintenance records. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | No Parts for 2. |  | M2. Acceptable evidence must include date‐stamped documentation on the completion of actions and may include, but is not limited to, identifying the equipment armed with UVLS relays, the UVLS relay settings, associated Load summaries, work management program records, work orders, and maintenance records. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: | M3. Acceptable evidence may include, but is not limited to, date‐stamped reports or other documentation detailing the assessment of the UVLS Program. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 3.1. | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. | M3. Acceptable evidence may include, but is not limited to, date‐stamped reports or other documentation detailing the assessment of the UVLS Program. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  |  | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 3.2. | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. | M3. Acceptable evidence may include, but is not limited to, date‐stamped reports or other documentation detailing the assessment of the UVLS Program. | Long-Term Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  |  | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: | Acceptable evidence may include, but is not limited to, date-stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program and associated equipment. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 4.1. | Whether its UVLS Program resolved the undervoltage issues associated with the event, and | Acceptable evidence may include, but is not limited to, date-stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program and associated equipment. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2017-04-02 |  |  |  |  | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 4.2. | The performance (i.e., operation and non-operation) of the UVLS Program equipment. | Acceptable evidence may include, but is not limited to, date-stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program and associated equipment. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | 2015-11-19 |  |  |  |  | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. | Acceptable evidence must include a date-stamped Corrective Action Plan that addresses identified deficiencies and may also include date-stamped reports or other documentation supporting the Corrective Action Plan. Evidence should also include date-stamped communications showing that the Corrective Action Plan and an associated implementation schedule were provided to UVLS entities. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | No Parts for 5. |  | Acceptable evidence must include a date-stamped Corrective Action Plan that addresses identified deficiencies and may also include date-stamped reports or other documentation supporting the Corrective Action Plan. Evidence should also include date-stamped communications showing that the Corrective Action Plan and an associated implementation schedule were provided to UVLS entities. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. | M6. Acceptable evidence may include, but is not limited to, date‐stamped spreadsheets, database reports, or other documentation demonstrating a UVLS Program database was updated. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | No Parts for 6. |  | M6. Acceptable evidence may include, but is not limited to, date‐stamped spreadsheets, database reports, or other documentation demonstrating a UVLS Program database was updated. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. | M7. Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating data was provided to the Planning Coordinator as specified. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | No Parts for 7. |  | M7. Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating data was provided to the Planning Coordinator as specified. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | 8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. | M8. Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating that the UVLS Program database was provided within 30 calendar days of receipt of a written request. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-010 | PRC-010-2 | No Parts for 8. |  | M8. Acceptable evidence may include, but is not limited to, date‐stamped emails, letters, or other documentation demonstrating that the UVLS Program database was provided within 30 calendar days of receipt of a written request. | Operations Planning | 2015-05-07 | 2015-06-08 | 2015-11-19 | 2015-11-19 | 2017-04-02 | [5 empty] | Filing/Order Docket No. RD15-5-000
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.1. | The UVLS system identification which shall include but is not limited to: | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.1.1. | Relays. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.1.2. | Instrument transformers. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.1.3. | Communications systems, where appropriate. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.1.4. | Batteries. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.1. DO NOT USE | The UVLS system identification which shall include but is not limited to: | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.2. | Documentation of maintenance and testing intervals and their basis. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.3. | Summary of testing procedure. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.4. | Schedule for system testing. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.5. | Schedule for system maintenance. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 1.6. | Date last tested/maintained. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | 2. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | M2. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have evidence it provided documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program as specified in Reliability Standard PRC-011-0_R2. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011 | PRC-011-0 | No Parts for 2. |  | M2. Each Transmission Owner and Distribution Provider that owns a UVLS system shall have evidence it provided documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program as specified in Reliability Standard PRC-011-0_R2. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-012 | PRC-012-0 | 1. | Each Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Providers that uses or is planning to use an SPS shall have a documented Regional Reliability Organization SPS review procedure to ensure that SPSs comply with Regional criteria and NERC Reliability Standards. The Regional SPS review procedure shall include: | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.1. | Description of the process for submitting a proposed SPS for Regional Reliability Organization review. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.2. | Requirements to provide data that describes design, operation, and modeling of an SPS. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.3. | Requirements to demonstrate that the SPS shall be designed so that a single SPS component failure, when the SPS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.4. | Requirements to demonstrate that the inadvertent operation of an SPS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.5. | Requirements to demonstrate the proposed SPS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.6. | Regional Reliability Organization definition of misoperation. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.7. | Requirements for analysis and documentation of corrective action plans for all SPS misoperations. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.8. | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 1.9. | Determination, as appropriate, of maintenance and testing requirements. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | 2. | The Regional Reliability Organization shall provide affected Regional Reliability Organizations and NERC with documentation of its SPS review procedure on request (within 30 calendar days). | M2. The Regional Reliability Organization shall have evidence it provided affected Regional Reliability Organizations and NERC with documentation of its SPS review procedure on request (within 30 calendar days). | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-0 | No Parts for 2. |  | M2. The Regional Reliability Organization shall have evidence it provided affected Regional Reliability Organizations and NERC with documentation of its SPS review procedure on request (within 30 calendar days). | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-012 | PRC-012-1 | 1. | Each Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Providers that uses or is planning to use a RAS shall have a documented Regional Reliability Organization RAS review procedure to ensure that RAS comply with Regional criteria and NERC Reliability Standards. The Regional RAS review procedure shall include: | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.1. | Description of the process for submitting a proposed RAS for Regional Reliability Organization review. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.2. | Requirements to provide data that describes design, operation, and modeling of a RAS. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.3. | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.4. | Requirements to demonstrate that the inadvertent operation of a RAS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.5. | Requirements to demonstrate the proposed RAS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.6. | Regional Reliability Organization definition of misoperation. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.7. | Requirements for analysis and documentation of corrective action plans for all RAS misoperations. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.8. | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 1.9. | Determination, as appropriate, of maintenance and testing requirements. | M1. The Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Provider using or planning to use a RAS shall have a documented Regional review procedure as defined in Reliability Standard PRC-012-1_R1. | Long-Term Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | 2. | The Regional Reliability Organization shall provide affected Regional Reliability Organizations and NERC with documentation of its RAS review procedure on request (within 30 calendar days). | M2. The Regional Reliability Organization shall have evidence it provided affected Regional Reliability Organizations and NERC with documentation of its RAS review procedure on request (within 30 calendar days). | Operations Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-012 | PRC-012-1 | No Parts for 2. |  | M2. The Regional Reliability Organization shall have evidence it provided affected Regional Reliability Organizations and NERC with documentation of its RAS review procedure on request (within 30 calendar days). | Operations Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 1. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS-entity shall provide the information identified in Attachment 1 for review to the Reliability Coordinator(s) where the RAS is located. | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | No Parts for 1. |  | M1. Acceptable evidence may include, but is not limited to, a copy of the Attachment 1 documentation and the dated communications with the reviewing Reliability Coordinator(s) in accordance with Requirement R1. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 2. | Each Reliability Coordinator that receives Attachment 1 information pursuant to Requirement R1 shall, within four full calendar months of receipt or on a mutually agreed upon schedule, perform a review of the RAS in accordance with Attachment 2, and provide written feedback to each RAS-entity. | M2. Acceptable evidence may include, but is not limited to, dated reports, checklists, or other documentation detailing the RAS review, and the dated communications with the RAS-entity in accordance with Requirement R2. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | No Parts for 2. |  | M2. Acceptable evidence may include, but is not limited to, dated reports, checklists, or other documentation detailing the RAS review, and the dated communications with the RAS-entity in accordance with Requirement R2. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 3. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS‐entity that receives feedback from the reviewing Reliability Coordinator(s) identifying reliability issue(s) shall resolve each issue to obtain approval of the RAS from each reviewing Reliability Coordinator. | M3. Acceptable evidence may include, but is not limited to, dated documentation and communications with the reviewing Reliability Coordinator that no reliability issues were identified during the review or that all identified reliability issues were resolved in accordance with Requirement R3. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | No Parts for 3. |  | M3. Acceptable evidence may include, but is not limited to, dated documentation and communications with the reviewing Reliability Coordinator that no reliability issues were identified during the review or that all identified reliability issues were resolved in accordance with Requirement R3. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4. | Each Planning Coordinator, at least once every five full calendar years, shall: | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 |  |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1. | Perform an evaluation of each RAS within its planning area to determine whether: | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.1. | The RAS mitigates the System condition(s) or Contingency(ies) for which it was designed. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.2. | The RAS avoids adverse interactions with other RAS, and protection and control systems. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.3. | For limited impact RAS, the inadvertent operation of the RAS or the failure of the RAS to operate does not cause or contribute to BES Cascading, uncontrolled separation, angular instability, voltage instability, voltage collapse, or unacceptably damped oscillations. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.4. | Except for limited impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following: | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.4.1. | The BES shall remain stable. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.4.2. | Cascading shall not occur. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.4.3. | Applicable Facility Ratings shall not be exceeded. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.4.4. | BES voltages shall be within post-Contingency voltage limits and post-Contingency voltage deviation limits as established by the Transmission Planner and the Planning Coordinator. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.4.5. | Transient voltage responses shall be within acceptable limits as established by the Transmission Planner and the Planning Coordinator. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.1.5. | Except for limited impact RAS, a single component failure in the RAS, when the RAS is intended to operate does not prevent the BES from meeting the same performance requirements (defined in Reliability Standard TPL-001-4 or its successor) as those required for the events and conditions for which the RAS is designed. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 4.2. | Provide the results of the RAS evaluation including any identified deficiencies to each reviewing Reliability Coordinator and RAS-entity, and each impacted Transmission Planner and Planning Coordinator. | M4. Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  | Requirement R4 For existing RAS, initial performance of obligations under Requirement R4 must be completed within five (5) full calendar years after the effective date of PRC-012-2, as described above. For new or functionally modified RAS, the initial performance of Requirement R4 must be completed within five (5) full calendar years after the date that the RAS is approved by the reviewing RC(s) under Requirement R3 |  |  | Filing/Order Docket No. RM16-20-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5. | Each RAS-entity, within 120 full calendar days of a RAS operation or a failure of its RAS to operate when expected, or on a mutually agreed upon schedule with its reviewing Reliability Coordinator(s), shall: | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5.1. | Participate in analyzing the RAS operational performance to determine whether: | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5.1.1. | The System events and/or conditions appropriately triggered the RAS. | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5.1.2. | The RAS responded as designed. | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5.1.3. | The RAS was effective in mitigating BES performance issues it was designed to address. | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5.1.4. | The RAS operation resulted in any unintended or adverse BES response. | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 5.2. | Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). | M5. Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 6. | Each RAS-entity shall participate in developing a Corrective Action Plan (CAP) and submit the CAP to its reviewing Reliability Coordinator(s) within six full calendar months of: • Being notified of a deficiency in its RAS pursuant to Requirement R4, or • Notifying the Reliability Coordinator of a deficiency pursuant to Requirement R5, Part 5.2, or • Identifying a deficiency in its RAS pursuant to Requirement R8. | M6. Acceptable evidence may include, but is not limited to, a dated CAP and dated communications among each reviewing Reliability Coordinator and each RAS-entity in accordance with Requirement R6. | Long-Term Planning, Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | No Parts for 6. |  | M6. Acceptable evidence may include, but is not limited to, a dated CAP and dated communications among each reviewing Reliability Coordinator and each RAS-entity in accordance with Requirement R6. | Long-Term Planning, Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 7. | Each RAS-entity shall, for each of its CAPs developed pursuant to Requirement R6: | M7. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | Long-Term Planning, Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | [5 empty] | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 7.1. | Implement the CAP. | M7. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | Long-Term Planning, Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 7.2. | Update the CAP if actions or timetables change. | M7. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | Long-Term Planning, Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 7.3. | Notify each reviewing Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. | M7. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | Long-Term Planning, Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 | 2021-01-01 |  |  |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 8. | Each RAS-entity shall participate in performing a functional test of each of its RAS to verify the overall RAS performance and the proper operation of non-Protection System components: • At least once every six full calendar years for all RAS not designated as limited impact, or • At least once every twelve full calendar years for all RAS designated as limited impact | M8. Acceptable evidence may include, but is not limited to, dated documentation detailing the RAS operational performance analysis for a correct RAS segment or an end-to-end operation (Measure M5 documentation), or dated documentation demonstrating that a functional test of each RAS segment or an end-to-end test was performed in accordance with Requirement R8. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 |  |  | Requirement R8 For each RAS not designated as limited impact, initial performance of obligations under Requirement R8 must be completed at least once within six (6) full calendar years after the effective date for PRC-012-2, as described above. For each RAS designated as limited impact, initial performance of obligations under Requirement R8 must be completed at least once within twelve (12) full calendar years after the effective date for PRC-012-2, as described above. |  |  | Filing/Order Docket No. RM16-20-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | No Parts for 8. |  | M8. Acceptable evidence may include, but is not limited to, dated documentation detailing the RAS operational performance analysis for a correct RAS segment or an end-to-end operation (Measure M5 documentation), or dated documentation demonstrating that a functional test of each RAS segment or an end-to-end test was performed in accordance with Requirement R8. | Long-Term Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 |  |  | Requirement R8 For each RAS not designated as limited impact, initial performance of obligations under Requirement R8 must be completed at least once within six (6) full calendar years after the effective date for PRC-012-2, as described above. For each RAS designated as limited impact, initial performance of obligations under Requirement R8 must be completed at least once within twelve (12) full calendar years after the effective date for PRC-012-2, as described above. |  |  | Filing/Order Docket No. RM16-20-000
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | 9. | Each Reliability Coordinator shall update a RAS database containing, at a minimum, the information in Attachment 3 at least once every twelve full calendar months. | M9. Acceptable evidence may include, but is not limited to, dated spreadsheets, database reports, or other documentation demonstrating a RAS database was updated in accordance with Requirement R9. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 |  |  | Requirement R9 For each Reliability Coordinator that does not have a RAS database, the initial obligation under Requirement R9 is to establish a database by the effective date of PRC-012-2. Each Reliability Coordinator will perform the obligation of Requirement R9 within twelve full calendar months after the effective date of PRC-012-2, as described above. |  |  | Filing/Order Docket No. RM16-20-000 | [13 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-012 | PRC-012-2 | No Parts for 9. |  | M9. Acceptable evidence may include, but is not limited to, dated spreadsheets, database reports, or other documentation demonstrating a RAS database was updated in accordance with Requirement R9. | Operations Planning | 2016-05-05 | 2016-08-05 | 2017-09-20 | 2017-11-27 | 2021-01-01 |  |  | Requirement R9 For each Reliability Coordinator that does not have a RAS database, the initial obligation under Requirement R9 is to establish a database by the effective date of PRC-012-2. Each Reliability Coordinator will perform the obligation of Requirement R9 within twelve full calendar months after the effective date of PRC-012-2, as described above. |  |  | Filing/Order Docket No. RM16-20-000
Inactive | PRC | PRC-013 | PRC-013-0 | 1. | The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Provider with an SPS installed shall maintain an SPS database. The database shall include the following types of information: | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with an SPS installed, shall have an SPS database as defined in PRC-013-0_R1 of this Reliability Standard. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-0 | 1.1. | Design Objectives — Contingencies and system conditions for which the SPS was designed, | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with an SPS installed, shall have an SPS database as defined in PRC-013-0_R1 of this Reliability Standard. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-0 | 1.2. | Operation — The actions taken by the SPS in response to Disturbance conditions, and | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with an SPS installed, shall have an SPS database as defined in PRC-013-0_R1 of this Reliability Standard. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-0 | 1.3. | Modeling — Information on detection logic or relay settings that control operation of the SPS. | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with an SPS installed, shall have an SPS database as defined in PRC-013-0_R1 of this Reliability Standard. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-0 | 2. | The Regional Reliability Organization shall provide to affected Regional Reliability Organization(s) and NERC documentation of its database or the information therein on request (within 30 calendar days). | M2. The Regional Reliability Organization shall have evidence it provided documentation of its database or the information therein, to affected Regional Reliability Organization(s) and NERC on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-0 | No Parts for 2. |  | M2. The Regional Reliability Organization shall have evidence it provided documentation of its database or the information therein, to affected Regional Reliability Organization(s) and NERC on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-013 | PRC-013-1 | 1. | The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Provider with a RAS installed shall maintain a RAS database. The database shall include the following types of information: | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with a RAS installed, shall have a RAS database as defined in PRC-013-1_R1 of this Reliability Standard. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-1 | 1.1. | Design Objectives — Contingencies and system conditions for which the RAS was designed, | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with a RAS installed, shall have a RAS database as defined in PRC-013-1_R1 of this Reliability Standard. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-1 | 1.2. | Operation — The actions taken by the RAS in response to Disturbance conditions, and | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with a RAS installed, shall have a RAS database as defined in PRC-013-1_R1 of this Reliability Standard. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-1 | 1.3. | Modeling — Information on detection logic or relay settings that control operation of the RAS. | M1. The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Providers with a RAS installed, shall have a RAS database as defined in PRC-013-1_R1 of this Reliability Standard. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-1 | 2. | The Regional Reliability Organization shall provide to affected Regional Reliability Organization(s) and NERC documentation of its database or the information therein on request (within 30 calendar days). | M2. The Regional Reliability Organization shall provide either a summary report or a detailed report of this assessment to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-013 | PRC-013-1 | No Parts for 2. |  | M2. The Regional Reliability Organization shall provide either a summary report or a detailed report of this assessment to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-014 | PRC-014-0 | 1. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all SPSs installed in its Region at least once every five years for compliance with NERC Reliability Standards and Regional criteria. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all SPSs installed in its Region at least once every five years for compliance with NERC standards and Regional criteria. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | No Parts for 1. |  | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all SPSs installed in its Region at least once every five years for compliance with NERC standards and Regional criteria. |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-014 | PRC-014-0 | 2. | The Regional Reliability Organization shall provide either a summary report or a detailed report of its assessment of the operation, coordination, and effectiveness of all SPSs installed in its Region to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). | M2. The Regional Reliability Organization shall provide either a summary report or a detailed report of this assessment to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | No Parts for 2. |  | M2. The Regional Reliability Organization shall provide either a summary report or a detailed report of this assessment to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-014 | PRC-014-0 | 3. | The documentation of the Regional Reliability Organization’s SPS assessment shall include the following elements: | M3. The Regional Reliability Organization’s documentation of the SPS assessment shall include all elements as defined in Reliability Standard PRC-014-0_R3. | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | 3.1. | Identification of group conducting the assessment and the date the assessment was performed. | M3. The Regional Reliability Organization’s documentation of the SPS assessment shall include all elements as defined in Reliability Standard PRC-014-0_R3. | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | 3.2. | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. | M3. The Regional Reliability Organization’s documentation of the SPS assessment shall include all elements as defined in Reliability Standard PRC-014-0_R3. | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | 3.3. | Identification of SPSs that were found not to comply with NERC standards and Regional Reliability Organization criteria. | M3. The Regional Reliability Organization’s documentation of the SPS assessment shall include all elements as defined in Reliability Standard PRC-014-0_R3. | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | 3.4. | Discussion of any coordination problems found between a SPS and other protection and control systems. | M3. The Regional Reliability Organization’s documentation of the SPS assessment shall include all elements as defined in Reliability Standard PRC-014-0_R3. | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-0 | 3.5. | Provide corrective action plans for non-compliant SPSs. | M3. The Regional Reliability Organization’s documentation of the SPS assessment shall include all elements as defined in Reliability Standard PRC-014-0_R3. | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | 1. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all RAS installed in its Region at least once every five years for compliance with NERC Reliability Standards and Regional criteria. | M1. The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all RAS installed in its Region at least once every five years for compliance with NERC standards and Regional criteria. | Operations Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | No Parts for 1. |  | M1. The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all RAS installed in its Region at least once every five years for compliance with NERC standards and Regional criteria. | Operations Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-014 | PRC-014-1 | 2. | The Regional Reliability Organization shall provide either a summary report or a detailed report of its assessment of the operation, coordination, and effectiveness of all RAS installed in its Region to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). | The Regional Reliability Organization shall provide either a summary report or a detailed report of this assessment to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). | Operations Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | No Parts for 2. |  | The Regional Reliability Organization shall provide either a summary report or a detailed report of this assessment to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). | Operations Planning | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-014 | PRC-014-1 | 3. | The documentation of the Regional Reliability Organization’s RAS assessment shall include the following elements: | M3. The Regional Reliability Organization’s documentation of the RAS assessment shall include all elements as defined in Reliability Standard PRC-014-1_R3. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | 3.1. | Identification of group conducting the assessment and the date the assessment was performed. | M3. The Regional Reliability Organization’s documentation of the RAS assessment shall include all elements as defined in Reliability Standard PRC-014-1_R3. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | 3.2. | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. | M3. The Regional Reliability Organization’s documentation of the RAS assessment shall include all elements as defined in Reliability Standard PRC-014-1_R3. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | 3.3. | Identification of RAS that were found not to comply with NERC standards and Regional Reliability Organization criteria. | M3. The Regional Reliability Organization’s documentation of the RAS assessment shall include all elements as defined in Reliability Standard PRC-014-1_R3. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | 3.4. | Discussion of any coordination problems found between a RAS and other protection and control systems. | M3. The Regional Reliability Organization’s documentation of the RAS assessment shall include all elements as defined in Reliability Standard PRC-014-1_R3. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-014 | PRC-014-1 | 3.5. | Provide corrective action plans for non-compliant RAS. | M3. The Regional Reliability Organization’s documentation of the RAS assessment shall include all elements as defined in Reliability Standard PRC-014-1_R3. |  | 2014-11-13 | 2015-02-03 | [7 empty] | 2020-12-31 | Filing/Order Docket No. RM15-13-000 | [16 empty] | RRO
Inactive | PRC | PRC-015 | PRC-015-0 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R1. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it maintains a list of and provides data for existing and proposed SPSs as defined in Reliability Standard PRC-013-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-015 | PRC-015-0 | No Parts for 1. |  | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it maintains a list of and provides data for existing and proposed SPSs as defined in Reliability Standard PRC-013-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-015 | PRC-015-0 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-015 | PRC-015-0 | No Parts for 2. |  | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-015 | PRC-015-0 | 3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of Studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | M3. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it provided documentation of SPS data and the results of studies that show compliance of new or functionally modified SPSs with NERC standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-015 | PRC-015-0 | No Parts for 3. |  | M3. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it provided documentation of SPS data and the results of studies that show compliance of new or functionally modified SPSs with NERC standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-015 | PRC-015-1 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall maintain a list of and provide data for existing and proposed RAS as specified in Reliability Standard PRC-013-1 R1. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it maintains a list of and provides data for existing and proposed RAS as defined in Reliability Standard PRC-013-1_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-015 | PRC-015-1 | No Parts for 1. |  | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it maintains a list of and provides data for existing and proposed RAS as defined in Reliability Standard PRC-013-1_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-015 | PRC-015-1 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it reviewed new or functionally modified RAS in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-1_R1 prior to being placed in service. | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it reviewed new or functionally modified RAS in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-1_R1 prior to being placed in service. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-015 | PRC-015-1 | No Parts for 2. |  | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it reviewed new or functionally modified RAS in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-1_R1 prior to being placed in service. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-015 | PRC-015-1 | 3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of RAS data and the results of Studies that show compliance of new or functionally modified RAS with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | M3. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of RAS data and the results of studies that show compliance of new or functionally modified RAS with NERC standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-015 | PRC-015-1 | No Parts for 3. |  | M3. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of RAS data and the results of studies that show compliance of new or functionally modified RAS with NERC standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-016 | PRC-016-0 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-016 | PRC-016-0 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-016 | PRC-016-0 | 3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-016 | PRC-016-0.1 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it analyzed SPS operations and maintained a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-0.1 | No Parts for 1. |  | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it analyzed SPS operations and maintained a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | PRC | PRC-016 | PRC-016-0.1 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it took corrective actions to avoid future misoperations. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-0.1 | No Parts for 2. |  | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it took corrective actions to avoid future misoperations. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | PRC | PRC-016 | PRC-016-0.1 | 3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it provided documentation of the misoperation analyses and the corrective action plans to the affected Regional Reliability Organization and NERC on request (within 90 calendar days). |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-0.1 | No Parts for 3. |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it provided documentation of the misoperation analyses and the corrective action plans to the affected Regional Reliability Organization and NERC on request (within 90 calendar days). |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | PRC | PRC-016 | PRC-016-1 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall analyze its RAS operations and maintain a record of all misoperations in accordance with the Regional RAS review procedure specified in Reliability Standard PRC-012-1_R1. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it analyzed RAS operations and maintained a record of all misoperations in accordance with the Regional RAS review procedure specified in Reliability Standard PRC-012-1_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-1 | No Parts for 1. |  | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it analyzed RAS operations and maintained a record of all misoperations in accordance with the Regional RAS review procedure specified in Reliability Standard PRC-012-1_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-016 | PRC-016-1 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall take corrective actions to avoid future misoperations. | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it took corrective actions to avoid future misoperations. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-1 | No Parts for 2. |  | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it took corrective actions to avoid future misoperations. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-016 | PRC-016-1 | 3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of the misoperation analyses and the corrective action plans to the affected Regional Reliability Organization and NERC on request (within 90 calendar days). | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-016 | PRC-016-1 | No Parts for 3. |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of the misoperation analyses and the corrective action plans to the affected Regional Reliability Organization and NERC on request (within 90 calendar days). | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2020-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-017 | PRC-017-0 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.1. | SPS identification shall include but is not limited to: | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.1.1. | Relays. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.1.2. | Instrument transformers. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.1.3. | Communications systems, where appropriate. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.1.4. | Batteries. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.2. | Documentation of maintenance and testing intervals and their basis. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.3. | Summary of testing procedure. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.4. | Schedule for system testing. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.5. | Schedule for system maintenance. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 1.6. | Date last tested/maintained. | M1. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-0_R1. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it provided documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-017 | PRC-017-0 | No Parts for 2. |  | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it provided documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.1. | RAS identification shall include but is not limited to: | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.1.1. | Relays. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.1.2. | Instrument transformers. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.1.3. | Summary of testing procedure. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.1.4. | Batteries. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.2. | Documentation of maintenance and testing intervals and their basis. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.3. | Summary of testing procedure. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.4. | Schedule for system testing. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.5. | Schedule for system maintenance. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 1.6. | Date last tested/maintained. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | Real-Time Operations | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | 2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | GO-2 | [13 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017 | PRC-017-1 | No Parts for 2. |  | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2027-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-018 | PRC-018-1 | 1. | Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: | M1. The Transmission Owner and Generator Owner shall each have evidence that DMEs it is required to have meet the functional requirements specified in Requirement 1 and are installed in accordance with its associated Regional Reliability Organization’s requirements (R2). |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 1.1. | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) | M1. The Transmission Owner and Generator Owner shall each have evidence that DMEs it is required to have meet the functional requirements specified in Requirement 1 and are installed in accordance with its associated Regional Reliability Organization’s requirements (R2). |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 1.2. | Recorded data from each Disturbance shall be retrievable for ten calendar days.. | M1. The Transmission Owner and Generator Owner shall each have evidence that DMEs it is required to have meet the functional requirements specified in Requirement 1 and are installed in accordance with its associated Regional Reliability Organization’s requirements (R2). |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 2. | The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | M2. The Transmission Owner and Generator Owner shall each maintain the data listed in Requirements 3.1 through 3.8 for the DMEs installed to meet its Regional Reliability Organization’s DME installation requirements. M2.1 The Transmission Owner and Generator Owner shall each have evidence it provided this DME data to its Regional Reliability Organization within 30 calendar days of a request. |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | No Parts for 2. |  | M2. The Transmission Owner and Generator Owner shall each maintain the data listed in Requirements 3.1 through 3.8 for the DMEs installed to meet its Regional Reliability Organization’s DME installation requirements. M2.1 The Transmission Owner and Generator Owner shall each have evidence it provided this DME data to its Regional Reliability Organization within 30 calendar days of a request. |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | PRC | PRC-018 | PRC-018-1 | 3. | The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.1. | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.1. DO NOT USE | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.2. | Make and model of equipment. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.3. | Installation location. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.4. | Operational status. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.5. | Date last tested. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.6. | Monitored elements, such as transmission circuit, bus section, etc. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.7. | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 3.8. | Monitored electrical quantities, such as voltage, current, etc. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 4. | The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | M4. Each Transmission Owner and Generator Owner that is required to install DMEs to meet its Regional Reliability Organization’s DME installation requirements, shall have an associated DME maintenance and testing program as defined in Requirement 6. |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | No Parts for 4. |  | M4. Each Transmission Owner and Generator Owner that is required to install DMEs to meet its Regional Reliability Organization’s DME installation requirements, shall have an associated DME maintenance and testing program as defined in Requirement 6. |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | PRC | PRC-018 | PRC-018-1 | 5. | The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | No Parts for 5. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | PRC | PRC-018 | PRC-018-1 | 6. | Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 6.1. | Maintenance and testing intervals and their basis. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-018 | PRC-018-1 | 6.2. | Summary of maintenance and testing procedures. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2022-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-019 | PRC-019-1 | 1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. The standard will become inactive 6/30/16. |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-019 | PRC-019-1 | 1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2014-05-27 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. The standard will become inactive 6/30/16. |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-019 | PRC-019-1 | 1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. The standard will become inactive 6/30/16. |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-019 | PRC-019-1 | 1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2016-07-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. The standard will become inactive 6/30/16. |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-019 | PRC-019-1 | 2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | M2. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence of the coordination required by the events listed in Requirement R2. This evidence should include dated documentation that demonstrates the specified intervals in Requirement R2 have been met. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. The standard will become inactive 6/30/16. |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-019 | PRC-019-1 | No Parts for 2. |  | M2. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence of the coordination required by the events listed in Requirement R2. This evidence should include dated documentation that demonstrates the specified intervals in Requirement R2 have been met. | Long-Term Planning | 2013-02-07 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 Please see the Implementation Plan for specific compliance dates and timeframes. The standard will become inactive 6/30/16.
Mandatory Subject to Enforcement | PRC | PRC-019 | PRC-019-2 | 1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. (Footnote: Limiters or protection functions that are installed and activated on the generator or synchronous condenser.) | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD15-3-000 Please see the Implementation Plan for Version 1 for specific compliance dates and timeframes. |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019 | PRC-019-2 | 1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RD15-3-000 Please see the Implementation Plan for Version 1 for specific compliance dates and timeframes. |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019 | PRC-019-2 | 1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RD15-3-000 Please see the Implementation Plan for Version 1 for specific compliance dates and timeframes. |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019 | PRC-019-2 | 1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | 2016-07-01 |  |  |  |  | Filing/Order Docket No. RD15-3-000 Please see the Implementation Plan for Version 1 for specific compliance dates and timeframes. |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019 | PRC-019-2 | 2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | Each Generator Owner and Transmission Owner with applicable Facilities will have evidence of the coordination required by the events listed in Requirement R2. This evidence should include dated documentation that demonstrates the specified intervals in Requirement R2 have been met. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD15-3-000 Please see the Implementation Plan for Version 1 for specific compliance dates and timeframes. |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019 | PRC-019-2 | No Parts for 2. |  | Each Generator Owner and Transmission Owner with applicable Facilities will have evidence of the coordination required by the events listed in Requirement R2. This evidence should include dated documentation that demonstrates the specified intervals in Requirement R2 have been met. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RD15-3-000 Please see the Implementation Plan for Version 1 for specific compliance dates and timeframes.
Inactive | PRC | PRC-020 | PRC-020-1 | 1. | The Regional Reliability Organization shall establish, maintain and annually update a database for UVLS programs implemented by entities within the region to mitigate the risk of voltage collapse or voltage instability in the BES. This database shall include the following items: | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 1.1. | Owner and operator of the UVLS program. | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 1.2. | Size and location of customer load, or percent of connected load, to be interrupted. | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 1.3. | Corresponding voltage set points and overall scheme clearing times. | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 1.4. | Time delay from initiation to trip signal. | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 1.5. | Breaker operating times. | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 1.6. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | M1. The Regional Reliability Organization shall have evidence that it established and annually updated its UVLS database to include all elements in Requirement 1.1 through 1.6. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | 2. | The Regional Reliability Organization shall provide the information in its UVLS database to the Planning Authority, the Transmission Planner, or other Regional Reliability Organizations and to NERC within 30 calendar days of a request. | M2. The Regional Reliability Organization shall have evidence that it provided the information in its UVLS database to the requesting entities and to NERC in accordance with Requirement 2. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | PRC | PRC-020 | PRC-020-1 | No Parts for 2. |  | M2. The Regional Reliability Organization shall have evidence that it provided the information in its UVLS database to the requesting entities and to NERC in accordance with Requirement 2. |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-020 | PRC-020-2 | 1. | The Regional Reliability Organization shall establish, maintain and annually update a database for UVLS programs implemented by entities within the region to mitigate the risk of voltage collapse or voltage instability in the BES. This database shall include the following items: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 1.1. | Owner and operator of the UVLS program. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 1.2. | Size and location of customer load, or percent of connected load, to be interrupted. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 1.3. | Corresponding voltage set points and overall scheme clearing times. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 1.4. | Time delay from initiation to trip signal |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 1.5. | Breaker operating times. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 1.6. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | 2. | The Regional Reliability Organization shall provide the information in its UVLS database to the Planning Authority, the Transmission Planner, or other Regional Reliability Organizations and to NERC within 30 calendar days of a request. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-020 | PRC-020-2 | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-021 | PRC-021-1 | 1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | M1. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have documentation that its UVLS data was updated annually and includes all items specified in Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | 1.1. | Size and location of customer load, or percent of connected load, to be interrupted. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have documentation that its UVLS data was updated annually and includes all items specified in Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | 1.2. | Corresponding voltage set points and overall scheme clearing times. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have documentation that its UVLS data was updated annually and includes all items specified in Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | 1.3. | Time delay from initiation to trip signal. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have documentation that its UVLS data was updated annually and includes all items specified in Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | 1.4. | Breaker operating times. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have documentation that its UVLS data was updated annually and includes all items specified in Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | 1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | M1. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have documentation that its UVLS data was updated annually and includes all items specified in Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | 2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | M2. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have evidence it provided the Regional Reliability Organization with its UVLS program data within 30 calendar days of a request. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-1 | No Parts for 2. |  | M2. Each Transmission Owner and Distribution Provider that owns a UVLS program shall have evidence it provided the Regional Reliability Organization with its UVLS program data within 30 calendar days of a request. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-021 | PRC-021-2 | 1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-2 | 1.1. | Size and location of customer load, or percent of connected load, to be interrupted. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-021 | PRC-021-2 | 1.2. | Corresponding voltage set points and overall scheme clearing times. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-021 | PRC-021-2 | 1.3. | Time delay from initiation to trip signal. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-2 | 1.4. | Breaker operating times. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-021 | PRC-021-2 | 1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-021 | PRC-021-2 | 2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. |  | DP | [17 empty] | TO
Inactive | PRC | PRC-021 | PRC-021-2 | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | PRC | PRC-022 | PRC-022-1 | 1. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include: | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have documentation of its analysis of UVLS operations and Misoperations in accordance with Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | 1.1. | A description of the event including initiating conditions. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have documentation of its analysis of UVLS operations and Misoperations in accordance with Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | 1.2. | A review of the UVLS set points and tripping times. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have documentation of its analysis of UVLS operations and Misoperations in accordance with Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | 1.3. | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have documentation of its analysis of UVLS operations and Misoperations in accordance with Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | 1.4. | A summary of the findings. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have documentation of its analysis of UVLS operations and Misoperations in accordance with Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | 1.5. | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have documentation of its analysis of UVLS operations and Misoperations in accordance with Requirement 1.1 through 1.5. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | 2. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall provide documentation of its analysis of UVLS program performance to its Regional Reliability Organization within 90 calendar days of a request. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have evidence that it provided documentation of its analysis of UVLS program performance within 90 calendar days of a request by the Regional Reliability Organization. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022 | PRC-022-1 | No Parts for 2. |  | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall have evidence that it provided documentation of its analysis of UVLS program performance within 90 calendar days of a request by the Regional Reliability Organization. |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | PRC | PRC-023 | PRC-023-1 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (R1.1 through R1.13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees: |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 |  |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.1. | Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.10. | Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that they do not operate at or below the greater of: - 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. - 115% of the highest operator established emergency transformer rating. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.11. | For transformer overload protection relays that do not comply with R1.10 set the relays according to one of the following: - Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater. The protection must allow this overload for at least 15 minutes to allow for the operator to take controlled action to relieve the overload. - Install supervision for the relays using either a top oil or simulated winding hot spot temperature element. The setting should be no less than 100° C for the top oil or 140° C for the winding hot spot temperature . |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.12. | When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.12.1. | Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.12.2. | Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.12.3. | Include a relay setting component of 87% of the current calculated in R1.12.2 in the Facility Rating determination for the circuit. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.13. | Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.2. | Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating2 of a circuit (expressed in amperes). |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.3. | Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.3.1. | An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.3.2. | An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.4. | Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: - 115% of the highest emergency rating of the series capacitor. - 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with R1.3, using the full line inductive reactance. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.5. | Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.6. | Set transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capability. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.7. | Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.8. | Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 1.9. | Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 | 2010-07-01 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | 2. | The Transmission Owner, Generator Owner, or Distribution Provider that uses a circuit capability with the practical limitations described in R1.6, R1.7, R1.8, R1.9, R1.12, or R1.13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. |  |  | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 |  |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-1 | No Parts for 2. |  |  |  | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2010-07-01 |  |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000
Inactive | PRC | PRC-023 | PRC-023-1 | 3. | The Planning Coordinator shall determine which of the facilities (transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV) in its Planning Coordinator Area are critical to the reliability of the Bulk Electric System to identify the facilities from 100 kV to 200 kV that must meet Requirement 1 to prevent potential cascade tripping that may occur when protective relay settings limit transmission loadability. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2011-11-17 |  |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-1 | 3.1. | The Planning Coordinator shall have a process to determine the facilities that are critical to the reliability of the Bulk Electric System. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2011-11-17 | 2011-11-17 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-1 | 3.1.1. | This process shall consider input from adjoining Planning Coordinators and affected Reliability Coordinators. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2011-11-17 | 2011-11-17 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-1 | 3.2. | The Planning Coordinator shall maintain a current list of facilities determined according to the process described in R3.1. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2011-11-17 | 2011-11-17 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-1 | 3.3. | The Planning Coordinator shall provide a list of facilities to its Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within 30 days of the establishment of the initial list and within 30 days of any changes to the list. |  | Long-Term Planning | 2008-02-12 | 2008-07-30 | 2010-03-18 | 2010-05-17 | 2011-11-17 | 2011-11-17 |  |  |  | 2012-06-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-2 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating of a circuit (expressed in amperes). 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: • An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. • An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: • 115% of the highest emergency rating of the series capacitor. • 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Set transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capability. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: • 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. • 115% of the highest operator established emergency transformer rating 10.1 Set load responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability . 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. • Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature . 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2012-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-2 | No Parts for 1. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2012-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000
Inactive | PRC | PRC-023 | PRC-023-2 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2012-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-2 | No Parts for 2. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2012-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000
Inactive | PRC | PRC-023 | PRC-023-2 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2012-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-2 | No Parts for 3. |  | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2012-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000
Inactive | PRC | PRC-023 | PRC-023-2 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. |  |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2013-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-2 | No Parts for 4. |  |  |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2013-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000
Inactive | PRC | PRC-023 | PRC-023-2 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. |  |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2013-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-2 | No Parts for 5. |  |  |  | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2013-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000
Inactive | PRC | PRC-023 | PRC-023-2 | 6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: |  | Long-Term Planning | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-2 | 6.1. | Maintain a list of circuits subject to PRC-023-2 per application of Attachment B, including identification of the first calendar year in which any criterion in Attachment B applies. |  | Long-Term Planning | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2014-01-01 | 2014-01-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-2 | 6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | Long-Term Planning | 2011-03-10 | 2011-03-18 | 2012-03-15 | 2012-05-07 | 2014-01-01 | 2014-01-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-13-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-3 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. Criteria:1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes).2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating of a circuit (expressed in amperes).3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation:• An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line.• An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance.4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of:• 115% of the highest emergency rating of the series capacitor.• 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance.5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes).6. Not used.7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration.8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration.9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration.10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of:• 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment.• 115% of the highest operator established emergency transformer rating.10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability .11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload.• Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature .12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints:a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer.b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees.c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit.13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-3 | No Parts for 1. |  | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000
Inactive | PRC | PRC-023 | PRC-023-3 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-3 | No Parts for 2. |  | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000
Inactive | PRC | PRC-023 | PRC-023-3 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-3 | No Parts for 3. |  | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000
Inactive | PRC | PRC-023 | PRC-023-3 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-3 | No Parts for 4. |  | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000
Inactive | PRC | PRC-023 | PRC-023-3 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | M5. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-3 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000
Inactive | PRC | PRC-023 | PRC-023-3 | 6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-3, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-3, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-3 | 6.1. | Maintain a list of circuits subject to PRC-023-3 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-3, Attachment B applies. | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-3, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 | 2014-09-22 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-3 | 6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-3, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2013-11-07 | 2013-12-17 | 2014-07-17 | 2014-09-22 | 2014-10-01 | 2014-09-22 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM14-3-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-4 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. Criteria: 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating of a circuit (expressed in amperes). 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: • An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. • An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: • 115% of the highest emergency rating of the series capacitor. • 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Not used. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: • 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. • 115% of the highest operator established emergency transformer rating. 10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability . 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. • Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature . 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. (Footnote: When a 15-minute rating has been calculated and published for use in real-time operations, the 15-minute rating can be used to establish the loadability requirement for the protective relays. As illustrated by the “dotted line” in IEEE C57.109-1993 - IEEE Guide for Liquid-Immersed Transformer Through-Fault-Current Duration, Clause 4.4, Figure 4. IEEE standard C57.91, Tables 7 and 8, specify that transformers are to be designed to withstand a winding hot spot temperature of 180 degrees C, and Annex A cautions that bubble formation may occur above 140 degrees C. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | No Parts for 1. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-023 | PRC-023-4 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | No Parts for 2. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-023 | PRC-023-4 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | No Parts for 3. |  | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-023 | PRC-023-4 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | No Parts for 4. |  | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-023 | PRC-023-4 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | No Parts for 5. |  | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | PRC | PRC-023 | PRC-023-4 | 6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [5 empty] | PA | PC |  | RC | [5 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | 6.1. | Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [5 empty] | PA | PC |  | RC | [5 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-4 | 6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 |  | DP |  |  | GO | [5 empty] | PA | PC |  | RC | [5 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. Criteria: 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating1 of a circuit (expressed in amperes). Note: When a 15-minute rating has been calculated and published for use in real-time operations, the 15-minute rating can be used to establish the loadability requirement for the protective relays. 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: · An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. · An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: · 115% of the highest emergency rating of the series capacitor. · 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Not used. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: · 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. · 115% of the highest operator established emergency transformer rating. 10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability. 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: · Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. · Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature3. 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. Note: As illustrated by the “dotted line” in IEEE C57.109-1993 - IEEE Guide for Liquid-Immersed Transformer Through-Fault-Current Duration, Clause 4.4, Figure 4. IEEE standard C57.91, Tables 7 and 8, specify that transformers are to be designed to withstand a winding hot spot temperature of 180 degrees C, and Annex A cautions that bubble formation may occur above 140 degrees C. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | No Parts for 1. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-023 | PRC-023-5 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | No Parts for 2. |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-023 | PRC-023-5 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | No Parts for 3. |  | Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-023 | PRC-023-5 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | No Parts for 4. |  | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-023 | PRC-023-5 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | No Parts for 5. |  | Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000
Inactive | PRC | PRC-023 | PRC-023-5 | 6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-023 | PRC-023-5 | 6.1. | Maintain a list of circuits subject to PRC-023-5 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-5, Attachment B applies. | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-023 | PRC-023-5 | 6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD22-2-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | No Parts for 1. |  | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 2. | Reserved. | N/A |  | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | No Parts for 2. |  | N/A |  | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | No Parts for 3. |  | M3. Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | M4. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | No Parts for 4. |  | M4. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability | M5. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | No Parts for 5. |  | M5. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-6, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-6, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6). | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD23-5-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 6.1. | Maintain a list of circuits subject to PRC-023-6 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023- 6, Attachment B applies. | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-6, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6). | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD23-5-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-023 | PRC-023-6 | 6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-6, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6). | Long-Term Planning | 2023-02-16 | 2023-03-02 | 2024-01-24 | 2024-01-25 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD23-5-000 | [10 empty] | PA | PC
Inactive | PRC | PRC-024 | PRC-024-1 | 1. | Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | M1. Each Generator Owner shall have evidence that generator frequency protective relays have been set in accordance with Requirement R1 such as dated setting sheets, calibration sheets or other documentation. | Long-Term Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-1 | No Parts for 1. |  | M1. Each Generator Owner shall have evidence that generator frequency protective relays have been set in accordance with Requirement R1 such as dated setting sheets, calibration sheets or other documentation. | Long-Term Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000
Inactive | PRC | PRC-024 | PRC-024-1 | 2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | M2. Each Generator Owner shall have evidence that generator voltage protective relays have been set in accordance with Requirement R2 such as dated setting sheets, voltage-time curves, calibration sheets, coordination plots, dynamic simulation studies or other documentation. | Long-Term Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-1 | No Parts for 2. |  | M2. Each Generator Owner shall have evidence that generator voltage protective relays have been set in accordance with Requirement R2 such as dated setting sheets, voltage-time curves, calibration sheets, coordination plots, dynamic simulation studies or other documentation. | Long-Term Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000
Inactive | PRC | PRC-024 | PRC-024-1 | 3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | Long-Term Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-1 | 3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | Long-Term Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 | 2014-05-27 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-1 | 4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. | M4. Each Generator Owner shall have evidence that it communicated applicable generator protective relay trip settings in accordance with Requirement R4, such as dated e-mails, correspondence or other evidence and copies of any requests it has received for that information. | Operations Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-1 | No Parts for 4. |  | M4. Each Generator Owner shall have evidence that it communicated applicable generator protective relay trip settings in accordance with Requirement R4, such as dated e-mails, correspondence or other evidence and copies of any requests it has received for that information. | Operations Planning | 2013-05-09 | 2013-05-30 | 2014-03-20 | 2014-05-27 | 2016-07-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-16-000
Inactive | PRC | PRC-024 | PRC-024-2 | 1. | Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. Footnote: Each Generator Owner is not required to have frequency or voltage protective relaying (including but not limited to frequency and voltage protective functions for discrete relays, volts per hertz relays evaluated at nominal frequency, multi-function protective devices or protective functions within control systems that directly trip or provide tripping signals to the generator based on frequency or voltage inputs) installed or activated on its unit. | Each Generator Owner shall have evidence that generator frequency protective relays have been set in accordance with Requirement R1 such as dated setting sheets, calibration sheets or other documentation. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-2 | No Parts for 1. |  | Each Generator Owner shall have evidence that generator frequency protective relays have been set in accordance with Requirement R1 such as dated setting sheets, calibration sheets or other documentation. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-024 | PRC-024-2 | 2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. (Footnote: Each Generator Owner is not required to have frequency or voltage protective relaying (including but not limited to frequency and voltage protective functions for discrete relays, volts per hertz relays evaluated at nominal frequency, multi-function protective devices or protective functions within control systems that directly trip or provide tripping signals to the generator based on frequency or voltage inputs) installed or activated on its unit. For frequency protective relays associated with dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies to frequency protective relays applied on the individual generating unit of the dispersed power producing resources, as well as frequency protective relays applied on equipment from the individual generating unit of the dispersed power producing resource up to the point of interconnection. For the purposes of this standard, point of interconnection means the transmission (high voltage) side of the generator step-up or collector transformer. For voltage protective relays associated with dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies to voltage protective relays applied on the individual generating unit of the dispersed power producing resources, as well as voltage protective relays applied on equipment from the individual generating unit of the dispersed power producing resource up to the point of interconnection. | Each Generator Owner shall have evidence that generator voltage protective relays have been set in accordance with Requirement R2 such as dated setting sheets, voltage-time curves, calibration sheets, coordination plots, dynamic simulation studies or other documentation. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-2 | No Parts for 2. |  | Each Generator Owner shall have evidence that generator voltage protective relays have been set in accordance with Requirement R2 such as dated setting sheets, voltage-time curves, calibration sheets, coordination plots, dynamic simulation studies or other documentation. | Long-Term Planning | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000
Inactive | PRC | PRC-024 | PRC-024-2 | 3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. (Footnote: Excludes limitations that are caused by the setting capability of the generator frequency and voltage protective relays themselves but does not exclude limitations originating in the equipment that they protect.) | Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. Each Generator Owner shall have evidence that it communicated applicable generator protective relay trip settings in accordance with Requirement R4, such as dated e-mails, correspondence or other evidence and copies of any requests it has received for that information. | Long-Term Planning, Real-Time Operations | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-2 | 3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. Each Generator Owner shall have evidence that it communicated applicable generator protective relay trip settings in accordance with Requirement R4, such as dated e-mails, correspondence or other evidence and copies of any requests it has received for that information. | Long-Term Planning, Real-Time Operations | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 | 2016-07-01 |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-2 | 4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. |  | Operations Planning, Real-Time Operations | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | PRC | PRC-024 | PRC-024-2 | No Parts for 4. |  |  | Operations Planning, Real-Time Operations | 2015-02-12 | 2015-03-13 | 2015-05-29 | 2015-05-29 | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2022-09-30 | Filing/Order Docket No. RD15-3-000
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | D.A.2. | Each Generator Owner and Transmission Owner shall set its applicable voltage protection5 in accordance with PRC-024 Attachment 2a, such that the applicable protection does not cause the generating resource to trip or cease injecting current during a voltage excursion within the “no trip zone” at the high side of the GSU or MPT, subject to the following exceptions: • For newly designated strategic power plants, applicable protections must comply with the high voltage durations for such plants within 48 calendar months of the notification made pursuant to Requirement D.A.5. During this transition period, voltage protections must at least comply with the high voltage durations for “all power plants”. • The generating resource(s) are permitted to be set to trip or to cease injecting current during a voltage excursion bounded by the “no trip zone” of PRC-024 Attachment 2a for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024 Attachment 2a, then the Generator Owner or Transmission Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Inverter-based resources voltage protection settings may be set to cease injecting current momentarily during a voltage excursion at the high side of the MPT, bounded by the “no trip zone” of PRC-024 Attachment 2a, under the following conditions: o After a minimum delay of 0.022 s, when the positive-sequence voltage exceeds 1.25 per unit (p.u.) Normal operation must resume once the voltage drops back below 1.25 p.u at the high side of the MPT. o After a minimum delay of 0.022 s, when the phase-to-ground root mean square (RMS) voltages exceeds 1.4 p.u., as measured at generator terminals, on one or multiple phases. Normal operation must resume once the positive-sequence voltage drops back below the 1.25 p.u. at the high side of the MPT. | M.D.A.2. Each Generator Owner and Transmission Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | No Parts for D.A.2. |  | M.D.A.2. Each Generator Owner and Transmission Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | D.A.5. | Each Planning Coordinator shall designate, at least once every five calendar years, the strategic power plants that must comply with Attachment 2a and notify, within 30 calendar days of its designation, each Generator Owner or Transmission Owner that owns facilities in the strategic power plants. | M.D.A.5 Each Planning Coordinator shall have evidence that it designated, at least once every five calendar years, strategic power plants in accordance with Requirement D.A.5, Part 5 and shall have dated evidence that each Generator Owner or Transmission Owner has been notified in accordance with Requirement D.A.5, part 5.2. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | No Parts for D.A.5. |  | M.D.A.5 Each Planning Coordinator shall have evidence that it designated, at least once every five calendar years, strategic power plants in accordance with Requirement D.A.5, Part 5 and shall have dated evidence that each Generator Owner or Transmission Owner has been notified in accordance with Requirement D.A.5, part 5.2. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | 1. | Each Generator Owner shall set its applicable frequency protection in accordance with PRC-024 Attachment 1 such that the applicable protection does not cause the generating resource to trip or cease injecting current within the “no trip zone” during a frequency excursion with the following exceptions: • Applicable frequency protection may be set to trip or cease injecting current within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | M1. Each Generator Owner shall have evidence that the applicable frequency protection has been set in accordance with Requirement R1, such as dated setting sheets, calibration sheets, calculations, or other documentation. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | No Parts for 1. |  | M1. Each Generator Owner shall have evidence that the applicable frequency protection has been set in accordance with Requirement R1, such as dated setting sheets, calibration sheets, calculations, or other documentation. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | 2. | Each Generator Owner shall set its applicable voltage protection5 in accordance with PRC-024 Attachment 2, such that the applicable protection does not cause the generating resource to trip or cease injecting current within the “no trip zone” during a voltage excursion at the high side of the GSU or MPT, subject to the following exceptions: • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024 Attachment 2, then the Generator Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Applicable voltage protection may be set to trip or cease injecting current during a voltage excursion within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | M2. Each Generator Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | No Parts for 2. |  | M2. Each Generator Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | 3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating resource(s) with frequency or voltage protection from meeting the protection setting criteria in Requirements R1 or R2, including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3, such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | 3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3, such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 | 2022-10-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | 4. | Each Generator Owner shall provide its applicable protection settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated generating resource(s) within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of protection setting changes is not required. |  |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-024 | PRC-024-3 | No Parts for 4. |  |  |  | 2020-02-06 | 2020-03-20 | 2020-07-09 | 2020-07-09 | 2022-10-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD20-7-000
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | D.A.2. | Each Generator Owner and Transmission Owner shall set applicable voltage protection [7] in accordance with PRC-024 Attachment 2A, such that the applicable protection does not cause the Facility to which it is applied to trip within the “no trip zone” during a voltage excursion at the high-side of the GSU or MPT, subject to the following exceptions: • For newly designated strategic power plants, applicable protections must comply with the high voltage durations for such plants within 48 calendar months of the notification made pursuant to Requirement D.A.5. During this transition period, voltage protections must at least comply with the high voltage durations for “all power plants”. • Applicable voltage protection may be set to trip during a voltage excursion within a portion of the “no trip zone” of PRC-024 Attachment 2A for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024 Attachment 2A, then the Generator Owner or Transmission Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. [7] Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the synchronous generator(s), type 1 or type 2 wind resource(s), or synchronous condenser(s); or (ii) provide signals to trip the same Facilities. | M.D.A.2. Each Generator Owner and Transmission Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO | [14 empty] | TO
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | No Parts for D.A.2. |  | M.D.A.2. Each Generator Owner and Transmission Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | D.A.5. | Each Planning Coordinator shall designate, at least once every five calendar years, the strategic power plants that must comply with Attachment 2A and notify, within 30 calendar days of its designation, each Generator Owner or Transmission Owner that owns facilities [8] in the strategic power plants. [8] Facilities in the strategic power plants include facilities with synchronous generator(s) from the generator up to and including the MPT or GSU. | M.D.A.5. Each Planning Coordinator shall have evidence that it designated, at least once every five calendar years, strategic power plants in accordance with Requirement D.A.5, Part 5 and shall have dated evidence that each Generator Owner or Transmission Owner has been notified in accordance with Requirement D.A.5, part 5.2. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates | [10 empty] | PA | PC
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | No Parts for D.A.5. |  | M.D.A.5. Each Planning Coordinator shall have evidence that it designated, at least once every five calendar years, strategic power plants in accordance with Requirement D.A.5, Part 5 and shall have dated evidence that each Generator Owner or Transmission Owner has been notified in accordance with Requirement D.A.5, part 5.2. Evidence may include, but is not limited to letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | 1. | Each Generator Owner and Transmission Owner shall set applicable frequency protection [4] in accordance with PRC-024-4 Attachment 1 such that the applicable protection does not cause the Facility to which it is applied to trip within the “no trip zone” during a frequency excursion with the following exceptions: • Applicable frequency protection may be set to trip within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. [4] Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the synchronous generator(s), type 1 or type 2 wind resource(s), or synchronous condenser(s); or (ii) provide signals to trip the same Facilities. | M1. Each Generator Owner and Transmission Owner shall have evidence that the applicable frequency protection has been set in accordance with Requirement R1, such as dated setting sheets, calibration sheets, calculations, or other documentation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO | [14 empty] | TO
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | No Parts for 1. |  | M1. Each Generator Owner and Transmission Owner shall have evidence that the applicable frequency protection has been set in accordance with Requirement R1, such as dated setting sheets, calibration sheets, calculations, or other documentation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | 2. | Each Generator Owner and Transmission Owner shall set applicable voltage protection [5] in accordance with PRC-024-4 Attachment 2, such that the applicable protection does not cause the Facility to which it is applied to trip within the “no trip zone” during a voltage excursion at the high-side of the GSU or MPT, subject to the following exceptions: • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024-4 Attachment 2, then the Generator Owner or Transmission Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Applicable voltage protection may be set to trip during a voltage excursion within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. [5] Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the synchronous generator(s), type 1 or type 2 wind resource(s), or synchronous condenser(s); or (ii) provide signals to trip the same Facilities. | M2. Each Generator Owner and Transmission Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO | [14 empty] | TO
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | No Parts for 2. |  | M2. Each Generator Owner and Transmission Owner shall have evidence that applicable voltage protection has been set in accordance with Requirement R2, such as dated setting sheets, voltage-time boundaries, calibration sheets, coordination plots, dynamic simulation studies, calculations, or other documentation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | 3. | Each Generator Owner and Transmission Owner shall document each known regulatory or equipment limitation [6] that prevents its Facility, with applicable frequency or voltage protection from meeting the protection setting criteria in Requirements R1 or R2, including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [6] Excludes limitations caused by the setting capability of the frequency, voltage, and volts per hertz protective relays applied to the synchronous generator(s), type 1 and type 2 wind resource(s), and synchronous condenser(s). This does not exclude limitations originating in the equipment protected by the relay(s). | M3. Each Generator Owner and Transmission Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3, such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO | [14 empty] | TO
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | 3.1. | The Generator Owner and Transmission Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | M3. Each Generator Owner and Transmission Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3, such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 |  |  |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO | [14 empty] | TO
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | 4. | Each Generator Owner and Transmission Owner shall provide its applicable protection settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated Facility within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of protection setting changes is not required. | M4. Each Generator Owner and Transmission Owner shall have evidence that it communicated applicable protection settings in accordance with Requirement R4, such as dated emails, correspondence or other evidence and copies of any requests it has received for that information. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO | [14 empty] | TO
Subject to Future Enforcement | PRC | PRC-024 | PRC-024-4 | No Parts for 4. |  | M4. Each Generator Owner and Transmission Owner shall have evidence that it communicated applicable protection settings in accordance with Requirement R4, such as dated emails, correspondence or other evidence and copies of any requests it has received for that information. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | [5 empty] | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Inactive | PRC | PRC-025 | PRC-025-1 | 1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | M1. For each load-responsive protective relay, each Generator Owner, Transmission Owner, and Distribution Provider shall have evidence (e.g., summaries of calculations, spreadsheets, simulation reports, or setting sheets) that settings were applied in accordance with PRC-025-1 – Attachment 1: Relay Settings. | Long-Term Planning | 2013-08-15 | 2013-09-30 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM13-19-000 See Implementation Plan. For applicable relays where the entity has determined replacement or removal is not necessary, the entity shall be compliant by 10/1/2019. For applicable relays |  | DP |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-025 | PRC-025-1 | No Parts for 1. |  | M1. For each load-responsive protective relay, each Generator Owner, Transmission Owner, and Distribution Provider shall have evidence (e.g., summaries of calculations, spreadsheets, simulation reports, or setting sheets) that settings were applied in accordance with PRC-025-1 – Attachment 1: Relay Settings. | Long-Term Planning | 2013-08-15 | 2013-09-30 | 2014-07-17 | 2014-09-22 | 2014-10-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM13-19-000 See Implementation Plan. For applicable relays where the entity has determined replacement or removal is not necessary, the entity shall be compliant by 10/1/2019. For applicable relays
Mandatory Subject to Enforcement | PRC | PRC-025 | PRC-025-2 | 1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-2 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | For each load-responsive protective relay, each Generator Owner, Transmission Owner, and Distribution Provider shall have evidence (e.g., summaries of calculations, spreadsheets, simulation reports, or setting sheets) that settings were applied in accordance with PRC-025-2 – Attachment 1: Relay Settings. | Long-Term Planning | 2018-02-08 | 2018-03-16 | 2018-05-02 | 2018-05-02 | 2018-07-01 |  | X |  |  |  | Filing/Order Docket No. RD18-4-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-025 | PRC-025-2 | No Parts for 1. |  | For each load-responsive protective relay, each Generator Owner, Transmission Owner, and Distribution Provider shall have evidence (e.g., summaries of calculations, spreadsheets, simulation reports, or setting sheets) that settings were applied in accordance with PRC-025-2 – Attachment 1: Relay Settings. | Long-Term Planning | 2018-02-08 | 2018-03-16 | 2018-05-02 | 2018-05-02 | 2018-07-01 |  | X |  |  |  | Filing/Order Docket No. RD18-4-000
Inactive | PRC | PRC-026 | PRC-026-1 | 1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. (Footnote: NERC Reliability Standard FAC-014-2 – Establish and Communicate System Operating Limits, Requirement R3. An example of an unstable power swing is provided in the Guidelines and Technical Basis section, “Justification for Including Unstable Power Swings in the Requirements section of the Guidelines and Technical Basis.”) | Each Planning Coordinator shall have dated evidence that demonstrates notification of the generator, transformer, and transmission line BES Element(s) that meet one or more of the criteria in Requirement R1, if any, to the respective Generator Owner and Transmission Owner. Evidence may include, but is not limited to, the following documentation: emails, facsimiles, records, reports, transmittals, lists, or spreadsheets. | Long-Term Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2018-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000 |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO
Inactive | PRC | PRC-026 | PRC-026-1 | No Parts for 1. |  | Each Planning Coordinator shall have dated evidence that demonstrates notification of the generator, transformer, and transmission line BES Element(s) that meet one or more of the criteria in Requirement R1, if any, to the respective Generator Owner and Transmission Owner. Evidence may include, but is not limited to, the following documentation: emails, facsimiles, records, reports, transmittals, lists, or spreadsheets. | Long-Term Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2018-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000
Inactive | PRC | PRC-026 | PRC-026-1 | 2. | Each Generator Owner and Transmission Owner shall: | M2. Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | Operations Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-026 | PRC-026-1 | 2.1 . | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. | M2. Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | Operations Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 | 2020-01-01 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-026 | PRC-026-1 | 2.2 . | Within 12 full calendar months of becoming aware3 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable4 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | M2. Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | Operations Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 | 2020-01-01 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-026 | PRC-026-1 | 3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | M3. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates the development of a CAP in accordance with Requirement R3. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Operations Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-026 | PRC-026-1 | No Parts for 3. |  | M3. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates the development of a CAP in accordance with Requirement R3. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Operations Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000
Inactive | PRC | PRC-026 | PRC-026-1 | 4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. | M4. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates implementation of each CAP according to Requirement R4, including updates to the CAP when actions or timetables change. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Long-Term Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | PRC | PRC-026 | PRC-026-1 | No Parts for 4. |  | M4. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates implementation of each CAP according to Requirement R4, including updates to the CAP when actions or timetables change. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Long-Term Planning | 2014-12-17 | 2014-12-31 | 2016-03-17 | 2016-05-23 | 2020-01-01 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-8-000
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | 1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: Criteria: 1. Generator(s) where an angular stability constraint, identified in Planning Assessments of the Near-Term Transmission Planning Horizon for a planning event, that is addressed by limiting the output of a generator or a Remedial Action Scheme (RAS), and those Elements terminating at the Transmission station associated with the generator(s). 2. Elements associated with angular instability identified in Planning Assessments of the Near-Term Transmission Planning Horizon for a planning event.. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment of the Near-Term Transmission Planning Horizon where relay tripping occurs due to a stable or unstable1 power swing during a simulated disturbance for a planning event. | M1. Each Planning Coordinator shall have dated evidence that demonstrates notification of the generator, transformer, and transmission line BES Element(s) that meet one or more of the criteria in Requirement R1, if any, to the respective Generator Owner and Transmission Owner. Evidence may include, but is not limited to, the following documentation: emails, facsimiles, records, reports, transmittals, lists, or spreadsheets. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | No Parts for 1. |  | M1. Each Planning Coordinator shall have dated evidence that demonstrates notification of the generator, transformer, and transmission line BES Element(s) that meet one or more of the criteria in Requirement R1, if any, to the respective Generator Owner and Transmission Owner. Evidence may include, but is not limited to, the following documentation: emails, facsimiles, records, reports, transmittals, lists, or spreadsheets. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | 2. | Each Generator Owner and Transmission Owner shall: | M2. Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | 2.1. | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-2 – Attachment B criteria has not been performed in the last five calendar years. | M2. Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 | X |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | 2.2. | Within 12 full calendar months of becoming aware2 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable3 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B. | M2. Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 | X |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | 3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-2 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: · The Protection System meets the PRC-026-2 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out- of-step tripping is applied at the terminal of the BES Element); or · The Protection System is excluded under the PRC-026-2 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | M3. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates the development of a CAP in accordance with Requirement R3. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | No Parts for 3. |  | M3. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates the development of a CAP in accordance with Requirement R3. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | 4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. | M4. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates implementation of each CAP according to Requirement R4, including updates to the CAP when actions or timetables change. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026 | PRC-026-2 | No Parts for 4. |  | M4. The Generator Owner and Transmission Owner shall have dated evidence that demonstrates implementation of each CAP according to Requirement R4, including updates to the CAP when actions or timetables change. Evidence may include, but is not limited to, the following documentation: corrective action plans, maintenance records, settings sheets, project or work management program records, or work orders. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 |  | X |  |  |  | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a process for developing new and revised Protection System settings for BES Elements, such that the Protection Systems operate in the intended sequence during Faults. The process shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.1. | A review and update of short-circuit model data for the BES Elements under study. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.2. | A review of the developed Protection System settings. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.3. | For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.3.1. | Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.3.2. | Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.3.3. | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 1.3.4. | Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall, for each BES Element with Protection System functions identified in Attachment A: • Option 1: Perform a Protection System Coordination Study in a time interval not to exceed six-calendar years; or • Option 2: Compare present Fault current values to an established Fault current baseline and perform a Protection System Coordination Study when the comparison identifies a 15 percent or greater deviation in Fault current values (either three phase or phase to ground) at a bus to which the BES Element is connected, all in a time interval not to exceed six-calendar years; or, • Option 3: Use a combination of the above. | M2. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity performed Protection System Coordination Study(ies) and/or Fault current comparisons in accordance with Requirement R2. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | No Parts for 2. |  | M2. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity performed Protection System Coordination Study(ies) and/or Fault current comparisons in accordance with Requirement R2. | Long-Term Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | 3. | Each Transmission Owner, Generator Owner, and Distribution Provider shall utilize its process established in Requirement R1 to develop new and revised Protection System settings for BES Elements. | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity utilized its settings development process established in Requirement R1, as specified in Requirement R3. | Operations Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000 |  | DP |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027 | PRC-027-1 | No Parts for 3. |  | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity utilized its settings development process established in Requirement R1, as specified in Requirement R3. | Operations Planning | 2015-11-05 | 2016-09-02 | 2018-06-07 | 2018-08-13 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM16-22-000
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1. | Each Generator Owner shall have sequence of event recording (SER) data for the following Elements that it owns: | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.1. | Circuit breaker position (open/close) for circuit breakers associated with the main power transformer(s) [1], collector bus(es), shunt static and dynamic reactive device(s), and AC-DC and DC-AC converters, if any, in case of VSC HVDC system with a dedicated connection to Inverter-Based Resource. [1] For the purpose of this standard, the main power transformer is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for Inverter-Based Resources. In case of dedicated VSC HVDC system connecting to an Inverter-Based Resource, a transformer isolating the DC-AC converter from the transmission system is also considered a main power transformer. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.2. | For IBR units [2] in commercial operation [3] after the effective date of this standard, the following data shall be recorded when triggered by ride-through operation or tripping of an IBR unit. [2] IBR unit includes the inverter, converter, wind turbine generator, or high voltage direct current converter connecting generating resource to alternating current Transmission network. [3] Commercial operation means achievement of this designation indicating that the facility has received all approvals necessary for operation after completion of initial start-up testing. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.2.1. | All fault codes. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.2.2. | All fault alarms. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.2.3. | High and low voltage ride-through mode status. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.2.4. | High and low frequency ride-through mode status. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.3. | For IBR units in commercial operation before the effective date of this standard, if capable, the following data shall be recorded when triggered by ride-through operation or tripping of an IBR unit. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.3.1. | All fault codes. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.3.2. | All fault alarms. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.3.3. | High and low voltage ride-through mode status. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 1.3.4. | High and low frequency ride-through mode status. | M1. The Generator Owner has evidence (electronic or hard copy) of data, as applicable, as specified in Requirement R1. Evidence may include, but is not limited to: (1) actual data recordings; or (2) documents describing the device interconnections and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. The evidence to show IBR unit capability to record fault codes, alarms, or ride-through mode status may include, but is not limited to: (1) equipment specification, (2) letter from equipment manufacturer, or (3) documents describing lack of recording capability. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2. | Each Generator Owner shall have triggered fault recording (FR) data to determine the following electrical quantities for Elements that it owns: | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.1. | High-side of the main power transformer FR data: | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.1.1. | Phase-to-neutral voltage for each phase. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.1.2. | Each phase current and the residual or neutral current. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.1.3. | Real and Reactive Power expressed on a three-phase basis. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.2. | Collector feeder breaker FR data: | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.2.1. | Phase-to-neutral voltage for each phase. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.2.2. | Each phase current and the residual or neutral current. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.2.3. | Real and Reactive Power expressed on a three-phase basis. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.3. | Shunt dynamic reactive device FR data: | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.3.1. | Phase-to-neutral voltage for each phase | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.3.2. | Each phase current and the residual or neutral current. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 2.3.3. | Reactive Power output expressed on a three-phase basis. | M2. The Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R2. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (3) station or equipment drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3. | Each Generator Owner shall have FR data as specified in Requirement R2 that meets the following: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1. | High-side of the main power transformer FR data: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1.1. | A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0seconds for the same trigger point. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1.2. | A minimum recording rate of 64 samples per cycle. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1.3. | Trigger settings for at least the following: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1.3.1. | Neutral (residual) overcurrent. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1.3.2. | AC phase overvoltage and undervoltage. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.1.3.3. | Overfrequency and underfrequency | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2. | Collector feeder breaker FR data: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2.1. | A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2.2. | A minimum recording rate of 64 samples per cycle. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2.3. | Trigger settings for at least the following: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2.3.1. | Neutral (residual) overcurrent, if applicable. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2.3.2. | AC phase overvoltage and undervoltage. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.2.3.3. | Overfrequency and underfrequency. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.3. | Shunt dynamic reactive device FR data: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.3.1. | A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.3.2. | A minimum recording rate of 64 samples per cycle. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.3.3. | Trigger settings for at least the following: | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.3.3.1. | Neutral (residual) overcurrent. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 3.3.3.2. | AC phase overvoltage and undervoltage. | M3. The Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R3. Evidence may include, but is not limited to: (1) actual data recordings or derivations, or (2) documents describing the device specification and device configuration or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 4. | Each Generator Owner shall have continuous dynamic disturbance recording (DDR) data and storage to determine the following electrical quantities for each main power transformer(s) it owns: | M4. The Generator Owner has evidence (electronic or hard copy) of continuous DDR data recording and storage to determine electrical quantities as specified in Requirement R4. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 4.1. | One phase-to-neutral or positive sequence voltage on high-side of the main power transformer(s). | M4. The Generator Owner has evidence (electronic or hard copy) of continuous DDR data recording and storage to determine electrical quantities as specified in Requirement R4. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 4.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R4, Part 4.1, or the positive sequence current. | M4. The Generator Owner has evidence (electronic or hard copy) of continuous DDR data recording and storage to determine electrical quantities as specified in Requirement R4. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 4.3. | Real Power and Reactive Power flows expressed on a three-phase basis corresponding to each main power transformer(s) where current measurements are required. | M4. The Generator Owner has evidence (electronic or hard copy) of continuous DDR data recording and storage to determine electrical quantities as specified in Requirement R4. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 4.4. | Frequency of any one of the voltage(s) in Requirement R4, Part 4.1. | M4. The Generator Owner has evidence (electronic or hard copy) of continuous DDR data recording and storage to determine electrical quantities as specified in Requirement R4. Evidence may include, but is not limited to: (1) actual data recordings or derivations; or (2) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 5. | Each Generator Owner responsible for DDR data for the electrical quantities identified in Requirement R4 shall have DDR data that meet the following: | M5. The Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R5. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R5, Part 5.1; R5, Part 5.2); or (2) actual data recordings (R5, Part 5.2). | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 5.1. | Input sampling rate of at least 960 samples per second. | M5. The Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R5. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R5, Part 5.1; R5, Part 5.2); or (2) actual data recordings (R5, Part 5.2). | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 5.2. | Output recording rate of electrical quantities of at least 60 times per second. | M5. The Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R5. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R5, Part 5.1; R5, Part 5.2); or (2) actual data recordings (R5, Part 5.2). | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 6. | Each Generator Owner shall time synchronize all SER, FR, and DDR data to meet the following: | M6. The Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 6.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | M6. The Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 6.2. | The IBR unit synchronized device clock accuracy within ± 100 milliseconds of UTC. For all other devices, synchronized device clock accuracy within ± 1 milliseconds of UTC. | M6. The Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7. | Each Generator Owner shall provide all requested SER, FR, and DDR data to its Transmission Planner, Planning Coordinator, Transmission Operator, Balancing Authority, Reliability Coordinator, Regional Entity, or NERC in accordance with the following: | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7.1. | Data shall be retrievable for the period of 20 calendar days, inclusive of the day the data was recorded. | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7.2. | Data subject to Part 7.1 shall be provided within 15 calendar days of a request unless an extension is granted by the requestor. | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7.3. | SER data shall be provided in ASCII4 Comma Separated Value (CSV) format following Attachment 1. | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7.4. | FR data shall be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7.5. | DDR data shall be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 7.6. | Data files shall be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | M7. The Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R7. Evidence may include, but is not limited to: (1) actual data recordings; (2) dated transmittals to the requesting entity with formatted records; or (3) documents describing data storage capability, device specification, configuration, or settings. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2025-04-01 | 2025-04-01 | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | 8. | Each Generator Owner shall, upon the discovery of a failure of the recording capability for the SER, FR, or DDR data: • Restore the recording capability within 90 calendar days, or • Submit a Corrective Action Plan (CAP) to the Regional Entity within 90 calendar days and then implement it according to CAP timeline. | M8. The Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R8. Evidence may include, but is not limited to: (1) dated reports of the discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated Corrective Action Plan transmittals to the Regional Entity and evidence of Corrective Action Plan implementation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-01-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | PRC | PRC-028 | PRC-028-1 | No Parts for 8. |  | M8. The Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R8. Evidence may include, but is not limited to: (1) dated reports of the discovery of a failure, (2) documentation noting the date the data recording was restored, (3) SCADA records, or (4) dated Corrective Action Plan transmittals to the Regional Entity and evidence of Corrective Action Plan implementation. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-01-01 |  | X | Compliance Dates BES IBR In Commercial Operation on/before April 1, 2025: R1-R7: 50% of BES IBR by December 31, 2028; 100% by January 1, 2030 BES IBR in Commercial Operation after April 1, 2025: R1-R7: by July 31, 2026 or within 15 calendar months of the commercial operation date, whichever is later. R8: January 1, 2026 Non-BES IBR in Commercial Operation in commercial operation on or before May 15, 2026: R1-R7: January 1, 2030 R8: April 1, 2027 Non-BES IBR in Commercial Operation after May 15, 2026: R1-R7: Within 15 calendar months following April 1, 2025 [July 31, 2026] or the commercial operation date, whichever is later. R8: April 1, 2027 |  |  | Filing/Order Docket No. RD25-2-000
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 1. | Each Generator Owner shall ensure the design and operation is such that each IBR meets or exceeds Ride-through requirements, in accordance with the “must Ride-through[1] zone” as specified in Attachment 1, except in the following conditions: • The IBR needed to electrically disconnect in order to clear a fault; • The voltage at the high-side of the main power transformer[2] went outside an accepted hardware limitation, in accordance with Requirement R4; • The instantaneous positive sequence voltage phase angle change is more than 25 electrical degrees at the high-side of the main power transformer and is initiated by a non-fault switching event on the transmission system[3]; or • The Volts per Hz (V/Hz) at the high-side of the main power transformer exceed 1.1 per unit for longer than 45 seconds or exceed 1.18 per unit for longer than 2 seconds. [1] Includes no tripping associated with phase lock loop loss of synchronism. [2] For the purpose of this standard, the main power transformer is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for IBRs. In case of IBR connecting via a dedicated Voltage Source Converter High Voltage Direct Current (VSC-HVDC), the main power transformer is the main power transformer on the receiving end. [3] Current blocking mode may be used for non-fault initiated phase jumps greater than 25 degrees in order to prevent tripping. | M1. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to Ride-through requirements, as specified in Requirement R1. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) to demonstrate that the operation of each IBR did adhere to Ride-through requirements, as specified in Requirement R1. If the Generator Owner choose to utilize Ride-through exemptions that occur within the “must Ride-through zone” and are caused by non-fault initiated phase jumps of greater than 25 electrical degrees, then each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the IBR failed to Ride-through during a phase jump of greater than or equal to 25 electrical degrees, and documentation from their Transmission Planner, Reliability Coordinator, Planning Coordinator, or Transmission Operator that a non-fault initiated switching event occurred. | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 |  | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | No Parts for 1. |  | M1. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to Ride-through requirements, as specified in Requirement R1. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) to demonstrate that the operation of each IBR did adhere to Ride-through requirements, as specified in Requirement R1. If the Generator Owner choose to utilize Ride-through exemptions that occur within the “must Ride-through zone” and are caused by non-fault initiated phase jumps of greater than 25 electrical degrees, then each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the IBR failed to Ride-through during a phase jump of greater than or equal to 25 electrical degrees, and documentation from their Transmission Planner, Reliability Coordinator, Planning Coordinator, or Transmission Operator that a non-fault initiated switching event occurred. | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 |  | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. | Each Generator Owner shall ensure the design and operation is such that the voltage performance for each IBR adheres to the following during a voltage excursion, unless a documented hardware limitation exists in accordance with Requirement R4. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 |  | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 1. | While the voltage at the high-side of the main power transformer remains within the continuous operation region as specified in Attachment 1, each IBR shall: | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 1.1. | Continue to deliver the pre-disturbance level of Real Power or available Real Power[4], whichever is less.[5] [4] “Available Real Power" refers to changes of facility Real Power output attributed to factors such as weather patterns, change of wind, and change in irradiance, but not changes of facility Real Power attributed to IBR tripping in whole or part. [5] Except if this would occur during a frequency excursion. The Real Power response should recover in accordance with the primary frequency controller. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 1.2. | Continue to deliver Reactive Rower up to its Reactive Power limit and according to its controller settings. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 1.3. | Prioritize Real Power or Reactive Power when the voltage is less than 0.95 per unit, the voltage is within the continuous operating region, and the IBR cannot deliver both Real Power and Reactive Power due to a current limit or Reactive Power limit, unless otherwise specified through other mechanisms by an associated Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 2. | While voltage at the high-side of the main power transformer is within the mandatory operation region as specified in Attachment 1, each IBR shall exchange current, up to the maximum capability to provide voltage support, on the affected phases during both symmetrical and asymmetrical voltage disturbances, either under[6]: • Reactive Power priority by default; or • Real Power priority if required through other mechanisms by an associated Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator [6] In either case and if required, the magnitude of Real Power and reactive current shall be as specified by the Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 3. | While voltage at the high-side of the main power transformer is within the permissive operation region, as specified in Attachment 1, each IBR may operate in current blocking mode if necessary to avoid tripping. Otherwise, each IBR shall follow the requirements for the mandatory operation region in Requirement R2.2. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 3.1. | If an IBR enters current blocking mode, it shall restart current exchange in less than or equal to five cycles of positive sequence voltage returning to a continuous operation region or mandatory operation region. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 4. | Each IBR shall not itself cause voltage at the high-side of the main power transformer to exceed the applicable high voltage thresholds and time durations in its response as voltage recovers from the mandatory or permissive operation regions to the continuous operation region. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 2. 5. | Each IBR shall restore Real Power output to the pre-disturbance or available level [7] (whichever is lesser) within 1.0 second when the voltage at the high-side of the main power transformer returns from the mandatory operation region or permissive operation region (including operating in current blocking mode) to the continuous operation region, as specified in Attachment 1, unless an associated Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator requires a lower post-disturbance Real Power level requirement or requires a different post-disturbance Real Power restoration time through other mechanisms.[8] [7] Except if this would occur during a frequency excursion. The Real Power response should recover in accordance with the primary frequency controller. [8] “Available Real Power" refers to changes of facility Real Power output attributed to factors such as weather patterns, change of wind, and change in irradiance, but not changes of facility Real Power attributed to IBR tripping in whole or part. | M2. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to requirements, as specified in Requirement R2. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate that the operation of each IBR did adhere to performance requirements, as specified in Requirement R2, during each voltage excursion measured at the high-side of the main power transformer. Regarding R2.1.3, R2.2, and R2.5, the Generator Owner shall retain evidence of receiving such performance requirements, (e.g., email exchange, contract information) if the Transmission Planner, Transmission Operator, Reliability Coordinator, or Planning Coordinator has required the Generator Owner through other mechanisms to follow performance requirements other than those in Requirement R2 (e.g., ramp rates, Reactive Power prioritization). | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 3. | Each Generator Owner shall ensure the design and operation is such that each IBR meets or exceeds Ride-through requirements during a frequency excursion event whereby the System frequency remains within the “must Ride-through zone” according to Attachment 2 and the absolute rate of change of frequency (RoCoF)[9] magnitude is less than or equal to 5 Hz/second, unless a documented hardware limitation exists in accordance with Requirement R4. [9] Rate of change of frequency (RoCoF) is calculated as the average rate of change for multiple calculated system frequencies for a time period of greater than or equal to 0.1 second. RoCoF is not calculated during the fault occurrence and clearance. | M3. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to Ride-through requirements, as specified in Requirement R3. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate the operation of each IBR did adhere to Ride‑through requirements, as specified in Requirement R3, during each frequency excursion event measured at the high-side of the main power transformer. | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 |  | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | No Parts for 3. |  | M3. Each Generator Owner shall have evidence to demonstrate the design of each IBR will adhere to Ride-through requirements, as specified in Requirement R3. Examples of evidence may include, but are not limited to dynamic simulations, studies, plant protection settings, and control settings design evaluation. Each Generator Owner shall also retain evidence of actual disturbance monitoring (i.e., sequence of event recorder, dynamic disturbance recorder, and fault recorder) data to demonstrate the operation of each IBR did adhere to Ride‑through requirements, as specified in Requirement R3, during each frequency excursion event measured at the high-side of the main power transformer. | Operations Assessment | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 |  | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4. | Each Generator Owner identifying an IBR that is in-service by the effective date of PRC-029-1, has known hardware limitations that prevent the IBR from meeting Ride-through criteria as detailed in Requirements R1-R3, and requires an exemption from specific Ride-through criteria shall:[10] [10] The exemption requests for a non-US Registered Entity should be implemented in a manner that is consistent with, or under the direction of, the applicable governmental authority or its agency in the non-US jurisdiction. | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 |  | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.1. | Document information supporting the identified hardware limitation no later than 12 months following the effective date of PRC-029-1. This documentation shall include: | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.1.1. | Identifying information of the IBR (name and facility number); | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.1.2. | Which aspects of Ride-through requirements that the IBR would be unable to meet and the capability of the hardware due to the limitation; | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.1.3. | Identification of the specific piece(s) of hardware causing the limitation; | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.1.4. | Technical documentation verifying the limitation is due to hardware that would need to be physically replaced to meet all Ride-through criteria, and that the limitation cannot be remedied by software updates or setting changes; and | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.1.5. | Information regarding any plans to remedy the hardware limitation (such as an estimated date). | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.2. | Provide a copy of the information detailed in Requirement R4.1, except for any material considered by the original equipment manufacturer to be proprietary information, to the associated Planning Coordinator(s), Transmission Planner(s), Transmission Operator(s), Reliability Coordinator(s), and the Compliance Enforcement Authority (CEA) no later than 12 months following the effective date of PRC-029-1.[11] [11] To the extent the original equipment manufacturer considers any material to be proprietary, the Generator Owner is required to share this proprietary material only with the CEA. | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.2.1. | Provide any response for additional information requested by the associated Planning Coordinator(s), Transmission Planner(s), Transmission Operator(s), Reliability Coordinator(s), and the CEA to the requestor within 90 days of the request. | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.2.2. | Provide a copy of the acceptance of a hardware limitation by the CEA to the associated Planning Coordinator(s), Transmission Planner(s), Transmission Operator(s), and Reliability Coordinator(s) within 90 days of receiving the acceptance.[12] [12] Acceptance by the CEA is verification that the information provided includes all information listed in Requirement R4.1. | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.3. | Each Generator Owner with a previously accepted limitation that replaces the hardware causing the limitation shall document and communicate such a hardware change to the associated Planning Coordinator(s), Transmission Planner(s), Transmission Operator(s), and Reliability Coordinator(s) within 90 days of the hardware change. | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-029 | PRC-029-1 | 4.3.1. | When existing hardware causing the limitation is replaced, the exemption for that Ride‑through criteria no longer applies. | M4. Each Generator Owner submitting for an exemption for an IBR that is in-service by the effective date of PRC-029-1, shall have evidence of submission to the CEA consistent with the information listed in Requirement R4.1. Each Generator Owner shall have evidence of communicated copies of each submission in accordance with Requirement R4.2 and to the associated entities described in Requirement R4.2. Acceptable types of evidence for submittals include, but are not limited to, meeting minutes, agreements, copies of procedures or protocols in effect, or email correspondence. Acceptable types of evidence for a hardware limitation may include, but is not limited to damage curves provided by the original equipment manufacturer. Each Generator Owner that receives a request for additional information under Requirement R4.2.1 shall have evidence of providing that information within 90 days. Each Generator Owner that replaces hardware at an IBR that is directly associated with an accepted exemption and that hardware is the cause for the limitation, shall have evidence of communicating the hardware change to the associated entities described in Requirement R4.3 within 90 days of the hardware replacement. | Long-Term Planning | 2024-10-08 | 2024-11-04 | 2025-07-24 | 2025-08-28 | 2026-10-01 | 2026-10-01 | X | PRC-029-1 Phased-in Compliance Dates Requirements R1, R2, and R3 Capability-Based Elements Bulk Electric System IBRs Entities shall comply with the portion of Requirements R1, R2, and R3 relating to the design of their BES IBRs to meet the requirements by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirements R1, R2, and R3 relating to the design of their applicable non-BES IBRs until January 1, 2027. Performance-Based Elements (all applicable IBRs) Entities shall not be required to comply with the portion of Requirements R1, R2, and R3 relating to the operation of IBRs to meet the requirements until the entity has established the required disturbance monitoring equipment capabilities for those IBRs in accordance with the implementation plan for Reliability Standard PRC-028-1. Requirement R4 Bulk Electric System IBRs Entities shall comply with Requirement R4 for their BES IBRs by October 1, 2026. Applicable Non-BES IBRs Entities shall not be required to comply with Requirement R4 or their non-BES IBRs until January 1, 2027. |  |  | Docket No. RM25-3-000 See Implementation Plan for more information on effective/compliance dates |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 1. | Each applicable Generator Owner shall implement a documented process to identify any complete facility loss of output, or changes in Real Power output that are at least 20 MW and at least 10% of the plant's gross nameplate rating, occurring within a 4 second period. Changes in Real Power for the following are excluded: • Changes associated with intermittent primary energy source availability, created by changes such as variation in wind speed and solar irradiance; • Resource dispatch, resource ramping, planned outages, or planned resource testing; • A Transmission or collection system loss that, by configuration, disconnects the Inverter-Based Resource generator; or • Real Power reduction due solely to a Protection System Misoperations being analyzed and corrected under PRC-004 Reliability Standard. | M1. Each applicable Generator Owner shall have evidence which includes but is not limited to: (1) the documented process for detecting changes in output as described in Requirement R1, (2) evidence to demonstrate implementation of its documented process, (3) actual data recordings, and (4) identification of gross nameplate rating. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 |  | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | No Parts for 1. |  | M1. Each applicable Generator Owner shall have evidence which includes but is not limited to: (1) the documented process for detecting changes in output as described in Requirement R1, (2) evidence to demonstrate implementation of its documented process, (3) actual data recordings, and (4) identification of gross nameplate rating. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 |  | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2. | Each applicable Generator Owner, within 90 calendar days of a Real Power change event pursuant to Requirement R1 or following a request from its associated Reliability Coordinator, Balancing Authority, or Transmission Operator that identified a Disturbance and a change in the Inverter-Based Resource(s) Real Power output, shall:[Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 |  | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2.1. | Analyze its Inverter-Based Resource facility performance during the event, including: | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2.1.1. | Determine the root cause(s) of change(s) in Real Power output; | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2.1.2. | Document the facility’s Ride-through performance including Reactive Power response during the event; | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2.1.3. | Assess any performance issues identified and if corrective actions are needed; and | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2.1.4. | Determine the applicability of the root cause(s) to the Generator Owner’s other Inverter-Based Resource facilities. | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 2.2. | Upon request, provide the analysis results to the requesting associated Reliability Coordinator, Balancing Authority, or Transmission Operator. | M2. Each applicable Generator Owner shall have dated documentation of the required analysis developed in accordance with Requirement R2. Evidence may include, but is not limited to: (1) an analysis report, (2) actual data recordings or derivations, (3) documents describing the device specification and device configuration or settings, and (4) plant configuration. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 3. | If performance issues and a need for corrective actions were identified in Requirement R2 Part 2.1.3, each applicable Generator Owner shall, within 60 calendar days of completing the analysis in Requirement R2, develop one of the following and provide it to the associated Reliability Coordinator, Balancing Authority, and Transmission Operator: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • A Corrective Action Plan (CAP) for the identified Inverter-Based Resource(s), including other applicable facilities owned by the Generator Owner as identified in Requirement R2 Part 2.1.3; or • A technical justification that addresses why corrective actions will not be implemented. | M3. Each applicable Generator Owner shall have dated evidence (electronic or hardcopy format) that demonstrates it developed a CAP or a technical justification, and evidence of transmittal to the Reliability Coordinator, Balancing Authority, and Transmission Operator in accordance with Requirement R3. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 |  | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | No Parts for 3. |  | M3. Each applicable Generator Owner shall have dated evidence (electronic or hardcopy format) that demonstrates it developed a CAP or a technical justification, and evidence of transmittal to the Reliability Coordinator, Balancing Authority, and Transmission Operator in accordance with Requirement R3. | Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 |  | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 4. | Each applicable Generator Owner shall, for each of its Corrective Action Plans developed pursuant to Requirement R3: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-term Planning] | M4. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, communication with equipment manufacturers, and communication with each associated Reliability Coordinator that documents the implementation, updating, or completion of a CAP in accordance with Requirement R3. | Long-Term Planning, Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 |  | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 4.1. | Implement the CAP; | M4. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, communication with equipment manufacturers, and communication with each associated Reliability Coordinator that documents the implementation, updating, or completion of a CAP in accordance with Requirement R3. | Long-Term Planning, Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 4.2. | Update the CAP if actions or timetables change; and | M4. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, communication with equipment manufacturers, and communication with each associated Reliability Coordinator that documents the implementation, updating, or completion of a CAP in accordance with Requirement R3. | Long-Term Planning, Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Subject to Future Enforcement | PRC | PRC-030 | PRC-030-1 | 4.3. | Notify each associated Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. | M4. Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, communication with equipment manufacturers, and communication with each associated Reliability Coordinator that documents the implementation, updating, or completion of a CAP in accordance with Requirement R3. | Long-Term Planning, Operations Planning | 2024-10-08 | 2024-11-04 | 2025-02-20 | 2025-02-20 | 2026-10-01 | 2026-10-01 | X | Phased-in Compliance Dates Requirements R1, R2, R3, and R4 Bulk Electric System IBRs Bulk Electric System IBRs shall initially comply with all Requirements by October 1, 2026. Applicable Non-BES IBRs Applicable Non-BES Inverter-Based Resources shall initially comply with Requirements R1, R2, R3, and R4 by January 1, 2027. Applicable Non-BES Inverter-Based Resources include non-BES Inverter-Based Resources that either have, or contribute to, an aggregate nameplate capacity of greater than or equal to 20 MVA, connected through a system designed primarily for delivering such capacity to a common point of connection at a voltage greater than or equal to 60 kV. |  |  | Filing/Order Docket No. RD25-3-000 See Implementation Plan for more effective/compliance date information |  |  |  |  | GO
Inactive | PRC | PRC-STD | PRC-STD-001-1 | W1. | Each Transmission Operator or Transmission Owner identified in Section 4.1 must submit documentation that an officer of the organization certifies that: a. All protective relay applications are appropriate for the Bulk Power Transmission Paths (“BPTP”) identified in Attachment A – Table 2 of this Standard pursuant to applicable WECC Standards and NERC Standards; b. The BPTP protective relay settings and logic are appropriate pursuant to applicable WECC Standards and NERC Standards; c. Since the last certification or for the last three years all network changes in the path, at the terminals of the path, or in nearby facilities that affect operation of the path have been considered in the protective relay application and settings; d. All relay operations since the last certification or during the last three-year period have been analyzed for correctness and appropriate corrective action taken pursuant to applicable WECC Standards and NERC Standards; e. Up-to-date relay information has been provided to the on-shift operating personnel and the appropriate Reliability Coordinator. Note: If a path operator cannot submit certification on behalf of the multiple owners of a path for Protective Relay Application and Settings because the authority for certification resides with one or more path owners, then the path owner(s) shall submit the certification. The path operator shall notify the path owner(s) and WECC in writing that the path owner(s) is (are) to submit the certification. (Source: WECC Criterion) |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RR07-_-000 | [19 empty] | TO | TOP
Inactive | PRC | PRC-STD | PRC-STD-001-1 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RR07-_-000
Inactive | PRC | PRC-STD | PRC-STD-003-1 | W1. | Owners of protective relays and Remedial Action Schemes (RAS) applied to path elements of selected WECC major transmission path facilities (listed in Attachment A - Table 2) and RAS (listed in Attachment B - Table 3) must take the following action for each known or probable relay misoperation: a. If functionally equivalent protective relaying or RAS remains in service to ensure bulk transmission system reliability; the relay or RAS that misoperated is to be removed from service for repair or modification within 22 hours of the relay or RAS misoperation. The relay or RAS shall be replaced, repaired, or modified such that the incorrect operation will not be repeated. b. If functionally equivalent protective relaying or RAS does not remain in service that will ensure bulk transmission system reliability, and the relay or RAS that misoperated cannot be repaired and placed back in service within 22 hours, the associated transmission path facility must be removed from service. The remaining path facilities, if any, must be de-rated to a reliable operating level. c. If the relay or RAS misoperates and there is some protection but not entirely functionally equivalent, the relay or RAS must be repaired or removed from service within 22 hours. The associated transmission may remain in service; however, system operation must fully comply with WECC and NERC operating standards. This may require an adjustment of operating levels. d. Protective relays or RAS removed from service must be repaired or replaced with functionally equivalent protective relays or RAS within 20 Business Days of removal, or the system shall be operated at levels that meet WECC Standards and NERC Standards or the associated transmission path elements shall be removed from service. It is not intended that the above requirements apply to system protection and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with WECC and NERC standards, and the protective relaying or RAS operation is later found to be incorrect. In such cases, upon determination of the incorrect operation, the requirements of (a) through (d) above will become applicable at the time the incorrect operation is identified. (Source: WECC Criterion) |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RR07-_-000 | [19 empty] | TO | TOP
Inactive | PRC | PRC-STD | PRC-STD-003-1 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RR07-_-000
Inactive | PRC | PRC-STD | PRC-STD-005-1 | W1. | All bulk power transmission elements (i.e. lines, stations and rights of way) included as part of the transmission facilities (or required to maintain transfer capability) impacting each of the transmission paths listed in Attachment A - WECC Table 2 shall be inspected and maintained in accordance with this criterion, taking into consideration diverse environmental and climatic conditions, terrain, equipment, maintenance philosophies, and design practices. a. General This Transmission Maintenance Standard requires each Responsible Entity identified in Section A.4.1 to develop and implement a Transmission Maintenance and Inspection Plan (TMIP) detailing the Responsible Entity’s inspection and maintenance activities applicable to the transmission facilities comprising each of the transmission paths identified in Attachment A – Table 2. b. Standard Requirements (i) TMIP To comply with this Standard, each Responsible Entity identified in Section A4.1 must develop and implement a TMIP. • Because maintenance and inspection practices vary, it is the intent of this Transmission Maintenance Standard to allow flexibility in inspection and maintenance practices while still requiring a description of certain specific inspection and maintenance practices. (a) TMIP Contents The TMIP may be performance-based, time-based, conditional¬based, or a combination of all three as may be appropriate. The TMIP shall: · Identify the facilities for which it is covering by listing the names of each transmission path and the quantities of each equipment component, such as; circuit breaker, relay scheme, transmission line; · Include the scheduled interval (e.g., every two years) for any time-based maintenance activities and a description of conditions that will initiate any condition or performance-based activities; · Describe the maintenance, testing and inspection methods for each activity or component listed under Transmission Line Maintenance and Station Maintenance; · Provide any checklists or forms, or reports used for maintenance activities; · Provide criteria to be used to assess the condition of a transmission facility or component; · Specify condition assessment criteria and the requisite response to each condition as may be appropriate for each specific type of component or feature of the transmission facilities; · Include specific details regarding Transmission Line and Station Maintenance practices as per subsections (1) and (2) below. (1) Transmission Line Maintenance Details The TMIP shall, at a minimum, describe the Responsible Entity’s practices for the following transmission line maintenance activities: · Patrol/Inspection; · Contamination Control (Insulator Washing) (2) Station Maintenance Details The TMIP shall describe the Responsible Entity’s maintenance practices for the following station equipment: · Circuit Breakers · Power Transformers (including phase-shifting transformers) · Regulators · Protective Relay Systems and associated Communication Equipment · RAS Systems and associated Communication Equipment · Reactive Devices (including, but not limited to, Shunt Capacitors, Series Capacitors, Synchronous Condensers, Shunt Reactors, and Tertiary Reactors) Maintenance Record Keeping M1. Each Responsible Entity identified in Section A.4.1 must retain all pertinent maintenance and inspection records that support the TMIP according to the following guidelines: · The Responsible Entity shall maintain records of all maintenance and inspection activities for at least five years. · Each Responsible Entity’s maintenance and inspection records shall identify, at a minimum: o The person(s) responsible for performing the work or inspection; o The date(s) the work or inspection was performed; o The transmission facility on which the work was performed, and o A description of the inspection or maintenance performed. The Transmission Owner or Operator shall maintain (and make available on request) records for maintenance or inspection pertaining to the items listed in subsections (a) and (b) below. (a) Transmission Line Maintenance Records · Patrol/Inspection · Contamination Control (Insulator Washing) (b) Station Maintenance Records · Circuit Breakers · Power Transformers · Regulators · Protective Relay Systems and associated Communication Equipment · RAS Systems and associated Communication Equipment · Reactive Devices c. Compliance Measures This section defines the items that will be reviewed by WECC Staff to monitor and measure each Responsible Entity’s compliance with this Standard, and the compliance levels that will be assessed in the review process. (i) TMIP Certification Each Responsible Entity identified in Section A.4.1 shall annually certify to WECC Staff that it has developed, documented, and implemented a TMIP. (ii) WECC Staff Review WECC Staff will assess performance in the three broad areas described in Paragraph 8 of the Certification Form. These areas are: (1) Development and documentation of the TMIP; (2) Performing maintenance in accordance with the TMIP; (3) Maintaining maintenance records as required by this Standard. (iii) Review Triggers The WECC Staff will conduct a review of the Responsible Entity’s TMIP, maintenance and inspection practices and maintenance records when triggered as described below. (a) Disturbance Report. If a WECC Disturbance Report identifies that transmission maintenance and inspection activities were a substantial contributing factor in the disturbance, WECC Staff may request a review of the Responsible Entity. (b) Recommendation by CMWG team. If in its tri-annual review, the CMWG review team notes areas in transmission availability or maintenance that warrant further review, they may recommend a review by the WECC Staff. (c) Incomplete Annual Certification. If the Responsible Entity identified in Section A.4.1 fails to certify one or more categories of paragraph 8 of the Certification Plan, WECC Staff may request a review of the Responsible Entity. (d) Random Audit. The WECC Staff shall randomly select two or three Responsible Entities each year for review. When a review is requested, the Responsible Entity shall make its TMIP and all maintenance records for the facilities that are part of RMS available to the WECC Staff for review within 30 calendar days from the request date. |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000 | [19 empty] | TO | TOP
Inactive | PRC | PRC-STD | PRC-STD-005-1 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000
Inactive | TOP | TOP-001 | TOP-001-0 | 1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-0 | 2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-0 | 3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-0 | 4. | Each Distribution Provider and Load Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 |  | DP | [7 empty] | LSE
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-0 | 5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-0 | 6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-0 | 7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | 7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | 7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | 7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | 8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-001 | TOP-001-1 | 1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1 | 2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1 | 3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1 | 4. | Each Distribution Provider and Load-Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load-Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 |  | DP | [7 empty] | LSE
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1 | 5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real-time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1 | 6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1 | 7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | 7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | 7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | 7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | 8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1 | No Parts for 8. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-11-20 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-001 | TOP-001-1a | 1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. | M1. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, signed agreements, an authority letter signed by an officer of the company, or other equivalent evidence that will be used to confirm that it has the authority, and has exercised the authority, to alleviate operating emergencies as described in Requirement 1. |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 1. |  | M1. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, signed agreements, an authority letter signed by an officer of the company, or other equivalent evidence that will be used to confirm that it has the authority, and has exercised the authority, to alleviate operating emergencies as described in Requirement 1. |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-1a | 2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. | M2. If an operating emergency occurs the Transmission Operator that experienced the emergency shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it took immediate actions to alleviate the operating emergency including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. (Requirement 2) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 2. |  | M2. If an operating emergency occurs the Transmission Operator that experienced the emergency shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it took immediate actions to alleviate the operating emergency including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. (Requirement 2) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-1a | 3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. | M3. Each Transmission Operator, Balancing Authority, and Generator Operator shall have and provide upon request evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it complied with its Reliability Coordinator’s reliability directives. If the Transmission Operator, Balancing Authority or Generator Operator did not comply with the directive because it would violate safety, equipment, regulatory or statutory requirements, it shall provide evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that it immediately informed the Reliability Coordinator of its inability to perform the directive. (Requirement 3) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 3. |  | M3. Each Transmission Operator, Balancing Authority, and Generator Operator shall have and provide upon request evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it complied with its Reliability Coordinator’s reliability directives. If the Transmission Operator, Balancing Authority or Generator Operator did not comply with the directive because it would violate safety, equipment, regulatory or statutory requirements, it shall provide evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that it immediately informed the Reliability Coordinator of its inability to perform the directive. (Requirement 3) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-1a | 4. | Each Distribution Provider and Load-Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load-Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | M4. Each Balancing Authority, Generator Operator, Distribution Provider and Load Serving Entity shall have and provide upon request evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it complied with its Transmission Operator’s reliability directives. If the Balancing Authority, Generator Operator, Distribution Provider and Load Serving Entity did not comply with the directive because it would violate safety, equipment, regulatory or statutory requirements, it shall provide evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that it immediately informed the Transmission Operator of its inability to perform the directive. (Requirements 3 and 4) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 |  | DP | [7 empty] | LSE
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 4. |  | M4. Each Balancing Authority, Generator Operator, Distribution Provider and Load Serving Entity shall have and provide upon request evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it complied with its Transmission Operator’s reliability directives. If the Balancing Authority, Generator Operator, Distribution Provider and Load Serving Entity did not comply with the directive because it would violate safety, equipment, regulatory or statutory requirements, it shall provide evidence such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that it immediately informed the Transmission Operator of its inability to perform the directive. (Requirements 3 and 4) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-1a | 5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real-time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. | M5. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it informed its Reliability Coordinator and any other potentially affected Transmission Operators of real time or anticipated emergency conditions, and took actions to avoid, when possible, or to mitigate an emergency. (Requirement 5) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 5. |  | M5. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it informed its Reliability Coordinator and any other potentially affected Transmission Operators of real time or anticipated emergency conditions, and took actions to avoid, when possible, or to mitigate an emergency. (Requirement 5) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-1a | 6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | M6. The Transmission Operator, Balancing Authority, and Generator Operator shall each have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it rendered assistance to others as requested, provided that the requesting entity had implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. (Requirement 6) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 6. |  | M6. The Transmission Operator, Balancing Authority, and Generator Operator shall each have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it rendered assistance to others as requested, provided that the requesting entity had implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. (Requirement 6) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-1a | 7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: | M7. The Transmission Operator and Generator Operator shall each have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified either their Transmission Operator in the case of the Generator Operator, or other Transmission Operators, and the Reliability Coordinator when it removed Bulk Electric System facilities from service if removing those facilities would burden neighboring systems. (Requirement 7) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | 7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | M7. The Transmission Operator and Generator Operator shall each have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified either their Transmission Operator in the case of the Generator Operator, or other Transmission Operators, and the Reliability Coordinator when it removed Bulk Electric System facilities from service if removing those facilities would burden neighboring systems. (Requirement 7) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 | 2011-11-21 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | 7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | M7. The Transmission Operator and Generator Operator shall each have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified either their Transmission Operator in the case of the Generator Operator, or other Transmission Operators, and the Reliability Coordinator when it removed Bulk Electric System facilities from service if removing those facilities would burden neighboring systems. (Requirement 7) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 | 2011-11-21 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | 7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. | M7. The Transmission Operator and Generator Operator shall each have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified either their Transmission Operator in the case of the Generator Operator, or other Transmission Operators, and the Reliability Coordinator when it removed Bulk Electric System facilities from service if removing those facilities would burden neighboring systems. (Requirement 7) |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 | 2011-11-21 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | 8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. |  |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-1a | No Parts for 8. |  |  |  | 2010-05-12 | 2010-07-16 | 2011-09-15 | 2011-11-21 | 2011-11-21 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-29-000
Inactive | TOP | TOP-001 | TOP-001-2 | 1. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall comply with each Reliability Directive issued and identified as such by its Transmission Operator(s), unless such action would violate safety, equipment, regulatory, or statutory requirements. | M1. Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall make available, upon request, evidence that it complied with each Reliability Directive issued and identified as such by the Transmission Operator(s) unless such action would violate safety, equipment, regulatory, or statutory requirements, in accordance with Requirement R1. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no event has occurred, the Balancing Authority, Generator Operator, Distribution Provider, or Load-Serving Entity may provide an attestation that an event has not occurred. | Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA | DP |  |  |  |  | GOP |  |  | LSE
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 1. |  | M1. Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall make available, upon request, evidence that it complied with each Reliability Directive issued and identified as such by the Transmission Operator(s) unless such action would violate safety, equipment, regulatory, or statutory requirements, in accordance with Requirement R1. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no event has occurred, the Balancing Authority, Generator Operator, Distribution Provider, or Load-Serving Entity may provide an attestation that an event has not occurred. | Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 2. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall inform its Transmission Operator of its inability to perform an identified Reliability Directive issued by that Transmission Operator. | M2. Each Balancing Authority, Generation Operator, Distribution Provider, and Load-Serving Entity shall make available, upon request, evidence which may include, but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with identified, Reliability Directive(s) issued in accordance with Requirement R2. If no event has occurred, the Balancing Authority, Generator Operator, Distribution Provider, or Load-Serving Entity may provide an attestation that an event has not occurred. | Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA | DP |  |  |  |  | GOP |  |  | LSE
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 2. |  | M2. Each Balancing Authority, Generation Operator, Distribution Provider, and Load-Serving Entity shall make available, upon request, evidence which may include, but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with identified, Reliability Directive(s) issued in accordance with Requirement R2. If no event has occurred, the Balancing Authority, Generator Operator, Distribution Provider, or Load-Serving Entity may provide an attestation that an event has not occurred. | Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 3. | Each Transmission Operator shall inform its Reliability Coordinator and Transmission Operator(s) that are known or expected to be affected by each actual and anticipated Emergency based on its assessment of its Operational Planning Analysis. | M3. Each Transmission Operator shall make available, upon request, evidence that it has informed its Reliability Coordinator and Transmission Operators that it knew or expected to be affected by each actual and anticipated Emergency based on its assessment of its Operational Planning Analysis in accordance with Requirement R3. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 3. |  | M3. Each Transmission Operator shall make available, upon request, evidence that it has informed its Reliability Coordinator and Transmission Operators that it knew or expected to be affected by each actual and anticipated Emergency based on its assessment of its Operational Planning Analysis in accordance with Requirement R3. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 4. | Each Transmission Operator shall render emergency assistance to other Transmission Operators, as requested and available, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | M4. Each Transmission Operator shall make available, upon request, evidence that requested and available emergency assistance was rendered to other Transmission Operators in accordance with Requirement R4, unless such actions would violate safety, equipment, regulatory, or statutory requirements. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 4. |  | M4. Each Transmission Operator shall make available, upon request, evidence that requested and available emergency assistance was rendered to other Transmission Operators in accordance with Requirement R4, unless such actions would violate safety, equipment, regulatory, or statutory requirements. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 5. | Each Transmission Operator shall inform its Reliability Coordinator and other Transmission Operators of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas unless conditions do not permit such communications. Examples of such operations are relay or equipment failures, and changes in generation, Transmission, or Load. | M5. Each Transmission Operator shall make available, upon request, evidence that it informed its Reliability Coordinator and other Transmission Operators of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas in accordance with Requirement R5, unless conditions did not permit such communications. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 5. |  | M5. Each Transmission Operator shall make available, upon request, evidence that it informed its Reliability Coordinator and other Transmission Operators of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas in accordance with Requirement R5, unless conditions did not permit such communications. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 6. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and negatively impacted interconnected NERC registered entities of planned outages of telemetering equipment, control equipment and associated communication channels between the affected entities. | M6. Each Balancing Authority and Transmission Operator shall make available, upon request, evidence that it notified its Reliability Coordinator and negatively impacted interconnected NERC registered entities of planned outages of telemetering equipment, control equipment, and associated communication channels in accordance with Requirement R6. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no event has occurred, the Balancing Authority or Transmission Operator may provide an attestation that an event has not occurred. | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 6. |  | M6. Each Balancing Authority and Transmission Operator shall make available, upon request, evidence that it notified its Reliability Coordinator and negatively impacted interconnected NERC registered entities of planned outages of telemetering equipment, control equipment, and associated communication channels in accordance with Requirement R6. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no event has occurred, the Balancing Authority or Transmission Operator may provide an attestation that an event has not occurred. | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 7. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | M7. Each Transmission Operator shall make available evidence for any occasion in which it has operated outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv as specified in Requirement R7. Such evidence could include, but is not limited to, dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 7. |  | M7. Each Transmission Operator shall make available evidence for any occasion in which it has operated outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv as specified in Requirement R7. Such evidence could include, but is not limited to, dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 8. | Each Transmission Operator shall inform its Reliability Coordinator of each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. | M8. Each Transmission Operator shall make available evidence that it has informed its Reliability Coordinator of each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis in accordance with Requirement R8. Such evidence could include, but is not limited to, an electronic or hard copy of information from the Operational Planning Analysis used in its assessment, dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 8. |  | M8. Each Transmission Operator shall make available evidence that it has informed its Reliability Coordinator of each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis in accordance with Requirement R8. Such evidence could include, but is not limited to, an electronic or hard copy of information from the Operational Planning Analysis used in its assessment, dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 9. | Each Transmission Operator shall not operate outside any System Operating Limit (SOL) identified in Requirement R8 for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based. | M9. Each Transmission Operator shall make available evidence for any occasion in which it has operated outside an SOL for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based, as specified in Requirement R8 and in Requirement R9. Such evidence could include, but is not limited to, dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 9. |  | M9. Each Transmission Operator shall make available evidence for any occasion in which it has operated outside an SOL for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based, as specified in Requirement R8 and in Requirement R9. Such evidence could include, but is not limited to, dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 10. | Each Transmission Operator shall inform its Reliability Coordinator of its actions to return the system to within limits when an IROL, or an SOL identified in Requirement R8, has been exceeded. | M10. Each Transmission Operator shall make available evidence that it has informed its Reliability Coordinator of actions being taken to return the system to within limits when an IROL, or an SOL identified in Requirement R8, has been exceeded in accordance with Requirement R10. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 10. |  | M10. Each Transmission Operator shall make available evidence that it has informed its Reliability Coordinator of actions being taken to return the system to within limits when an IROL, or an SOL identified in Requirement R8, has been exceeded in accordance with Requirement R10. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-2 | 11. | Each Transmission Operator shall act or direct others to act, to mitigate both the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8. | M11. Each Transmission Operator shall make available evidence of when it acted or directed others to mitigate both the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8, in accordance with Requirement R11. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-2 | No Parts for 11. |  | M11. Each Transmission Operator shall make available evidence of when it acted or directed others to mitigate both the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8, in accordance with Requirement R11. Such evidence could include, but is not limited to, dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If no event has occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-001 | TOP-001-3 | 1. | Each Transmission Operator shall act to address the reliability of its Transmission Operator Area via direct actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 1. |  | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 2. | Each Balancing Authority shall act to address the reliability of its Balancing Authority Area via direct actions or by issuing Operating Instructions. | M2. Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 2. |  | M2. Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  |  |  | GOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 3. |  | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 4. | Each Balancing Authority, Generator Operator, and Distribution Providershall inform its Transmission Operator of its inability to perform an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  |  |  | GOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 4. |  | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 5. | Each Transmission Operator, Generator Operator and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 5. |  | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to perform an Operating Instruction issued by that Balancing Authority. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 6. |  | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 7. | Each Transmission Operator shall assist other Transmission Operators, if requested and able, provided that the requesting entity has implemented its Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 7. |  | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 8. |  | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 9. |  | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 10. | Each Transmission Operator shall perform the following as necessary for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized status, voltages, and flow data for Facilities and the status of Special Protection Systems as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | 10.1. | Within its Transmission Operator Area, monitor Facilities and the status of Special Protection Systems, and | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized status, voltages, and flow data for Facilities and the status of Special Protection Systems as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2017-04-01 |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | 10.2. | Outside its Transmission Operator Area, obtain and utilize status, voltages, and flow data for Facilities and the status of Special Protection Systems. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized status, voltages, and flow data for Facilities and the status of Special Protection Systems as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | 11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Special Protection Systems that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Special Protection Systems that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 11. |  | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Special Protection Systems that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 12. |  | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 13. |  | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 14. |  | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 15. |  | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 16. |  | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 17. |  | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 18. |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 19. | Each Transmission Operator shall have data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Transmission Operator Area. | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, or other evidence that it has data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Transmission Operator Area. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 19. |  | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, or other evidence that it has data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Transmission Operator Area. | Operations Planning, Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-3 | 20. | Each Balancing Authority shall have data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Balancing Authority Area. | Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, or other evidence that it has data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Balancing Authority Area. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-3 | No Parts for 20. |  | Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, or other evidence that it has data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Balancing Authority Area. | Real-Time Operations, Same-Day Operations | 2015-02-12 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-001 | TOP-001-4 | 1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 1. |  | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 2. |  | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA | DP |  |  |  |  | GOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 3. |  | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA | DP |  |  |  |  | GOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 4. |  | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 5. |  | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 6. |  | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 7. |  | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 8. |  | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 9. |  | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 10.1. | Monitor Facilities within its Transmission Operator Area; | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 | 2017-04-17 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 | 2017-04-17 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 | 2017-04-17 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 | 2017-04-17 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 | 2017-04-17 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 | 2017-04-17 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | 11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 11. |  | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 12. |  | Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 13. |  | Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 14. |  | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 15. |  | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 16. |  | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 17. |  | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 18. |  | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 19. | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 19. |  | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 20. |  | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 21. |  | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 22. | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | M22. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 22. |  | M22. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 23. |  | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-4 | 24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000 | BA
Inactive | TOP | TOP-001 | TOP-001-4 | No Parts for 24. |  | Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2018-07-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD17-4-000
Inactive | TOP | TOP-001 | TOP-001-5 | 1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 1. |  | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 2. |  | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 3. |  | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 4. |  | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 5. |  | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 6. |  | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 7. |  | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 8. |  | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 9. |  | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 10.1. | Monitor Facilities within its Transmission Operator Area; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | 11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 11. |  | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 12. |  | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 13. |  | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 14. |  | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 15. |  | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 16. |  | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 17. |  | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 18. |  | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 19. | Reserved. | Reserved. |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 19. |  | Reserved. |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 20. |  | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 21. |  | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 22. | Reserved. | Reserved. |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 22. |  | Reserved. |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 23. |  | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Inactive | TOP | TOP-001 | TOP-001-5 | 24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000 | BA
Inactive | TOP | TOP-001 | TOP-001-5 | No Parts for 24. |  | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | M1. Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 1. |  | M1. Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | M2. Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 2. |  | M2. Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA | DP |  |  |  |  | GOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 3. |  | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | M4. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA | DP |  |  |  |  | GOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 4. |  | M4. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | M5. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 5. |  | M5. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  | DP |  |  |  |  | GOP | [13 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 6. |  | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | M7. Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 7. |  | M7. Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | M8. Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 8. |  | M8. Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 9. |  | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10.1. | Monitor Facilities within its Transmission Operator Area; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 11. |  | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 12. |  | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 13. |  | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. Other evidence could include but is not limited to: Reliability Coordinator’s SOL methodology, system logs/records showing successfully mitigated SOL exceedances in conjunction with Operating Plans (e.g. mutually agreed operating protocols between TOPs and their Reliability Coordinator, Operating Procedures, Operating Processes, operating policies, generator redispatch logs, equipment settings for automatically switched equipment and reactive power/voltage control devices, switching schedules, etc.). | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 14. |  | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. Other evidence could include but is not limited to: Reliability Coordinator’s SOL methodology, system logs/records showing successfully mitigated SOL exceedances in conjunction with Operating Plans (e.g. mutually agreed operating protocols between TOPs and their Reliability Coordinator, Operating Procedures, Operating Processes, operating policies, generator redispatch logs, equipment settings for automatically switched equipment and reactive power/voltage control devices, switching schedules, etc.). | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded in accordance with its Reliability Coordinator’s SOL methodology. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded in accordance with its Reliability Coordinator’s SOL methodology. Such evidence could include but is not limited to dated operator logs, electronic communications, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 15. |  | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded in accordance with its Reliability Coordinator’s SOL methodology. Such evidence could include but is not limited to dated operator logs, electronic communications, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 16. |  | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 17. |  | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 18. |  | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 19. | Reserved. | Reserved. |  | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 19. |  | Reserved. |  | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 20. |  | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 21. |  | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 22. | Reserved. | Reserved. |  | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 22. |  | Reserved. |  | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 23. |  | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 24. |  | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | 25. | Each Transmission Operator shall use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real- time monitoring, and Operational Planning Analysis. | M25. Each Transmission Operator shall have, and provide upon request, evidence that it used the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. Evidence could include, but is not limited to: Reliability Coordinator’s SOL methodology, Operating Plans, contingency sets, alarming and study reporting thresholds, operator logs, voice recordings or other equivalent evidence. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001 | TOP-001-6 | No Parts for 25. |  | M25. Each Transmission Operator shall have, and provide upon request, evidence that it used the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. Evidence could include, but is not limited to: Reliability Coordinator’s SOL methodology, Operating Plans, contingency sets, alarming and study reporting thresholds, operator logs, voice recordings or other equivalent evidence. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Inactive | TOP | TOP-002 | TOP-002-0 | 1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP |  |  | LSE
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 9. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 9. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 10. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject confidentiality requirements), and to its Reliability Coordinator. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 11. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 12. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 13. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-0 | 14.1. | Changes in real and reactive output capabilities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-0 | 14.2. | Automatic Voltage Regulator status and mode setting. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-0 | 15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 15. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | 16.1. | Changes in transmission facility status |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | 16.2. | Changes in transmission facility rating. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | 17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 17. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 18. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-0 | 19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-0 | No Parts for 19. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-08-07 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-1 | 1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 1. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 2. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [6 empty] | GOP |  |  | LSE
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 3. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 4. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 5. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 6. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 7. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 8. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 9. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 9. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 10. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject confidentiality requirements), and to its Reliability Coordinator. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 11. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [22 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 12. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 13. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-1 | 14.1. | Changes in real output capabilities |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-1 | 15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 15. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | 16.1. | Changes in transmission facility status. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | 16.2. | Changes in transmission facility rating. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | 17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 17. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [5 empty] | GOP | [13 empty] | TOP |  | TSP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 18. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-1 | 19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-1 | No Parts for 19. |  |  |  | 2006-08-02 | [8 empty] | 2007-01-01 | Replaced with TOP-002-2 (TOP-002-1 was never enforceable)
Inactive | TOP | TOP-002 | TOP-002-2 | 1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 7. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 8. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 9. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 10. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 11. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [22 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 12. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 13. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2 | 14.1. | Changes in real output capabilities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2 | 14.2. | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2 | 15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 15. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | 16.1. | Changes in transmission facility status. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | 16.2. | Changes in transmission facility rating. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | 17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 17. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 18. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2 | 19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2 | No Parts for 19. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-12-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 1. |  | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 2. |  | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 3. |  | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 4. |  | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 5. |  | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 6. |  | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 7. |  | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 8. |  | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 9. |  | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 10. |  | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 11. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [22 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 12. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 13. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | 14.1. | Changes in real output capabilities. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | 15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 15. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | 16.1. | Changes in transmission facility status. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | 16.2. | Changes in transmission facility rating. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | 17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 17. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 18. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2.1b | 19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2.1b | No Parts for 19. |  |  |  | 2012-04-11 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | TOP | TOP-002 | TOP-002-2a | 1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 1. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 2. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 3. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 4. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 5. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 6. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 7. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 8. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 9. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 10. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 11. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [22 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 12. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 13. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2a | 14.1. | Changes in real output capabilities. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2a | 14.2. | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2a | 15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 15. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | 16.1. | Changes in transmission facility status. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | 16.2. | Changes in transmission facility rating. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | 17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 17. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 18. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2a | 19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2a | No Parts for 19. |  |  |  | 2009-02-10 | 2009-03-05 | 2009-12-02 | 2009-12-02 | 2009-12-02 |  |  |  |  | 2011-10-19 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-002 | TOP-002-2b | 1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 1. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 2. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [5 empty] | GOP |  |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 3. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 4. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 5. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 6. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 7. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 8. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 9. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 10. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 11. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [22 empty] | TSP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 12. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 13. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2b | 14.1. | Changes in real output capabilities. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2b | 14.2. | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2b | 15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [6 empty] | GOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 15. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | 16.1. | Changes in transmission facility status. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | 16.2. | Changes in transmission facility rating. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | 17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 17. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 18. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-2b | 19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-2b | No Parts for 19. |  |  |  | 2010-11-04 | 2011-04-15 | 2011-10-20 | 2011-10-20 | 2011-10-20 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM11-23-000
Inactive | TOP | TOP-002 | TOP-002-3 | 1. | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  |  | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-3 | No Parts for 1. |  |  |  | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-002 | TOP-002-3 | 2. | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has developed a plan to operate within each IROL and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1 in accordance with Requirement R2. Such evidence could include, but it is not limited to, plans for precluding operating in excess of each IROL and each SOL which, while not an IROL, was identified as a result of the Operational Planning Analysis | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-3 | No Parts for 2. |  | Each Transmission Operator shall have evidence that it has developed a plan to operate within each IROL and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1 in accordance with Requirement R2. Such evidence could include, but it is not limited to, plans for precluding operating in excess of each IROL and each SOL which, while not an IROL, was identified as a result of the Operational Planning Analysis | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-002 | TOP-002-3 | 3. | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). | Each Transmission Operator shall have evidence that it notified all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in the plan(s) in accordance with Requirement R3. Such evidence could include but is not limited to dated operator logs, voice recordings, or e-mail records. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-3 | No Parts for 3. |  | Each Transmission Operator shall have evidence that it notified all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in the plan(s) in accordance with Requirement R3. Such evidence could include but is not limited to dated operator logs, voice recordings, or e-mail records. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-002 | TOP-002-4 | 1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-4 | No Parts for 1. |  | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-002 | TOP-002-4 | 2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-4 | No Parts for 2. |  | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-002 | TOP-002-4 | 3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-4 | No Parts for 3. |  | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-002 | TOP-002-4 | 4. | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | 4.1. | Expected generation resource commitment and dispatch | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | 4.2. | Interchange scheduling | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | 4.3. | Demand patterns | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | 4.4. | Capacity and energy reserve requirements, including deliverability capability | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2016-01-26 |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | 5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | No Parts for 5. |  | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-002 | TOP-002-4 | 6. | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-002 | TOP-002-4 | No Parts for 6. |  | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-002 | TOP-002-4 | 7. | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-002 | TOP-002-4 | No Parts for 7. |  | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | M1. Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include, but is not limited to dated power flow study results. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | No Parts for 1. |  | M1. Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include, but is not limited to dated power flow study results. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | M2. Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include, but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | No Parts for 2. |  | M2. Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include, but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include, but is not limited to dated operator logs, or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | No Parts for 3. |  | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include, but is not limited to dated operator logs, or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 4. | Each Balancing Authority shall have an Operating Plan(s) for the next day that addresses: | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 4.1. | Expected generation resource commitment and dispatch; | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 4.2. | Interchange scheduling; | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 4.3. | Demand patterns; and | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 4.4. | Capacity and energy reserve requirements, including deliverability capability. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | M5. Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | No Parts for 5. |  | M5. Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 6. | Each Transmission Operator shall provide its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | No Parts for 6. |  | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 7. | Each Balancing Authority shall provide its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | No Parts for 7. |  | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include, but is not limited to dated operator logs or email records. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8. | Each Balancing Authority shall have an extreme cold weather Operating Process for its Balancing Authority Area, addressing preparations for and operations during extreme cold weather periods. The extreme cold weather Operating Process shall include, but is not limited to: | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.1. | A methodology for identifying an extreme cold weather period within each Balancing Authority Area; | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.2. | A methodology to determine an adequate reserve margin during the extreme cold weather period considering the generating unit(s) operating limitations in previous extreme cold weather periods that includes, but is not limited to: | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.2.1. | Capability and availability; | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.2.2. | Fuel supply and inventory concerns; | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.2.3. | Start-up issues; | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.2.4. | Fuel switching capabilities; and | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.2.5. | Environmental constraints. | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.3. | A methodology to determine a five-day hourly forecast during the identified extreme cold weather periods that includes, but is not limited to: | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.3.1. | Expected generation resource commitment and dispatch; | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.3.2. | Demand patterns | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.3.3. | Capacity and energy reserve requirements, including deliverability capability; and | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-002 | TOP-002-5 | 8.3.4. | Weather forecast. | M8. Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Inactive | TOP | TOP-003 | TOP-003-0 | 1. | Generator Operators and Transmission Operators shall provide planned outage information. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-0 | 1.1. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-0 | 1.2. | Each Transmission Operator shall provide outage information daily to its Reliability Coordinator, and to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. The Reliability Coordinator shall establish the outage reporting requirements. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-0 | 1.3. | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-0 | 2. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-003 | TOP-003-0 | 3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-003 | TOP-003-0 | 4. | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | TOP | TOP-003 | TOP-003-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-003 | TOP-003-1 | 1. | Generator Operators and Transmission Operators shall provide planned outage information. | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-1 | 1.1. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-1 | 1.2. | Each Transmission Operator shall provide outage information daily to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-1 | 1.3. | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-1 | 2. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-1 | No Parts for 2. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-003 | TOP-003-1 | 3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-1 | No Parts for 3. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-003 | TOP-003-1 | 4. | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | TOP | TOP-003 | TOP-003-1 | No Parts for 4. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-003 | TOP-003-2 | 1. | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | Operations Planning | 2012-05-09 | 2013-04-16 | [5 empty] |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses and Real-time monitoring. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [5 empty] |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | 1.2. | A mutually-agreeable format. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [5 empty] |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | 1.3. | A periodicity for providing data. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [5 empty] |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | 1.4. | The deadline by which the respondent is to provide the indicated data. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [5 empty] |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | 2. | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA
Inactive | TOP | TOP-003 | TOP-003-2 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA
Inactive | TOP | TOP-003 | TOP-003-2 | 2.2. | A mutually-agreeable format. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA
Inactive | TOP | TOP-003 | TOP-003-2 | 2.3. | A periodicity for providing data. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA
Inactive | TOP | TOP-003 | TOP-003-2 | 2.4. | The deadline by which the respondent is to provide the indicated data. |  | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA
Inactive | TOP | TOP-003 | TOP-003-2 | 3. | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification, as developed in Requirement R1, to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements in accordance with Requirement R3. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | No Parts for 3. |  | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification, as developed in Requirement R1, to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements in accordance with Requirement R3. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-003 | TOP-003-2 | 4. | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements, in accordance with Requirement R4. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA
Inactive | TOP | TOP-003 | TOP-003-2 | No Parts for 4. |  | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements, in accordance with Requirement R4. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-003 | TOP-003-2 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications for data, in accordance with Requirement R5. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000 | BA | DP |  |  | GO |  | GOP |  | IA | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-2 | No Parts for 5. |  | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications for data, in accordance with Requirement R5. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning | 2012-05-09 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-14-000
Inactive | TOP | TOP-003 | TOP-003-3 | 1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 1.3. | A periodicity for providing data. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 1.4. | The deadline by which the respondent is to provide the indicated data. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-003 | TOP-003-3 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-003 | TOP-003-3 | 2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-003 | TOP-003-3 | 2.3. | A periodicity for providing data. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-003 | TOP-003-3 | 2.4. | The deadline by which the respondent is to provide the indicated data. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2016-01-26 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-003 | TOP-003-3 | 3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | No Parts for 3. |  | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-003 | TOP-003-3 | 4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA
Inactive | TOP | TOP-003 | TOP-003-3 | No Parts for 4. |  | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Long-Term Planning, Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | TOP | TOP-003 | TOP-003-3 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 5.1. | A mutually agreeable format | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2017-04-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 5.2. | A mutually agreeable process for resolving data conflicts | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2017-04-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-3 | 5.3. | A mutually agreeable security protocol | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | 2017-04-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 1.3. | A periodicity for providing data. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 1.4. | The deadline by which the respondent is to provide the indicated data. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA
Inactive | TOP | TOP-003 | TOP-003-4 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA
Inactive | TOP | TOP-003 | TOP-003-4 | 2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA
Inactive | TOP | TOP-003 | TOP-003-4 | 2.3. | A periodicity for providing data. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA
Inactive | TOP | TOP-003 | TOP-003-4 | 2.4. | The deadline by which the respondent is to provide the indicated data. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA
Inactive | TOP | TOP-003 | TOP-003-4 | 3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | No Parts for 3. |  | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | TOP | TOP-003 | TOP-003-4 | 4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA
Inactive | TOP | TOP-003 | TOP-003-4 | No Parts for 4. |  | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Operations Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000
Inactive | TOP | TOP-003 | TOP-003-4 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 5.1. | A mutually agreeable format | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 5.2. | A mutually agreeable process for resolving data conflicts | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-4 | 5.3. | A mutually agreeable security protocol | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-03-31 | Filing/Order Docket No. RD20-4-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.1. | Operating limitations based on: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.1.2. | fuel supply and inventory concerns; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.1.3. | fuel switching capabilities; and | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.1.4. | environmental constraints | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.2. | Generating unit(s) minimum: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.2.1. | design temperature; or | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.2.2. | historical operating temperature; or | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.4. | A periodicity for providing data. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 1.5. | The deadline by which the respondent is to provide the indicated data. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.1. | Operating limitations based on: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.1.1. | capability and availability; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.1.2. | fuel supply and inventory concerns; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.1.3. | fuel switching capabilities; and | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.1.4. | environmental constraints. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.2. | Generating unit(s) minimum: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.2.1. | design temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.2.2. | historical operating temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.4. | A periodicity for providing data. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 2.5. | The deadline by which the respondent is to provide the indicated data. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | 3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | No Parts for 3. |  | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000
Inactive | TOP | TOP-003 | TOP-003-5 | 4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | TOP | TOP-003 | TOP-003-5 | No Parts for 4. |  | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000
Inactive | TOP | TOP-003 | TOP-003-5 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 |  |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 5.1. | A mutually agreeable format | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 5.2. | A mutually agreeable process for resolving data conflicts | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-5 | 5.3. | A mutually agreeable security protocol | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  | 2025-06-30 | Filing/Order Docket No. RD21-5-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. The specification shall include, but not be limited to: | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments including non‐BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Transmission Operator. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.1. | Operating limitations based on: | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.1.1. | capability and availability; | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.1.2. | fuel supply and inventory concerns; | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.1.3. | fuel switching capabilities; and | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.1.4. | environmental constraints | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.2. | Generating unit(s) minimum: | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.2.1. | design temperature; or | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.2.2. | historical operating temperature; or | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.4. | Identification of a mutually agreeable process for resolving conflicts. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes at a minimum the following. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.5.1. | Specified deadlines or periodicity which data and information is to be provided; | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable; | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.5.3. | Provisions to update or correct data and information, as applicable or necessary; | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.5.4. | A mutually agreeable format; | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 1.5.5. | Mutually agreeable method(s) for securely transferring data and information. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | 2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐time monitoring. The data specification shall include, but not be limited to: | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real‐time monitoring including non‐Bulk Electric System data and information, and external network data and information, as deemed necessary by the Balancing Authority, and identification of the entity responsible for responding to the specification. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.1. | Operating limitations based on: | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.1.1. | capability and availability; | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.1.2. | fuel supply and inventory concerns; | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.1.3. | fuel switching capabilities; and | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.1.4. | environmental constraints. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.2. | Generating unit(s) minimum: | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.2.1. | design temperature; or | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.2.2. | historical operating temperature; or | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.4. | Identification of a mutually agreeable process in resolving conflicts | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes at a minimum the following. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.5.3. | Provisions to update or correct data and information, as applicable or necessary. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.5.4. | A mutually agreeable format. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 2.5.5. | A mutually agreeable methods for securely transferring data and information. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA
Inactive | TOP | TOP-003 | TOP-003-6 | 3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e‐mail records. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | [20 empty] | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | No Parts for 3. |  | Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e‐mail records. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata)
Inactive | TOP | TOP-003 | TOP-003-6 | 4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e‐mail records. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | No Parts for 4. |  | Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e‐mail records. | Operations Planning | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata)
Inactive | TOP | TOP-003 | TOP-003-6 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata) | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Inactive | TOP | TOP-003 | TOP-003-6 | No Parts for 5. |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2023-08-17 | [8 empty] | 2023-08-23 | Repalced by TOP-003-6.1 (errata)
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The specification shall include, but not be limited to: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Transmission Operator. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.3.1. | Operating limitations based on: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.3.1.1. | capability and availability; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.3.1.2. | fuel supply and inventory concerns; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.3.1.3. | fuel switching capabilities; and | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.3.1.4. | environmental constraints | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.4. | Identification of a mutually agreeable process for resolving conflicts. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes at a minimum the following. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.5.1. | Specified deadlines or periodicity which data and information is to be provided; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.5.3. | Provisions to update or correct data and information, as applicable or necessary; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.5.4. | A mutually agreeable format; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 1.5.5. | Mutually agreeable method(s) for securely transferring data and information. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring including non-Bulk Electric System data and information, and external network data and information, as deemed necessary by the Balancing Authority, and identification of the entity responsible for responding to the specification. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.1. | Operating limitations based on: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.1.1. | capability and availability; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.1.2. | fuel supply and inventory concerns; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.1.3. | fuel switching capabilities; and | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.1.4. | environmental constraints. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.2. | Generating unit(s) minimum: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.2.1. | design temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.2.2. | historical operating temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.4. | Identification of a mutually agreeable process in resolving conflicts | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes at a minimum the following. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.5.3. | Provisions to update or correct data and information, as applicable or necessary. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.5.4. | A mutually agreeable format. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 2.5.5. | A mutually agreeable method(s) for securely transferring data and information. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 | 2025-07-01 |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | No Parts for 3. |  | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Long-Term Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | No Parts for 4. |  | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Long-Term Planning | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000 | BA | DP |  |  | GO | GO-2 | GOP | GOP-2 | [11 empty] | TO | TOP
Mandatory Subject to Enforcement | TOP | TOP-003 | TOP-003-6.1 | No Parts for 5. |  | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2023-08-23 | 2023-09-21 | 2023-11-02 | 2023-11-02 | 2025-07-01 |  |  |  |  | 2026-09-30 | Filing/Order Docket No. RD23-6-000
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The specification shall include, but not be limited to: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Transmission Operator. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.1. | Operating limitations based on: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.1.1. | capability and availability; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.1.2. | fuel supply and inventory concerns; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.1.3. | fuel switching capabilities; and | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.1.4. | environmental constraints | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.2. | Generating unit(s) minimum: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.2.1. | design temperature; or | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.2.2. | historical operating temperature; or | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.4. | Identification of a mutually agreeable process for resolving conflicts. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes, at a minimum, the following. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.5.1. | Specified deadlines or periodicity which data and information is to be provided; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.5.3. | Provisions to update or correct data and information, as applicable or necessary; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.5.4. | A mutually agreeable format; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 1.5.5. | Mutually agreeable method(s) for securely transferring data and information. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. The data specification shall include, but not be limited to: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments, including non-Bulk Electric System data and information, and external network data and information, as deemed necessary by the Balancing Authority, and identification of the entity responsible for responding to the specification. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.1. | Operating limitations based on: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.1.1. | capability and availability; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.1.2. | fuel supply and inventory concerns; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.1.3. | fuel switching capabilities; and | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.1.4. | environmental constraints. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.2. | Generating unit(s) minimum: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.2.1. | design temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.2.2. | historical operating temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.4. | Identification of a mutually agreeable process in resolving conflicts | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes at a minimum the following. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.5.3. | Provisions to update or correct data and information, as applicable or necessary. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.5.4. | A mutually agreeable format. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 2.5.5. | A mutually agreeable method(s) for securely transferring data and information. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 | 2026-10-01 |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | No Parts for 3. |  | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | No Parts for 4. |  | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-7 | No Parts for 5. |  | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | 2026-10-01 |  |  |  |  | 2029-03-31 | Filing/Order Docket No. RD25-5-000
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The specification shall include, but not be limited to: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments, as deemed necessary by the Transmission Operator, including non-BES data and information, external network data and information, Inverter-based Resource (IBR)-specific data and parameters, and identification of the entities responsible for responding to the specification. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.1. | Operating limitations based on: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.1.1. | capability and availability; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.1.2. | fuel supply and inventory concerns; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.1.3. | fuel switching capabilities; and | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.1.4. | environmental constraints | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.2. | Generating unit(s) minimum: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.2.1. | design temperature; or | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.2.2. | historical operating temperature; or | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.4. | Identification of a mutually agreeable process for resolving conflicts. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes, but is not limited to: | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5.1. | Specified deadlines or periodicity in which data and information is to be provided; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5.3. | Requirements for necessary model submissions to be consistent with the model submitted for planning purposes, subject to modifications for operations purposes, as applicable; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5.4. | Provisions to update or correct data and information, as applicable or necessary; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5.5. | A mutually agreeable format; | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 1.5.6. | Mutually agreeable method(s) for securely transferring data and information. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. The data specification shall include, but not be limited to: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments, as deemed necessary by the Balancing Authority, including non Bulk Electric System data and information, IBR-specific data and parameters, and external network data and information, and identification of the entity responsible for responding to the specification. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.1. | Operating limitations based on: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.1.1. | capability and availability; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.1.2. | fuel supply and inventory concerns; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.1.3. | fuel switching capabilities; and | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.1.4. | environmental constraints. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.2. | Generating unit(s) minimum: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.2.1. | design temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.2.2. | historical operating temperature; or | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.4. | Identification of a mutually agreeable process in resolving conflicts; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes, but is not limited to: | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5.3. | Requirements for necessary model submissions to be consistent with the model submitted for planning purposes, subject to modifications for operations purposes, as applicable; | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5.4. | Provisions to update or correct data and information, as applicable or necessary. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5.5. | A mutually agreeable format. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 2.5.6. | A mutually agreeable method(s) for securely transferring data and information. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | 2029-04-01 |  |  |  |  | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | [20 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | No Parts for 3. |  | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or email records. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | BA
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | No Parts for 4. |  | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions, Real-time monitoring, and Near-Term Energy Reliability Assessments. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or email records. | Operations Planning | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | 5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000 | BA | DP |  |  | GO |  | GOP | [12 empty] | TO | TOP
Subject to Future Enforcement | TOP | TOP-003 | TOP-003-8 | No Parts for 5. |  | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2025-10-31 | 2025-11-04 | 2026-02-19 | 2026-02-19 | 2029-04-01 | [5 empty] | Filing/Order Docket No. RD26-1-000
Inactive | TOP | TOP-004 | TOP-004-0 | 1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable
Inactive | TOP | TOP-004 | TOP-004-0 | 2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable
Inactive | TOP | TOP-004 | TOP-004-0 | 3. | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable
Inactive | TOP | TOP-004 | TOP-004-0 | 4. | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable
Inactive | TOP | TOP-004 | TOP-004-0 | 5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable
Inactive | TOP | TOP-004 | TOP-004-0 | 6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | 6.1. | Equipment ratings. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | 6.2. | Monitoring and controlling voltage levels and real and reactive power flows. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | 6.3. | Switching transmission elements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | 6.4. | Planned outages of transmission elements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | 6.5. | Development of IROLs and SOLs. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-0 | 6.6. | Responding to IROL and SOL violations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2005-04-01 | Filing/Order Docket No. RM06-16-000 TOP-004-0 was never enforceable | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-004 | TOP-004-1 | 2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-004 | TOP-004-1 | 3. | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-004 | TOP-004-1 | 4. | If a Transmission Operator enters an unknown operating state (i.e., any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-004 | TOP-004-1 | 5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-004 | TOP-004-1 | 6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 6.1. | Equipment ratings. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 6.2. | Monitoring and controlling voltage levels and real and reactive power flows. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 6.3. | Switching transmission elements. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 6.4. | Planned outages of transmission elements. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 6.5. | Development of IROLs and SOLs. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-1 | 6.6. | Responding to IROL and SOL violations. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | 1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). | M1. Each Transmission Operator that enters an unknown operating state for which valid limits have not been determined, shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it restored operations to respect proven reliable power system limits within 30 minutes as specified in Requirement 4. |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | No Parts for 1. |  | M1. Each Transmission Operator that enters an unknown operating state for which valid limits have not been determined, shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it restored operations to respect proven reliable power system limits within 30 minutes as specified in Requirement 4. |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31
Inactive | TOP | TOP-004 | TOP-004-2 | 2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. | M2. Each Transmission Operator shall have and provide upon request current policies and procedures that address the execution and coordination of activities that impact inter- and intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | No Parts for 2. |  | M2. Each Transmission Operator shall have and provide upon request current policies and procedures that address the execution and coordination of activities that impact inter- and intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31
Inactive | TOP | TOP-004 | TOP-004-2 | 3. | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | No Parts for 3. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31
Inactive | TOP | TOP-004 | TOP-004-2 | 4. | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | No Parts for 4. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31
Inactive | TOP | TOP-004 | TOP-004-2 | 5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | No Parts for 5. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31
Inactive | TOP | TOP-004 | TOP-004-2 | 6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | 6.1. | Monitoring and controlling voltage levels and real and reactive power flows. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | 6.2. | Switching transmission elements. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | 6.3. | Planned outages of transmission elements. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-004 | TOP-004-2 | 6.4. | Responding to IROL and SOL violations. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2017-03-31 | [21 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-0 | 1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-0 | 1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable) | [13 empty] | RC
Inactive | TOP | TOP-005 | TOP-005-0 | 2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable)
Inactive | TOP | TOP-005 | TOP-005-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable)
Inactive | TOP | TOP-005 | TOP-005-0 | 3. | Upon request, each Reliability Coordinator shall, via the ISN or equivalent system, exchange with other Reliability Coordinators operating data that are necessary to allow the Reliability Coordinators to perform operational reliability assessments and coordinate reliable operations. Reliability Coordinators shall share with each other the types of data listed in Attachment 1- TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable) | [13 empty] | RC
Inactive | TOP | TOP-005 | TOP-005-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable)
Inactive | TOP | TOP-005 | TOP-005-0 | 4. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable) | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-0 | No Parts for 4. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable)
Inactive | TOP | TOP-005 | TOP-005-0 | 5. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable) | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-0 | No Parts for 5. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with TOP-005-1 (TOP-005-0 was never enforceable)
Inactive | TOP | TOP-005 | TOP-005-1 | 1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1 | 1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | TOP | TOP-005 | TOP-005-1 | 2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-005 | TOP-005-1 | 3. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1 | No Parts for 3. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-005 | TOP-005-1 | 4. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-1 | No Parts for 4. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-005 | TOP-005-1.1 | 1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1.1 | 1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | TOP | TOP-005 | TOP-005-1.1 | 2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1.1 | No Parts for 2. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000
Inactive | TOP | TOP-005 | TOP-005-1.1 | 3. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1.1 | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000
Inactive | TOP | TOP-005 | TOP-005-1.1 | 4. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000 | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-1.1 | No Parts for 4. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RD09-2-000
Inactive | TOP | TOP-005 | TOP-005-1.1a | 1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1.1a | 1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | TOP | TOP-005 | TOP-005-1.1a | 2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1.1a | No Parts for 2. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | TOP | TOP-005 | TOP-005-1.1a | 3. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-1.1a | No Parts for 3. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | TOP | TOP-005 | TOP-005-1.1a | 4. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-1.1a | No Parts for 4. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | TOP | TOP-005 | TOP-005-2 | 1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-2 | No Parts for 1. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-005 | TOP-005-2 | 2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-2 | No Parts for 2. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-005 | TOP-005-2 | 3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-2 | No Parts for 3. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-005 | TOP-005-2a | 1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-2a | No Parts for 1. |  | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-005 | TOP-005-2a | 2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-2a | No Parts for 2. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-005 | TOP-005-2a | 3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-2a | No Parts for 3. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-005 | TOP-005-3a | 1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | [11 empty] | PSE | [7 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-3a | No Parts for 1. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | TOP | TOP-005 | TOP-005-3a | 2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | [19 empty] | TOP
Inactive | TOP | TOP-005 | TOP-005-3a | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | TOP | TOP-005 | TOP-005-3a | 3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [12 empty] | PSE
Inactive | TOP | TOP-005 | TOP-005-3a | No Parts for 3. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | TOP | TOP-006 | TOP-006-0 | 1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | 1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | [6 empty] | GOP
Inactive | TOP | TOP-006 | TOP-006-0 | 1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable
Inactive | TOP | TOP-006 | TOP-006-0 | 3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable
Inactive | TOP | TOP-006 | TOP-006-0 | 4. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable
Inactive | TOP | TOP-006 | TOP-006-0 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable
Inactive | TOP | TOP-006 | TOP-006-0 | 6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable
Inactive | TOP | TOP-006 | TOP-006-0 | 7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 TOP-006-0 was never enforceable
Inactive | TOP | TOP-006 | TOP-006-1 | 1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | 1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [6 empty] | GOP
Inactive | TOP | TOP-006 | TOP-006-1 | 1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-006 | TOP-006-1 | 3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-006 | TOP-006-1 | 4. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-006 | TOP-006-1 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-006 | TOP-006-1 | 6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-006 | TOP-006-1 | 7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-1 | No Parts for 7. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-006 | TOP-006-2 | 1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | 1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | TOP | TOP-006 | TOP-006-2 | 1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | No Parts for 2. |  | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-006 | TOP-006-2 | 3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | No Parts for 3. |  | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-006 | TOP-006-2 | 4. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | No Parts for 4. |  | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-006 | TOP-006-2 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | No Parts for 5. |  | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-006 | TOP-006-2 | 6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | No Parts for 6. |  | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-006 | TOP-006-2 | 7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-2 | No Parts for 7. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | TOP | TOP-006 | TOP-006-3 | 1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement R1.1) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | 1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement R1.1) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | [6 empty] | GOP
Inactive | TOP | TOP-006 | TOP-006-3 | 1.2. | Each Transmission Operator shall inform the Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement R1.1) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | [20 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | 1.3. | Each Balancing Authority shall inform its Reliability Coordinator of all generation resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement R1.1) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA
Inactive | TOP | TOP-006 | TOP-006-3 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. (Requirement R1.2) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | No Parts for 2. |  | M2. Each Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. (Requirement R1.2) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000
Inactive | TOP | TOP-006 | TOP-006-3 | 3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide its operating personnel with appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. | M3. Each Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator of all generation resources available for use. (Requirement R1.3) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | No Parts for 3. |  | M3. Each Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator of all generation resources available for use. (Requirement R1.3) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000
Inactive | TOP | TOP-006 | TOP-006-3 | 4. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement R2. | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | No Parts for 4. |  | M4. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement R2. | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000
Inactive | TOP | TOP-006 | TOP-006-3 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. | M5. Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, operating instructions, training materials, or other equivalent evidence that will be used to confirm that it informed its operating personnel of appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. (Requirement R3) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | No Parts for 5. |  | M5. Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, operating instructions, training materials, or other equivalent evidence that will be used to confirm that it informed its operating personnel of appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. (Requirement R3) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000
Inactive | TOP | TOP-006 | TOP-006-3 | 6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement R4) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | No Parts for 6. |  | M6. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement R4) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000
Inactive | TOP | TOP-006 | TOP-006-3 | 7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. | M7. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement R5) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006 | TOP-006-3 | No Parts for 7. |  | M7. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement R5) | Real-Time Operations | 2012-11-07 | 2013-04-05 | [7 empty] | 2015-03-18 | Filing/Order Docket No. RM13-12-000
Inactive | TOP | TOP-007 | TOP-007-0 | 1. | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL or SOL was exceeded and the actions taken to return the system to within limits. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-0 | No Parts for 1. |  | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL or SOL was exceeded and the actions taken to return the system to within limits. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-007 | TOP-007-0 | 2. | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. | M2. Evidence that the Transmission Operator returned the system to within IROL within 30 minutes for each incident that an IROL, or SOL that became an IROL due to changed system conditions, was exceeded. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-0 | No Parts for 2. |  | M2. Evidence that the Transmission Operator returned the system to within IROL within 30 minutes for each incident that an IROL, or SOL that became an IROL due to changed system conditions, was exceeded. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-007 | TOP-007-0 | 3. | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to return the system to within limits. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-0 | No Parts for 3. |  | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to return the system to within limits. |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-007 | TOP-007-0 | 4. | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | TOP | TOP-007 | TOP-007-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-007 | TOP-007-WECC-1 | 1. | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. [Time Horizon: Real-time Operations] |  |  | 2008-10-29 | 2009-03-25 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2014-06-17 | Filing/Order Docket No. RM09-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-WECC-1 | No Parts for 1. |  |  |  | 2008-10-29 | 2009-03-25 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2014-06-17 | Filing/Order Docket No. RM09-14-000
Inactive | TOP | TOP-007 | TOP-007-WECC-1 | 2. | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. [Time Horizon: Real-time Operations] |  |  | 2008-10-29 | 2009-03-25 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2014-06-17 | Filing/Order Docket No. RM09-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-WECC-1 | 2.1. | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. |  |  | 2008-10-29 | 2009-03-25 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2014-06-17 | Filing/Order Docket No. RM09-14-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-WECC-1a | 1. | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. | M1. Evidence that actual power flow has not exceeded the SOL for the specified time limit in R1. | Real-Time Operations | 2014-02-06 | 2014-03-12 | 2014-06-18 | 2014-06-18 | 2014-06-18 |  |  |  |  | 2017-03-10 | Filing/Order Docket No. RM09-14-000 and RD14-8-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-WECC-1a | No Parts for 1. |  | M1. Evidence that actual power flow has not exceeded the SOL for the specified time limit in R1. | Real-Time Operations | 2014-02-06 | 2014-03-12 | 2014-06-18 | 2014-06-18 | 2014-06-18 |  |  |  |  | 2017-03-10 | Filing/Order Docket No. RM09-14-000 and RD14-8-000
Inactive | TOP | TOP-007 | TOP-007-WECC-1a | 2. | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. | M2. Evidence that Net Scheduled Interchange has not exceeded the SOL when the Transmission Operator implements real-time schedules as required by R2. | Real-Time Operations | 2014-02-06 | 2014-03-12 | 2014-06-18 | 2014-06-18 | 2014-06-18 |  |  |  |  | 2017-03-10 | Filing/Order Docket No. RM09-14-000 and RD14-8-000 | [20 empty] | TOP
Inactive | TOP | TOP-007 | TOP-007-WECC-1a | 2.1. | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. | M2. Evidence that Net Scheduled Interchange has not exceeded the SOL when the Transmission Operator implements real-time schedules as required by R2. | Real-Time Operations | 2014-02-06 | 2014-03-12 | 2014-06-18 | 2014-06-18 | 2014-06-18 | 2014-06-18 |  |  |  | 2017-03-10 | Filing/Order Docket No. RM09-14-000 and RD14-8-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-0 | 1. | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-0 | No Parts for 1. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-008 | TOP-008-0 | 2. | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-0 | No Parts for 2. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-008 | TOP-008-0 | 3. | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-0 | No Parts for 3. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-008 | TOP-008-0 | 4. | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-0 | No Parts for 4. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | TOP | TOP-008 | TOP-008-1 | 1. | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. | The Transmission Operator involved in an SOL or IROL violation shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it took immediate steps to relieve the condition. (Requirement 1) | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-1 | No Parts for 1. |  | The Transmission Operator involved in an SOL or IROL violation shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it took immediate steps to relieve the condition. (Requirement 1) | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-008 | TOP-008-1 | 2. | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program print outs, or other equivalent evidence that will be used to determine if it disconnected an overloaded facility in accordance with Requirement 3 Part 1 | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-1 | No Parts for 2. |  | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program print outs, or other equivalent evidence that will be used to determine if it disconnected an overloaded facility in accordance with Requirement 3 Part 1 | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-008 | TOP-008-1 | 3. | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permitted, otherwise, immediately thereafter. (Requirement 3 Part 2) | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-1 | No Parts for 3. |  | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permitted, otherwise, immediately thereafter. (Requirement 3 Part 2) | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-008 | TOP-008-1 | 4. | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. | M4. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, computer facilities documents, computer printouts, training documents, copies of analysis program results, operator logs or other equivalent evidence that will be used to confirm that it has sufficient information and analysis tools to determine the cause(s) of SOL violations. (Requirement 4 Part 1) M5. The Transmission Operator that violates an SOL shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it used the results of these analyses to immediately mitigate the SOL violation. (Requirement 4 Part 3) | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | TOP | TOP-008 | TOP-008-1 | No Parts for 4. |  | M4. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, computer facilities documents, computer printouts, training documents, copies of analysis program results, operator logs or other equivalent evidence that will be used to confirm that it has sufficient information and analysis tools to determine the cause(s) of SOL violations. (Requirement 4 Part 1) M5. The Transmission Operator that violates an SOL shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it used the results of these analyses to immediately mitigate the SOL violation. (Requirement 4 Part 3) | Long-Term Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | TOP | TOP-010 | TOP-010-1 | 1. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 1.1. | Criteria for evaluating the quality of Real-time data; | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 2. | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | BA
Inactive | TOP | TOP-010 | TOP-010-1 | 2.1. | Criteria for evaluating the quality of Real-time data; | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | BA
Inactive | TOP | TOP-010 | TOP-010-1 | 2.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | BA
Inactive | TOP | TOP-010 | TOP-010-1 | 2.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | BA
Inactive | TOP | TOP-010 | TOP-010-1 | 3. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 3.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 3.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 3.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 |  | 2016-09-22 |  |  |  | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | [20 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | 4. | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000 | BA | [19 empty] | TOP
Inactive | TOP | TOP-010 | TOP-010-1 | No Parts for 4. |  | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-05-05 | 2016-05-26 | 2016-09-22 | 2016-09-22 | [5 empty] | 2018-03-31 | Filing/Order Docket No. RD16-6-000
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 1. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 1.1. | Criteria for evaluating the quality of Real-time data; | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 2. | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 2.1. | Criteria for evaluating the quality of Real-time data; | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 2.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 2.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | BA
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 3. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 3.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 3.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 3.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | 2016-12-14 |  |  |  |  | Filing/Order Docket No. RD-16-6-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | 4. | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000 | BA | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010 | TOP-010-1(i) | No Parts for 4. |  | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | Real-Time Operations | 2016-11-02 | 2016-11-07 | 2016-12-14 | 2016-12-14 | 2018-04-01 | [5 empty] | Filing/Order Docket No. RD-16-6-000
Inactive | TOP | TOP-STD | TOP-STD-007-0 | W1. | Operating Transfer Capability Limit Criteria Actual power flow and net scheduled power flow over an interconnection or transfer path shall be maintained within Operating Transfer Capability Limits (“OTC”). The OTC is the maximum amount of actual power that can be transferred over direct or parallel transmission elements comprising: • An interconnection from one Transmission Operator area to another Transmission Operator area; or • A transfer path within a Transmission Operator area. The net schedule over an interconnection or transfer path within a Transmission Operator area shall not exceed the OTC, regardless of the prevailing actual power flow on the interconnection or transfer path. a. Operating limits. No elements within the interconnection shall be scheduled above continuous operating limits. An element is defined as any generating unit, transmission line, transformer, bus, or piece of electrical equipment involved in the transfer of power within an interconnection. b. Stability. The interconnected power system shall remain stable upon loss of any one single element without system cascading that could result in the successive loss of additional elements. The system voltages shall be within acceptable limits defined in the WECC Reliability Criteria for Transmission System Planning. If a single event could cause loss of multiple elements, these shall be considered in lieu of a single element outage. This could occur in exceptional cases such as two lines on the same right-of-way next to an airport. In either case, loss of either single or multiple elements should not cause uncontrolled, widespread collapse of the interconnected power system. For purposes of this WECC Standard TOP-STD-007-0 - Operating Transfer Capability Section, stability shall include transient stability, post transient stability or dynamic stability whichever is most limiting to OTC. c. System contingency response. Following the outage and before adjustments can be made: (i) No remaining element shall exceed its short-time emergency rating. (ii) The steady-state system voltages shall be within emergency limits. The limiting event shall be determined by conducting power flow and stability studies while simulating various operating conditions. These studies shall be updated as system configurations introduce significant changes in the interconnection.(Source: WECC Criterion) |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000 | [20 empty] | TOP
Inactive | TOP | TOP-STD | TOP-STD-007-0 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000
Inactive | TPL | TPL-001 | TPL-001-0 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.1. | Be made annually. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.8. | Include existing and planned facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 2.1.1. | Including a schedule for implementation. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | 3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.4. | Have established normal (pre-contingency) operating procedures in place. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.5. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.6. | Be performed for selected demand levels over the range of forecast system demands. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.8. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 2.1.1. | Including a schedule for implementation. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 2.1.2. | Including a discussion of expected required in-service dates of facilities. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 2.1.3. | Consider lead times necessary to implement plans. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | 3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1 | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD09-2-000
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.4. | Have established normal (pre-contingency) operating procedures in place. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.5. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.6. | Be performed for selected demand levels over the range of forecast system demands. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.8. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0.1(i)_R1, the Planning Authority and Transmission Planner shall each: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 2.1.1. | Including a schedule for implementation. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 2.1.2. | Including a discussion of expected required in-service dates of facilities. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 2.1.3. | Consider lead times necessary to implement plans. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | 3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-0.1(i) | No Parts for 3. |  |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | TPL | TPL-001 | TPL-001-1 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.1. | Be made annually. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.8. | Include existing and planned facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 2.1.1. | Including a schedule for implementation. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | 3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-1 | No Parts for 3. |  |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000
Inactive | TPL | TPL-001 | TPL-001-2 | 1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [See standard for further information regarding R1] |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 1. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [See standard for further information regarding R2] |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 2. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R3] |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 3. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R4] |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 4. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 5. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 6. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 7. |  |  |  | 2011-08-04 | 2011-10-19 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-2 | 8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [See standard for further information regarding R8] | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | Long-Term Planning | 2011-08-04 | 2011-10-19 | [5 empty] | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2013-12-23 | Filing/Order Docket No. RM12-1-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-2 | No Parts for 8. |  | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | Long-Term Planning | 2011-08-04 | 2011-10-19 | [5 empty] | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  | 2013-12-23 | Filing/Order Docket No. RM12-1-000
Inactive | TPL | TPL-001 | TPL-001-3 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.1. | Be made annually. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.5. | Have all projected firm transfers modeled. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.8. | Include existing and planned facilities. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | Long-Term Planning | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 2.1.1. | Including a schedule for implementation. |  | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 2.1.3. | Consider lead times necessary to implement plans. |  | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | 3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-3 | No Parts for 3. |  | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-Time Operations | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000
Inactive | TPL | TPL-001 | TPL-001-4 | 1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1. | System models shall represent: | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2013-12-23 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1.1. | Existing Facilities | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2015-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1.2. | Known outage(s) of generation or Transmission Facility(ies) with a duration of at least six months. | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2015-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1.3. | New planned Facilities and changes to existing Facilities | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2015-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1.4. | Real and reactive Load forecasts | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2015-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1.5. | Known commitments for Firm Transmission Service and Interchange | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2015-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 1.1.6. | Resources (supply or demand side) required for Load | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 | 2015-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.1.1. | System peak Load for either Year One or year two, and for year five. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.1.2. | System Off-Peak Load for one of the five years. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.1.3. | P1 events in Table 1, with known outages modeled as in Requirement R1, Part 1.1.2, under those System peak or Off-Peak conditions when known outages are scheduled. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.1.4. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : -Real and reactive forecasted Load. -Expected transfers. -Expected in service dates of new or modified Transmission Facilities. -Generation additions, retirements, or other dispatch scenarios. -Controllable Loads and Demand Side Management. -Duration or timing of known Transmission outages. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.3 . | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.4.2. | System Off-Peak Load for one of the five years. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.3. | Contingency analyses for Requirement R3, Parts 3.1 & 3.2 shall: | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.4 . | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.4 .1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 3.5 . | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Special Protection System is not considered pulling out of synchronism. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall: | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.4 . | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.4 .1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 4.5 . | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | No Parts for 5. |  | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000
Inactive | TPL | TPL-001 | TPL-001-4 | 6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | No Parts for 6. |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000
Inactive | TPL | TPL-001 | TPL-001-4 | 7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | No Parts for 7. |  | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2015-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000
Inactive | TPL | TPL-001 | TPL-001-4 | 8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 |  |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-4 | 8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2013-02-07 | 2013-02-28 | 2013-10-17 | 2013-12-23 | 2016-01-01 | 2016-01-01 |  |  |  | 2023-06-30 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1.1. | System models shall represent: |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1.1.1. | Existing Facilities. |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1.1.2. | New planned Facilities and changes to existing Facilities. |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1.1.3. | Real and reactive Load forecasts. |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1.1.4. | Known commitments for Firm Transmission Service and Interchange. |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 1.1.5. | Resources (supply or demand side) required for Load. |  |  | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.1.1. | System peak Load for either Year One or year two, and for year five. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.1.2. | System Off-Peak Load for one of the five years. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.1.3. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : • Real and reactive forecasted Load. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. • Controllable Loads and Demand Side Management. • Duration or timing of known Transmission outages. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.1.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.4.2. | System Off-Peak Load for one of the five years. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.4.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.4.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.3. | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | No Parts for 5. |  | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000
Inactive | TPL | TPL-001 | TPL-001-5 | 6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | M6. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | No Parts for 6. |  | M6. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000
Inactive | TPL | TPL-001 | TPL-001-5 | 7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | No Parts for 7. |  | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000
Inactive | TPL | TPL-001 | TPL-001-5 | 8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-001 | TPL-001-5 | 8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2018-11-07 | 2018-12-07 | 2020-01-23 | 2020-04-13 | [5 empty] | 2020-06-10 | Filing/Order Docket No. RM19-10-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1.1. | System models shall represent: | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1.1.1. | Existing Facilities. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1.1.2. | New planned Facilities and changes to existing Facilities. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1.1.3. | Real and reactive Load forecasts. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1.1.4. | Known commitments for Firm Transmission Service and Interchange. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 1.1.5. | Resources (supply or demand side) required for Load. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.1.1. | System peak Load for either Year One or year two, and for year five. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.1.2. | System Off-Peak Load for one of the five years. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.1.3. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : - Real and reactive forecasted Load. - Expected transfers. - Expected in service dates of new or modified Transmission Facilities. - Reactive resource capability. - Generation additions, retirements, or other dispatch scenarios. - Controllable Loads and Demand Side Management. - Duration or timing of known Transmission outages. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.1.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.4.2. | System Off-Peak Load for one of the five years. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress TPL-001-5.1 — Transmission System Planning Performance Requirements Page 4 of 32 the System within a range of credible conditions that demonstrate a measurable change in performance: - Load level, Load forecast, or dynamic Load model assumptions. - Expected transfers. - Expected in service dates of new or modified Transmission Facilities. - Reactive resource capability. - Generation additions, retirements, or other dispatch scenarios. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.4.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.4.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.3 and 2.4.3. The Corrective Action Plan(s) shall: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2025-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: - Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. - Installation, modification, or removal of Protection Systems or Remedial Action Schemes. - Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. - Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. - Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. - Use of rate applications, DSM, new technologies, or other initiatives. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2025-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2025-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2025-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2025-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.3. | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4. | For the Stability portion of the Planning Assessment, as described in Requirement R2,Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.3.2 DO NOT USE | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | No Parts for 5. |  | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | M6. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | No Parts for 6. |  | M6. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | No Parts for 7. |  | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. 8.1. If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001 | TPL-001-5.1 | 8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2018-11-07 | 2020-04-23 | 2020-06-10 | 2020-06-10 | 2023-07-01 | 2023-07-01 | X |  |  |  | Filing/Order Docket No. RD20-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.1. | Be made annually. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.7. | Demonstrate that system performance meets Category B contingencies. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.8. | Include existing and planned facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 1.5. | Consider all contingencies applicable to Category B. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 2.1.1. | Including a schedule for implementation. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | 3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000
Inactive | TPL | TPL-002 | TPL-002-0a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.1. | Be made annually. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.7. | Demonstrate that system performance meets Category B contingencies. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.8. | Include existing and planned facilities. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 1.5. | Consider all contingencies applicable to Category B. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 2.1.1. | Including a schedule for implementation. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | 3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0a | No Parts for 3. |  |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2011-10-23 | Filing/Order Docket No. RD09-4-000
Inactive | TPL | TPL-002 | TPL-002-0b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.11. | Include the effects of existing and planned control devices. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.5. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.7. | Demonstrate that system performance meets Category B contingencies. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.8. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 1.5. | Consider all contingencies applicable to Category B. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 2.1.1. | Including a schedule for implementation. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 2.1.3. | Consider lead times necessary to implement plans. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 | 2011-10-24 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | 3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0b | No Parts for 3. |  |  |  | 2009-11-05 | 2009-11-17 | 2011-09-15 | 2011-10-24 | 2011-10-24 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-16-000, RM10-6-000
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.11. | Include the effects of existing and planned control devices. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.5. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.7. | Demonstrate that system performance meets Category B contingencies. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.8. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 1.5. | Consider all contingencies applicable to Category B. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0(i)b_R1, the Planning Authority and Transmission Planner shall each: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 2.1.1. | Including a schedule for implementation. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 2.1.3. | Consider lead times necessary to implement plans. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | 3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-0(i)b | No Parts for 3. |  |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | TPL | TPL-002 | TPL-002-1b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.1. | Be made annually. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.7. | Demonstrate that system performance meets Category B contingencies. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.8. | Include existing and planned facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 1.5. | Consider all contingencies applicable to Category B. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 2.1.1. | Including a schedule for implementation. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | 3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-1b | No Parts for 3. |  |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000
Inactive | TPL | TPL-002 | TPL-002-2b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.1. | Be made annually. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.7. | Demonstrate that system performance meets Category B contingencies. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.8. | Include existing and planned facilities. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 1.5. | Consider all contingencies applicable to Category B. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 2.1.1. | Including a schedule for implementation. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | 3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4. | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-002 | TPL-002-2b | No Parts for 3. |  |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Superseded by FERC Approval of TPL-001-4.
Inactive | TPL | TPL-003 | TPL-003-0 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I. The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: See standard for table. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.1. | Be made annually. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.8. | Include existing and planned facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 1.5. | Consider all contingencies applicable to Category C. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 2.1.1. | Including a schedule for implementation. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2010-04-22 | Filing/Order Docket No. RM06-16-000
Inactive | TPL | TPL-003 | TPL-003-0a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.1. | Be made annually. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.8. | Include existing and planned facilities. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 1.5. | Consider all contingencies applicable to Category C. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 2.1.1. | Including a schedule for implementation. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0a | No Parts for 3. |  |  |  | 2008-07-30 | 2008-10-24 | 2010-04-23 | 2010-04-23 | 2010-04-23 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RD09-4-000
Inactive | TPL | TPL-003 | TPL-003-0b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.11. | Include the effects of existing and planned control devices. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.5. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.8. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 1.5. | Consider all contingencies applicable to Category C. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 2.1.1. | Including a schedule for implementation. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 2.1.3. | Consider lead times necessary to implement plans. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0b | No Parts for 3. |  |  |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.11. | Include the effects of existing and planned control devices. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.5. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.8. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 1.5. | Consider all contingencies applicable to Category C. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0(i)b_R1, the Planning Authority and Transmission Planner shall each: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 2.1.1. | Including a schedule for implementation. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 2.1.3. | Consider lead times necessary to implement plans. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-0(i)b | No Parts for 3. |  |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | TPL | TPL-003 | TPL-003-1a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.1. | Be made annually. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.8. | Include existing and planned facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 1.5. | Consider all contingencies applicable to Category C. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-1_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 2.1.1. | Including a schedule for implementation. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-1a | No Parts for 3. |  |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000
Inactive | TPL | TPL-003 | TPL-003-2a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.1. | Be made annually. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.8. | Include existing and planned facilities. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 1.5. | Consider all contingencies applicable to Category C. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 2.1.1. | Including a schedule for implementation. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2a | No Parts for 3. |  |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000
Inactive | TPL | TPL-003 | TPL-003-2b | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.1. | Be made annually. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.11. | Include the effects of existing and planned control devices. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.5. | Have all projected firm transfers modeled. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.8. | Include existing and planned facilities. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 1.5. | Consider all contingencies applicable to Category C. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 2.1.1. | Including a schedule for implementation. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 2.1.2. | Including a discussion of expected required in-service dates of facilities. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 2.1.3. | Consider lead times necessary to implement plans. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | 3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-003 | TPL-003-2b | No Parts for 3. |  |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000
Inactive | TPL | TPL-004 | TPL-004-0 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.1. | Be made annually. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.2. | Be conducted for near-term (years one through five). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.4. | Have all projected firm transfers modeled. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.5. | Include existing and planned facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.8. | Include the effects of existing and planned control devices. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 1.4. | Consider all contingencies applicable to Category D. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | 2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-19 | Filing/Order Docket No. RM06-16-000
Inactive | TPL | TPL-004 | TPL-004-0a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.2. | Be conducted for near-term (years one through five). | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.4. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.5. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.8. | Include the effects of existing and planned control devices. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 1.4. | Consider all contingencies applicable to Category D. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | 2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0a | No Parts for 2. |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0_R1. |  | 2013-02-07 | 2013-04-12 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RD13-8-000
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.1. | Be made annually. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.2. | Be conducted for near-term (years one through five). | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.4. | Have all projected firm transfers modeled. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.5. | Include existing and planned facilities. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.8. | Include the effects of existing and planned control devices. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 1.4. | Consider all contingencies applicable to Category D. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 |  | 2016-01-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | 2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-0(i)a | No Parts for 2. |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0(i)a_R1. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | [5 empty] | 2015-12-31 | Filing/Order Docket No. RM15-13-000
Inactive | TPL | TPL-004 | TPL-004-1 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.1. | Be made annually. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.2. | Be conducted for near-term (years one through five). |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.4. | Have all projected firm transfers modeled. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.5. | Include existing and planned facilities. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.8. | Include the effects of existing and planned control devices. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 1.4. | Consider all contingencies applicable to Category D. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 |  | 2012-07-06 |  |  |  | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | 2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-1 | No Parts for 2. |  |  |  | 2011-02-17 | 2011-03-31 | 2012-04-19 | 2012-07-06 | [5 empty] | 2012-07-06 | Filing/Order Docket No. RM06-16-009, RM11-18-000
Inactive | TPL | TPL-004 | TPL-004-2 | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.1. | Be made annually. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.2. | Be conducted for near-term (years one through five). |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.4. | Have all projected firm transfers modeled. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.5. | Include existing and planned facilities. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.8. | Include the effects of existing and planned control devices. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 1.4. | Consider all contingencies applicable to Category D. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | 2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2 | No Parts for 2. |  |  |  | 2013-02-07 | 2013-02-28 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM12-1-000 and RM13-9-000
Inactive | TPL | TPL-004 | TPL-004-2a | 1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.1. | Be made annually. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.2. | Be conducted for near-term (years one through five). |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.4. | Have all projected firm transfers modeled. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.5. | Include existing and planned facilities. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.8. | Include the effects of existing and planned control devices. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 1.4. | Consider all contingencies applicable to Category D. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | 2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-004 | TPL-004-2a | No Parts for 2. |  |  |  | 2013-02-07 | 2013-04-12 | [7 empty] | 2013-12-23 | Filing/Order Docket No. RD13-8-000
Inactive | TPL | TPL-005 | TPL-005-0 | 1. | Each Regional Reliability Organization shall annually conduct reliability assessments of its respective existing and planned Regional Bulk Electric System (generation and transmission facilities) for: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.1. | Current year: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.1.1 | Winter |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.1.2. | Summer. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.1.3. | Other system conditions as deemed appropriate by the Regional Reliability Organization. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.2. | Near-term planning horizons (years one through five). Detailed assessments shall be conducted. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.3. | Longer-term planning horizons (years six through ten). Assessment shall focus on the analysis of trends in resources and transmission Adequacy, other industry trends and developments, and reliability concerns. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 1.4. | Inter-Regional reliability assessments to demonstrate that the performance of these systems is in compliance with NERC Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0, TPL-004-0 and respective Regional transmission and generation criteria. These assessments shall also identify key reliability issues and the risks and uncertainties affecting Adequacy and Security. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 2. | The Regional Reliability Organization shall provide its Regional and Inter-Regional seasonal, near-term, and longer-term reliability assessments to NERC on an annual basis. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000
Inactive | TPL | TPL-005 | TPL-005-0 | 3. | The Regional Reliability Organization shall perform special reliability assessments as requested by NERC or the NERC Board of Trustees under their specific directions and criteria. Such assessments may include, but are not limited to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 3.1. | Security assessments. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 3.2. | Operational assessments. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 3.3. | Evaluations of emergency response preparedness. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 3.4. | Adequacy of fuel supply and hydro conditions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 3.5. | Reliability impacts of new or proposed environmental rules and regulations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-005 | TPL-005-0 | 3.6. | Reliability impacts of new or proposed legislation that affects, has affected, or has the potential to affect the Adequacy of the interconnected Bulk Electric Systems in North America. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2014-12-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1. | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.1. | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.2. | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.3. | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.4. | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.5. | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.6. | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0 | 1.7. | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | [7 empty] | 2009-04-15 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1. | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.1. | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.2. | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.3. | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.4. | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.5. | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.6. | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-006 | TPL-006-0.1 | 1.7. | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | Long-Term Planning | 2009-04-15 | [8 empty] | 2014-12-31 | This standard has not been filed with FERC for approval because TPL-006-0 has not been approved by FERC. | [16 empty] | RRO
Inactive | TPL | TPL-007 | TPL-007-1 | 1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s), in accordance with Requirement R1. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2017-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | No Parts for 1. |  | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s), in accordance with Requirement R1. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2017-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000
Inactive | TPL | TPL-007 | TPL-007-1 | 2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2018-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | No Parts for 2. |  | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2018-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000
Inactive | TPL | TPL-007 | TPL-007-1 | 3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | No Parts for 3. |  | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000
Inactive | TPL | TPL-007 | TPL-007-1 | 4. | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 4.1. | The study or studies shall include the following conditions: | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements in Table 1. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 4.3. | The GMD Vulnerability Assessment shall be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners, and to any functional entity that submits a written request and has a reliability-related need. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 4.3.1. | If a recipient of the GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2019-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2019-01-01 | 2019-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2019-01-01 | 2019-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 6. | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2021-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-1 | 6.1. | Be based on the effective GIC flow information provided in Requirement R5; | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2021-01-01 | 2021-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-1 | 6.2. | Document assumptions used in the analysis; | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2021-01-01 | 2021-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-1 | 6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2021-01-01 | 2021-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-1 | 6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2021-01-01 | 2021-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-1 | 7. | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems. • Use of Operating Procedures, specifying how long they will be needed as part of the Corrective Action Plan. • Use of Demand-Side Management, new technologies, or other initiatives. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 7.2. | Be reviewed in subsequent GMD Vulnerability Assessments until it is determined that the System meets the performance requirements contained in Table 1. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 7.3. | Be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), functional entities referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-1 | 7.3.1. | If a recipient of the Corrective Action Plan provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2014-12-17 | 2015-01-21 | 2016-09-22 | 2016-11-29 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM15-11-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2019-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | No Parts for 1. |  | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2019-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-2 | 2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2019-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | No Parts for 2. |  | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2019-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-2 | 3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | No Parts for 3. |  | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-2 | 4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 4.1. | The study or studies shall include the following conditions: | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2020-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2020-01-01 | 2020-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2020-01-01 | 2020-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 6.1. | Be based on the effective GIC flow information provided in Requirement R5; | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 6.2. | Document assumptions used in the analysis; | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.3. | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2024-01-01 | 2024-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.1. | The study or studies shall include the following conditions: | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2023-01-01 | 2023-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2020-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2020-01-01 | 2019-01-25 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2020-01-01 | 2020-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | 10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 10.1. | Be based on the effective GIC flow information provided in Requirement R9; | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 10.2. | Document assumptions used in the analysis; | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2022-01-01 | 2022-01-01 | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-2 | 11. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2021-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | No Parts for 11. |  | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2021-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-2 | 12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2021-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-2 | No Parts for 12. |  | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | Long-Term Planning | 2017-11-09 | 2018-01-22 | 2018-11-15 | 2019-01-25 | 2021-07-01 |  | X |  |  | 2019-06-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-3 | D.A.7.3. | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  |  | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 |  |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | D.A.7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and |  |  | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 |  |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | D.A.7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. |  |  | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 |  |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2019-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | No Parts for 1. |  | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2019-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-3 | 2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2019-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | No Parts for 2. |  | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2019-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-3 | 3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | No Parts for 3. |  | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-3 | 4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 4.1. | The study or studies shall include the following conditions: | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2020-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2020-01-01 | 2020-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2020-01-01 | 2020-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 6.1. | Be based on the effective GIC flow information provided in Requirement R5; | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 6.2. | Document assumptions used in the analysis; | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.1. | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP