Inactive | TPL | TPL-007 | TPL-007-3 | 7.3. | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2019-07-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2019-07-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2019-07-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2024-01-01 | 2024-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.1. | The study or studies shall include the following conditions: | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2023-01-01 | 2023-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2020-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2020-01-01 | 2020-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2020-01-01 | 2020-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | 10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 10.1. | Be based on the effective GIC flow information provided in Requirement R9; | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 10.2. | Document assumptions used in the analysis; | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2022-01-01 | 2022-01-01 | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | TPL | TPL-007 | TPL-007-3 | 11. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2021-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | No Parts for 11. |  | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2021-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000
Inactive | TPL | TPL-007 | TPL-007-3 | 12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M12. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2021-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | TPL | TPL-007 | TPL-007-3 | No Parts for 12. |  | M12. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | Long-Term Planning | 2019-02-07 | 2019-02-21 | 2019-02-21 | 2019-02-21 | 2021-07-01 |  | X |  |  | 2020-09-30 | Filing/Order Docket No. RM18-8-000
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.3. | Include a timetable, subject to revision by the responsible entity in Part D.A.11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.4. | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.11.3. The revised CAP shall document the following: |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.4.2. | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures if applicable; and |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.4.3. | Updated timetable for implementing the selected actions in Part 11.1. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.11.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.3. | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.4. | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.7.3. The revised CAP shall document the following: |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.4.2. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable; and |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.4.3. | Updated timetable for implementing the selected actions in Part 7.1 |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | D.A.7.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  |  | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [5 empty] | PA | PC | [7 empty] | TO |  | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | No Parts for 1. |  | Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | No Parts for 2. |  | Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 | Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | No Parts for 3. |  | Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4.1. | The study or studies shall include the following conditions: | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 6.1. | Be based on the effective GIC flow information provided in Requirement R5; | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 6.2. | Document assumptions used in the analysis; | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.1. | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.3. | Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.4. | Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.4.2. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.4.3. | Updated timetable for implementing the selected actions in Part 7.1. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 7.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8.1. | The study or studies shall include the following conditions: | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8.3. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 8.3.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2023-01-01 | 2023-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2020-10-01 | 2020-10-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 10.1. | Be based on the effective GIC flow information provided in Requirement R9; | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 10.2. | Document assumptions used in the analysis; | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2022-01-01 | 2022-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11. | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.2. | Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.3. | Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.4. | Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.4.2. | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.4.3. | Updated timetable for implementing the selected actions in Part 11.1. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 11.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R12. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2021-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | No Parts for 12. |  | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R12. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2021-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | 13. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R13. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2021-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007 | TPL-007-4 | No Parts for 13. |  | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R13. | Long-Term Planning | 2020-02-06 | 2020-02-07 | 2020-03-19 | 2020-03-19 | 2021-07-01 |  | X |  |  |  | Filing/Order Docket No. RD20-3-000 This Variance shall be applicable in those Canadian jurisdictions where the Variance has been approved for use by the applicable governmental authority or has otherwise become effective in t
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 1. | Each Planning Coordinator shall identify, in conjunction with its Transmission Planner(s), each entity’s individual and joint responsibilities for completing the Extreme Temperature Assessment, which shall include each of the responsibilities described in Requirements R2 through R11. Each responsible entity shall complete its responsibilities such that the Extreme Temperature Assessment is completed at least once every five calendar years. | M1. Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall provide dated documentation of each entity’s individual and joint responsibilities, such as meeting minutes, agreements, copies of procedures, or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for completing the Extreme Temperature Assessment, and that these responsibilities were completed such that the Extreme Temperature Assessment was completed once every five calendar years. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2026-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | No Parts for 1. |  | M1. Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall provide dated documentation of each entity’s individual and joint responsibilities, such as meeting minutes, agreements, copies of procedures, or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for completing the Extreme Temperature Assessment, and that these responsibilities were completed such that the Extreme Temperature Assessment was completed once every five calendar years. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2026-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 2. | Each Planning Coordinator shall identify the zone(s) to which the Planning Coordinator belongs to under Attachment 1 and shall coordinate with all Planning Coordinators within each of its identified zone(s), to identify one common extreme heat benchmark temperature event and one common extreme cold benchmark temperature event for each of its identified zone(s) when completing the Extreme Temperature Assessment. The benchmark temperature events shall be obtained from the benchmark library maintained by the ERO or developed by the Planning Coordinators. Each benchmark temperature event identified by the Planning Coordinators shall: | M2. Each Planning Coordinator shall have evidence in either electronic or hard copy format that it identified the zone(s) to which it belongs to, under Attachment 1, and that it coordinated with all other Planning Coordinators within each of its identified zone(s) to identify one common extreme heat benchmark temperature event and one common extreme cold benchmark temperature event meeting the criteria of Requirement R2 for each of their identified zone(s) when completing the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 2.1. | Consider no less than a 40-year period of temperature data ending no more than five years prior to the time the benchmark temperature events are selected; and | M2. Each Planning Coordinator shall have evidence in either electronic or hard copy format that it identified the zone(s) to which it belongs to, under Attachment 1, and that it coordinated with all other Planning Coordinators within each of its identified zone(s) to identify one common extreme heat benchmark temperature event and one common extreme cold benchmark temperature event meeting the criteria of Requirement R2 for each of their identified zone(s) when completing the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 2.2. | Represent one of the 20 most extreme temperature conditions based on the three-day rolling average of daily maximum (heat) or daily minimum (cold) temperature across the zone. | M2. Each Planning Coordinator shall have evidence in either electronic or hard copy format that it identified the zone(s) to which it belongs to, under Attachment 1, and that it coordinated with all other Planning Coordinators within each of its identified zone(s) to identify one common extreme heat benchmark temperature event and one common extreme cold benchmark temperature event meeting the criteria of Requirement R2 for each of their identified zone(s) when completing the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 3. | Each Planning Coordinator shall coordinate with all Planning Coordinators within each of its zone(s) identified in Requirement R2, to implement a process for developing benchmark planning cases for the Extreme Temperature Assessment that represent the benchmark temperature events selected in Requirement R2 and sensitivity cases to demonstrate the impact of changes to the basic assumptions used in the benchmark planning cases. This process shall include the following: | M3. Each Planning Coordinator shall have dated evidence that it implemented a process for coordinating the development of benchmark planning cases and sensitivity cases for the Extreme Temperature Assessment as specified in Requirement R3. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 3.1. | Selection of System models within the Long-Term Transmission Planning Horizon to form the basis for the benchmark planning cases. | M3. Each Planning Coordinator shall have dated evidence that it implemented a process for coordinating the development of benchmark planning cases and sensitivity cases for the Extreme Temperature Assessment as specified in Requirement R3. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 3.2. | Forecasted seasonal and temperature dependent adjustments for Load, generation, Transmission, and transfers within the zone. | M3. Each Planning Coordinator shall have dated evidence that it implemented a process for coordinating the development of benchmark planning cases and sensitivity cases for the Extreme Temperature Assessment as specified in Requirement R3. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 3.3. | Assumed seasonal and temperature dependent adjustments for Load, generation, Transmission, and transfers in areas outside the zone, as needed. | M3. Each Planning Coordinator shall have dated evidence that it implemented a process for coordinating the development of benchmark planning cases and sensitivity cases for the Extreme Temperature Assessment as specified in Requirement R3. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 3.4. | Identification of changes to at least one of the following conditions for sensitivity cases: generation, real and reactive forecasted Load, or transfers. | M3. Each Planning Coordinator shall have dated evidence that it implemented a process for coordinating the development of benchmark planning cases and sensitivity cases for the Extreme Temperature Assessment as specified in Requirement R3. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 4. | Each responsible entity, as identified in Requirement R1, shall use the process developed in Requirement R3 and data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, to develop the following and establish category P0 as the normal System condition in Table 1: | M4. Each responsible entity, as identified in Requirement R1, shall have dated evidence in either electronic or hard copy format that it developed benchmark planning cases and sensitivity cases in accordance with Requirement R4. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 4.1. | One common extreme heat and one common extreme cold benchmark planning case. | M4. Each responsible entity, as identified in Requirement R1, shall have dated evidence in either electronic or hard copy format that it developed benchmark planning cases and sensitivity cases in accordance with Requirement R4. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 4.2. | One common extreme heat and one common extreme cold sensitivity case. | M4. Each responsible entity, as identified in Requirement R1, shall have dated evidence in either electronic or hard copy format that it developed benchmark planning cases and sensitivity cases in accordance with Requirement R4. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 | 2028-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 5. | Each responsible entity, as identified in Requirement R1, shall have criteria for acceptable System steady state voltage limits and post-Contingency voltage deviations for completing the Extreme Temperature Assessment. | M5. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of the documentation, specifying the criteria for acceptable System steady state voltage limits and post-Contingency voltage deviations for completing the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | No Parts for 5. |  | M5. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of the documentation, specifying the criteria for acceptable System steady state voltage limits and post-Contingency voltage deviations for completing the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 6. | Each responsible entity, as identified in Requirement R1, shall define and document the criteria or methodology to be used in the Extreme Temperature Assessment to identify instability, uncontrolled separation, or Cascading within an Interconnection. | M6. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, specifying the criteria or methodology to be used in the Extreme Temperature Assessment to identify instability, uncontrolled separation, or Cascading within an Interconnection in accordance with Requirement R6. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | No Parts for 6. |  | M6. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, specifying the criteria or methodology to be used in the Extreme Temperature Assessment to identify instability, uncontrolled separation, or Cascading within an Interconnection in accordance with Requirement R6. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2028-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 7. | Each responsible entity, as identified in Requirement R1, shall identify the Contingencies for each category in Table 1 that are expected to produce more severe System impacts on its portion of the Bulk Electric System. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | M7. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of the Contingencies for each category in Table 1 that are expected to produce more severe System impacts on its portion of the Bulk Electric System along with supporting rationale. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | No Parts for 7. |  | M7. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of the Contingencies for each category in Table 1 that are expected to produce more severe System impacts on its portion of the Bulk Electric System along with supporting rationale. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 8. | Each responsible entity, as identified in Requirement R1, shall complete steady state and transient stability analyses in the Extreme Temperature Assessment using the Contingencies identified in Requirement R7, and shall document the assumptions and results. Steady state and transient stability analyses shall be performed for the following: | M8. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of the assumptions and results of the steady state and transient stability analyses completed in the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 8.1. | Benchmark planning cases developed in accordance with Requirement R4 Part 4.1. | M8. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of the assumptions and results of the steady state and transient stability analyses completed in the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 8.2. | Sensitivity cases developed in accordance with Requirement R4 Part 4.2. | M8. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of the assumptions and results of the steady state and transient stability analyses completed in the Extreme Temperature Assessment. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 9. | Each responsible entity, as identified in Requirement R1, shall develop a Corrective Action Plan(s) when the analysis of a benchmark planning case, in accordance with Requirement R8 Part 8.1, indicates its portion of the Bulk Electric System is unable to meet performance requirements for category P0 or P1 in Table 1. For each Corrective Action Plan, the responsible entity shall: | M9. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of each Corrective Action Plan developed in accordance with Requirement R9 when the analysis of a benchmark planning case indicates its portion of the Bulk Electric System is unable to meet performance requirements for category P0 or P1 in Table 1. Evidence shall include documentation of correspondence with applicable regulatory authorities or governing bodies responsible for retail electric service issues and any revision history. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 9.1. | Document alternative(s) considered when Non-Consequential Load Loss is utilized as an element of a Corrective Action Plan for a Table 1 P1 Contingency. | M9. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of each Corrective Action Plan developed in accordance with Requirement R9 when the analysis of a benchmark planning case indicates its portion of the Bulk Electric System is unable to meet performance requirements for category P0 or P1 in Table 1. Evidence shall include documentation of correspondence with applicable regulatory authorities or governing bodies responsible for retail electric service issues and any revision history. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 9.2. | Be permitted to utilize Non-Consequential Load Loss as an interim solution, which normally is not permitted for category P0 in Table 1 for situations that are beyond the control of the Planning Coordinator or Transmission Planner that prevent the implementation of a Corrective Action Plan in the required timeframe, provided that the responsible entity documents the situation causing the problem, alternatives evaluated, and takes actions to resolve the situation. | M9. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of each Corrective Action Plan developed in accordance with Requirement R9 when the analysis of a benchmark planning case indicates its portion of the Bulk Electric System is unable to meet performance requirements for category P0 or P1 in Table 1. Evidence shall include documentation of correspondence with applicable regulatory authorities or governing bodies responsible for retail electric service issues and any revision history. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 9.3. | Make its Corrective Action Plan available to, and solicit feedback from, applicable regulatory authorities or governing bodies responsible for retail electric service issues. | M9. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of each Corrective Action Plan developed in accordance with Requirement R9 when the analysis of a benchmark planning case indicates its portion of the Bulk Electric System is unable to meet performance requirements for category P0 or P1 in Table 1. Evidence shall include documentation of correspondence with applicable regulatory authorities or governing bodies responsible for retail electric service issues and any revision history. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 9.4. | Be permitted to have revisions to the Corrective Action Plan in subsequent Extreme Temperature Assessments, provided that the planned Bulk Electric System shall continue to meet the performance requirements of Table 1. | M9. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation, of each Corrective Action Plan developed in accordance with Requirement R9 when the analysis of a benchmark planning case indicates its portion of the Bulk Electric System is unable to meet performance requirements for category P0 or P1 in Table 1. Evidence shall include documentation of correspondence with applicable regulatory authorities or governing bodies responsible for retail electric service issues and any revision history. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 10. | Each responsible entity, as identified in Requirement R1, shall evaluate and document possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) if analyses conclude there could be instability, uncontrolled separation, or Cascading within an Interconnection, for the following: | M10. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation that it evaluated and documented possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts when the analyses conclude there could be instability, uncontrolled separation, or Cascading within an Interconnection for Table 1 P7 Contingencies in benchmark planning cases or categories P0, P1, or P7 in Table 1 in sensitivity cases. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 10.1. | Table 1 P7 Contingencies in benchmark planning cases analyzed in accordance with Requirement R8 Part 8.1. | M10. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation that it evaluated and documented possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts when the analyses conclude there could be instability, uncontrolled separation, or Cascading within an Interconnection for Table 1 P7 Contingencies in benchmark planning cases or categories P0, P1, or P7 in Table 1 in sensitivity cases. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 10.2. | Categories P0, P1, and P7 in Table 1 in sensitivity cases analyzed in accordance with Requirement R8 Part 8.2. | M10. Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as electronic or hard copies of documentation that it evaluated and documented possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts when the analyses conclude there could be instability, uncontrolled separation, or Cascading within an Interconnection for Table 1 P7 Contingencies in benchmark planning cases or categories P0, P1, or P7 in Table 1 in sensitivity cases. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 | 2030-04-01 | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | 11. | Each responsible entity, as identified in Requirement R1, shall provide its Extreme Temperature Assessment results within 60 calendar days of a request to any functional entity that has a reliability related need and submits a written request for the information. | M11. .Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as email notices, documentation of updated web pages, or postal receipts showing recipient, that it provided its Extreme Temperature Assessment to any functional entity who has a reliability need within 60 calendar days of a written request. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-008 | TPL-008-1 | No Parts for 11. |  | M11. .Each responsible entity, as identified in Requirement R1, shall provide dated evidence, such as email notices, documentation of updated web pages, or postal receipts showing recipient, that it provided its Extreme Temperature Assessment to any functional entity who has a reliability need within 60 calendar days of a written request. | Long-Term Planning | 2024-12-10 | 2024-12-17 | 2025-02-20 | 2025-02-20 | 2030-04-01 |  | X |  |  |  | Filing/Order Docket No. RD25-4-000 See the bottom of the TPL-008-1 Reliability Standards page for related documents
Inactive | VAR | VAR-001 | VAR-001-0 | 1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and MVAR flows within their individual areas and with the areas of neighboring Transmission Operators. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 2. | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 3. | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [12 empty] | PSE
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 4. | The Transmission Operator shall know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 5. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 6. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 7. | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | 7.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | 8. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-0 | 9. | Each Generator Operator shall provide information to its Transmission Operator on the status of all generation reactive power resources, including the status of voltage regulators and power system stabilizers. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | 9.1. | When a generator’s voltage regulator is out of service, the Generator Operator shall maintain the generator field excitation at a level to maintain Interconnection and generator stability. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-0 | 10. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-0 | No Parts for 10. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 VAR-001-0 was never enforceable
Inactive | VAR | VAR-001 | VAR-001-1 | 1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 1. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 2. | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 2. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 4. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 5. | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [12 empty] | PSE
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 5. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 7. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2007-01-01 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 8. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2007-01-01 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 9. | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2007-01-01 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2007-01-01 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | 10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2007-01-01 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 10. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2007-01-01 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 11. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1 | 12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1 | No Parts for 12. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-001 | VAR-001-1a | 1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 1. |  |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 2. | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 2. |  |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule 1 at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 4. |  |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 5. | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [12 empty] | PSE
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 5. |  |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 7. |  |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 8. |  |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 9. | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  |  | 2008-03-26 | [8 empty] | 2009-05-21 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | 10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  |  | 2008-03-26 |  |  |  | 2007-06-18 |  |  |  |  | 2011-09-30 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 10. |  |  |  | 2008-03-26 |  |  |  | 2007-06-18 |  |  |  |  | 2011-09-30 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  |  | 2008-03-26 |  |  |  | 2007-06-18 |  |  |  |  | 2011-09-30 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 11. |  |  |  | 2008-03-26 |  |  |  | 2007-06-18 |  |  |  |  | 2011-09-30 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-1a | 12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  |  | 2008-03-26 |  |  |  | 2007-06-18 |  |  |  |  | 2011-09-30 | FERC approved withdraw and remand of the interpretation | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-1a | No Parts for 12. |  |  |  | 2008-03-26 |  |  |  | 2007-06-18 |  |  |  |  | 2011-09-30 | FERC approved withdraw and remand of the interpretation
Inactive | VAR | VAR-001 | VAR-001-2 | 1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 1. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 2. | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 2. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 4. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 5. | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RD10-15-000 | [9 empty] | LSE |  |  | PSE
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 5. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-10-01 |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 7. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 8. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 9. | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2013-12-31 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | 10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2009-05-21 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 10. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2009-05-21 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2009-05-21 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 11. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2009-05-21 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-2 | 12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2009-05-21 | Filing/Order Docket No. RD10-15-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-2 | No Parts for 12. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2009-05-21 | Filing/Order Docket No. RD10-15-000
Inactive | VAR | VAR-001 | VAR-001-3 | E.A.13 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for E.A.13 |  |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | E.A.14 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for E.A.14 |  |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | E.A.15 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for E.A.15 |  |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | E.A.16 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for E.A.16 |  |  | Long-Term Planning | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | E.A.17 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for E.A.17 |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | E.A.18 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for E.A.18 |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 1. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 2. | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 2. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 | 2013-06-20 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 | 2013-06-20 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 4. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 5. | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RD13-6-000 | [9 empty] | LSE |  |  | PSE
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 5. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-01-21 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 | 2014-01-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 7. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 8. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 9. | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; and controllable load– to support its voltage under first Contingency conditions. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2014-01-01 | 2013-06-20 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | 10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 10. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 11. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-3 | 12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-3 | No Parts for 12. |  |  |  | 2012-05-09 | 2013-02-25 | 2013-06-20 | 2013-06-20 | 2013-06-20 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-6-000
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: •A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | M.E.A.13 Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for E.A.13. |  | M.E.A.13 Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. •The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for E.A.14. |  | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for E.A.15. |  | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.16. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for E.A.16. |  | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.17. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for E.A.17. |  | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.18. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-01-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.18.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-01-01 | 2014-08-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4 | E.A.18.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-01-01 | 2014-08-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4 | 1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-08-01 |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for 2. |  | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | 3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for 3. |  | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4 | 4. | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-08-01 |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-10-01 |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-10-01 |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-10-01 |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | 6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4 | No Parts for 6. |  | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2014-02-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for E.A.13. |  | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, email, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for E.A.14. |  | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, email, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for E.A.15. |  | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | Operations Planning, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.16. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for E.A.16. |  | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.17. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for E.A.17. |  | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.18. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.18.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | E.A.18.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for 2. |  | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | 3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for 3. |  | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.1 | 4. | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | 6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.1 | No Parts for 6. |  | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2014-02-06 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2014-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for E.A.13. |  | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for E.A.14. |  | The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for E.A.15. |  | Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.16. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for E.A.16. |  | The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2019-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.17. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for E.A.17. |  | The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.18. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.18.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 | 2017-09-26 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | E.A.18.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 | 2017-09-26 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for 2. |  | Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | 3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for 3. |  | Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-001 | VAR-001-4.2 | 4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | 6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000 | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-4.2 | No Parts for 6. |  | The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2015-11-13 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-7-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | Operations Planning, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for E.A.13. |  | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | Operations Planning, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | Operations Planning, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for E.A.14. |  | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | Operations Planning, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.15. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for E.A.15. |  | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.16. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for E.A.16. |  | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2018-10-15 | [5 empty] | Filing/Order Docket No. RD18-8-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.17. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | Long-Term Planning, Real-Time Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.17.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | Long-Term Planning, Real-Time Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2017-09-26 | 2018-10-15 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | E.A.17.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | Long-Term Planning, Real-Time Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2017-09-26 | 2018-10-15 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | 2018-10-15 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for 2. |  | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | Operations Planning, Real-Time Operations, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for 3. |  | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | 2019-01-01 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 5.1 . | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | 2019-01-01 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 5.2 . | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | 2019-01-01 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 5.3 . | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | 2019-01-01 |  |  |  |  | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | 6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001 | VAR-001-5 | No Parts for 6. |  | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2018-08-16 | 2018-09-06 | 2018-10-15 | 2018-10-15 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RD18-8-000
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | Operations Planning, Same-Day Operations | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for E.A.13. |  | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | Operations Planning, Same-Day Operations | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | Operations Planning, Same-Day Operations | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for E.A.14. |  | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | Operations Planning, Same-Day Operations | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.15. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for E.A.15. |  | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.16. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for E.A.16. |  | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.17. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | Real-Time Operations | 2019-05-09 | 2019-06-07 |  |  | 2019-01-01 |  |  |  |  | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.17.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | Real-Time Operations | 2019-05-09 | 2019-06-07 |  |  | 2019-01-01 |  |  |  |  | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-6 | E.A.17.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | Real-Time Operations | 2019-05-09 | 2019-06-07 |  |  | 2019-01-01 |  |  |  |  | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [6 empty] | GOP
Inactive | VAR | VAR-001 | VAR-001-6 | 1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. . | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. . | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 2. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for 2. |  | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | 3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for 3. |  | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-001 | VAR-001-6 | 4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviationsfrom the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | 6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020. | [20 empty] | TOP
Inactive | VAR | VAR-001 | VAR-001-6 | No Parts for 6. |  | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2020-05-14 | Filing/Order Docket No. RM19-16-000 Standard withdrawn on 5/14/2020.
Inactive | VAR | VAR-002 | VAR-002-1 | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | No Parts for 1. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | VAR | VAR-002 | VAR-002-1 | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings. [1] as directed by the Transmission Operator |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | 2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-08-02 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | 2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-08-02 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | 3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | 3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | 3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1 | 4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 4.1.1. | Tap settings. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-08-02 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 4.1.2. | Available fixed tap ranges. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-08-02 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 4.1.3. | Impedance data. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-08-02 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-08-02 | 2007-08-02 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1 | 5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | No Parts for 1. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000
Inactive | VAR | VAR-002 | VAR-002-1.1a | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1a | 4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 4.1.1. | Tap settings. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 4.1.2. | Available fixed tap ranges. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 4.1.3. | Impedance data. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2010-09-15 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2007-08-02 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RD09-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1a | 5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2007-08-02 | 2009-05-13 |  |  |  | 2008-08-26 | Filing/Order Docket No. RD09-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | No Parts for 1. |  |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000
Inactive | VAR | VAR-002 | VAR-002-1.1b | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1.1b | 4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 4.1.1. | Tap settings. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 4.1.2. | Available fixed tap ranges. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 4.1.3. | Impedance data. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2010-09-16 | 2010-09-16 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2009-05-13 |  |  |  |  | 2010-09-15 | Filing/Order Docket No. RM09-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1.1b | 5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  |  | 2009-02-10 | 2009-03-05 | 2010-09-16 | 2010-09-16 | 2009-05-13 | 2010-09-16 |  |  |  | 2010-09-15 | Filing/Order Docket No. RM09-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | No Parts for 1. |  |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000
Inactive | VAR | VAR-002 | VAR-002-1a | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings [see footnote in standard]) as directed by the Transmission Operator. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-1a | 4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 4.1.1. | Tap settings. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 4.1.2. | Available fixed tap ranges. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 4.1.3. | Impedance data. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2010-09-16 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM08-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-1a | 5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  |  | 2007-08-01 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2010-09-16 | 2008-08-27 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM08-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following: -That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or -That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | No Parts for 1. |  |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000
Inactive | VAR | VAR-002 | VAR-002-2b | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings as directed by the Transmission Operator. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-2b | 4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 4.1.1. | Tap settings. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 4.1.2. | Available fixed tap ranges. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 4.1.3. | Impedance data. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2013-07-01 | 2013-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RD13-2-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-2b | 5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  |  | 2012-08-16 | 2012-11-21 | 2013-04-16 | 2013-07-01 | 2008-08-27 | 2013-07-01 |  |  |  | 2009-05-12 | Filing/Order Docket No. RD13-2-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | No Parts for 1. |  | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-002 | VAR-002-3 | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | 2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-10-01 |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | 2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-10-01 |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | 2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 | 2014-08-01 |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | 3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | No Parts for 3. |  |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-002 | VAR-002-3 | 4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. |  | Long-Term Planning | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-3 | No Parts for 4. |  |  | Long-Term Planning | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000
Inactive | VAR | VAR-002 | VAR-002-3 | 5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2013-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-3 | 5.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2013-07-01 | 2014-08-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-3 | 5.1.1. | Tap settings. |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2013-07-01 | 2014-10-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-3 | 5.1.2. | Available fixed tap ranges. |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2013-07-01 | 2014-10-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-3 | 5.1.3. | Impedance data. |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2013-07-01 | 2014-10-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-3 | 6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-3 | 6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  |  | 2014-05-06 | 2014-06-09 | 2014-08-01 | 2014-08-01 | 2014-08-01 | 2014-08-01 |  |  |  | 2015-05-28 | Filing/Order Docket No. RD14-11-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | No Parts for 1. |  | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000
Inactive | VAR | VAR-002 | VAR-002-4 | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | 2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | 2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | 2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | 3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | No Parts for 3. |  | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000
Inactive | VAR | VAR-002 | VAR-002-4 | 4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 | [6 empty] | GOP
Inactive | VAR | VAR-002 | VAR-002-4 | No Parts for 4. |  | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000
Inactive | VAR | VAR-002 | VAR-002-4 | 5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 5.1. | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 5.1.1. | Tap settings. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 5.1.2. | Available fixed tap ranges. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 5.1.3. | Impedance data. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2015-05-29 | 2015-05-29 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2014-10-01 |  |  |  |  | 2015-05-28 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-4 | 6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | Real-Time Operations | 2014-11-13 | 2015-02-06 | 2015-05-29 | 2015-05-29 | 2014-10-01 | 2015-05-29 |  |  |  | 2015-05-28 | Filing/Order Docket No. RD15-3-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000 | [7 empty] | GOP-2
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | No Parts for 1. |  | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000 | [7 empty] | GOP-2
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 2.1 . | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 2.2 . | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000 | [7 empty] | GOP-2
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | No Parts for 3. |  | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000 | [7 empty] | GOP-2
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | No Parts for 4. |  | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO | GO-2
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 5.1. | For generator step-up and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: (Footnote: For dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies only to those transformers that have at least one winding at a voltage of 100 kV or above.) | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 5.1.1. | Tap settings. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 5.1.2. | Available fixed tap ranges. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 5.1.3. | Impedance data. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | [5 empty] | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO | GO-2
Mandatory Subject to Enforcement | VAR | VAR-002 | VAR-002-4.1 | 6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1. | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [Time Horizon: Operations Assessment] |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.1. | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.10. | If AVR exhibits instability due to operation of a Load Tap Changer (LTC) transformer in the area, the Transmission Operator may authorize the Generator Operator to operate the excitation system in modes other than automatic voltage control until the system configuration changes. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.3. | AVR exhibits instability due to abnormal system configuration. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.4. | Due to component failure, the AVR may be out of service up to 60 consecutive days for repair per incident. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.5. | Due to a component failure, the AVR may be out of service up to one year provided the Generator Operator or Transmission Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.6. | Due to a component failure, the AVR may be out of service up to 24 months provided the Generator Operator or Transmission Operator submits documentation identifying the need for time for excitation system replacement (replace the AVR, limiters, and controls but not necessarily the power source and power bridge) and to schedule an outage. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.7. | The synchronous generator or synchronous condenser has not achieved Commercial Operation. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.8. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 1.9. | The Reliability Coordinator directs Transmission Operator to operate the synchronous condenser, and the AVR is unavailable for service. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | 2. | Generator Operators and Transmission Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.10. [Time Horizon: Operations Assessment] |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-1 | No Parts for 2. |  |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1. | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [See Standard for additional information.] | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 |  |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.1. | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.10. | If AVR exhibits instability due to operation of a Load Tap Changer (LTC) transformer in the area, the Transmission Operator may authorize the Generator Operator to operate the excitation system in modes other than automatic voltage control until the system configuration changes. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.3. | AVR exhibits instability due to abnormal system configuration. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.4. | Due to component failure, the AVR may be out of service up to 60 consecutive days for repair per incident. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.5. | Due to a component failure, the AVR may be out of service up to one year provided the Generator Operator or Transmission Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.6. | Due to a component failure, the AVR may be out of service up to 24 months provided the Generator Operator or Transmission Operator submits documentation identifying the need for time for excitation system replacement (replace the AVR, limiters, and controls but not necessarily the power source and power bridge) and to schedule an outage. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.7. | The synchronous generator or synchronous condenser has not achieved Commercial Operation. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.8. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-002 | VAR-002-WECC-2 | 1.9. | The Reliability Coordinator directs Transmission Operator to operate the synchronous condenser, and the AVR is unavailable for service. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-03-03 |  |  |  | 2018-09-05 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1. | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [Time Horizon: Operations Assessment] |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.1. | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.10. | Due to a component failure, the PSS may be out of service up to 24 months provided the Generator Operator submits documentation identifying the need for time for PSS replacement and to schedule an outage. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.11. | The synchronous generator has not achieved Commercial Operation. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.12. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the PSS is unavailable for service. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.3. | PSS exhibits instability due to abnormal system configuration. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.4. | Unit is operating in the synchronous condenser mode (very near zero real power level). |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.5. | Unit is generating less power than its design limit for effective PSS operation. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.6. | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.7. | The generator AVR is not in service. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.8. | Due to component failure, the PSS may be out of service up to 60 consecutive days for repair per incident. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 1.9. | Due to a component failure, the PSS may be out of service up to one year provided the Generator Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-06-27 |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | 2. | Generator Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.12. [Time Horizon: Operations Assessment] |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-1 | No Parts for 2. |  |  |  | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RM09-9-000
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1. | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [See Standard for additional information.] | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 |  |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.1. | The synchronous generator operates for less than five percent of all hours during any calendar quarter. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.10. | Due to a component failure, the PSS may be out of service up to 24 months provided the Generator Operator submits documentation identifying the need for time for PSS replacement and to schedule an outage. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.11. | The synchronous generator has not achieved Commercial Operation. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.12. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the PSS is unavailable for service. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.3. | PSS exhibits instability due to abnormal system configuration. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.4. | Unit is operating in the synchronous condenser mode (very near zero real power level). | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.5. | Unit is generating less power than its design limit for effective PSS operation. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.6. | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.7. | The generator AVR is not in service. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.8. | Due to component failure, the PSS may be out of service up to 60 consecutive days for repair per incident. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-2 | 1.9. | Due to a component failure, the PSS may be out of service up to one year provided the Generator Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | Operations Assessment | 2014-11-13 | 2014-12-15 | 2015-03-03 | 2015-03-03 | 2015-04-01 | 2015-04-01 |  |  |  | 2017-06-30 | Filing/Order Docket No. RD15-1-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 1. | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date, or; • Any changes to the PSS operating specifications. | M1. Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | No Parts for 1. |  | M1. Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 2. | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances during which the PSS was not in service for periods in excess of 30 minutes. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | No Parts for 2. |  | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances during which the PSS was not in service for periods in excess of 30 minutes. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 3. | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 3.1. | PSS shall be set to provide the measured, simulated, or calculated compensated VT/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 | 2017-04-28 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 3.2. | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 | 2017-04-28 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 3.3. | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 | 2017-04-28 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 3.4. | PSS washout time constant shall be no greater than 30 seconds. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 | 2017-04-28 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 3.5. | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-07-01 | 2017-07-01 |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 4. | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-04-28 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | No Parts for 4. |  | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-04-28 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | 5. | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. | M5. Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-04-28 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3 | No Parts for 5. |  | M5. Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | Operations Assessment | 2017-02-09 | 2017-03-10 | 2017-04-28 | 2017-04-28 | 2017-04-28 |  |  |  |  | 2017-09-25 | Filing/Order Docket No. RD17-5-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 1. | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date; or • Any changes to the PSS operating specifications. | M1. Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | Operations Planning, Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | No Parts for 1. |  | M1. Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | Operations Planning, Real-Time Operations | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 2. | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 | [6 empty] | GOP
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | No Parts for 2. |  | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 3. | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 3.1. | PSS shall be set to provide the measured, simulated, or calculated compensated Vt/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 3.2. | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 3.3. | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 3.4. | PSS washout time constant shall be no greater than 30 seconds. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 3.5 . | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 4. | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | No Parts for 4. |  | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | 5. | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. | M5. Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000 |  |  |  |  | GO
Inactive | VAR | VAR-501 | VAR-501-WECC-3.1 | No Parts for 5. |  | M5. Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | Operations Assessment | 2017-08-10 | 2017-08-18 | 2017-09-26 | 2017-09-26 | 2017-09-26 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD17-7-000
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 1. | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date; or • Any changes to the PSS operating specifications. | M1. Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | Long-Term Planning | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | No Parts for 1. |  | M1. Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | Long-Term Planning | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 2. | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator • A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances during which the PSS was not in service for periods in excess of 30 minutes. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | No Parts for 2. |  | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances during which the PSS was not in service for periods in excess of 30 minutes. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 3. | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below | R3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 3.1. | PSS shall be set to provide the measured, simulated, or calculated compensated Vt/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. | R3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 3.2. | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. | R3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 3.3. | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. | R3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 3.4. | PSS washout time constant shall be no greater than 30 seconds. | R3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 3.5. | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. | R3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 4. | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. The first bullet of Requirement R4 only applies to equipment on its initial (first energization) connection to the BES. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | No Parts for 4. |  | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. The first bullet of Requirement R4 only applies to equipment on its initial (first energization) connection to the BES. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | 5. | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. | M5. Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | VAR | VAR-501 | VAR-501-WECC-4 | No Parts for 5. |  | M5. Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | Operations Assessment | 2023-12-12 | 2023-12-15 | 2024-01-30 | 2024-01-30 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD24-2-000
Inactive | VAR | VAR-STD | VAR-STD-002a-1 | W1. | Automatic voltage control equipment on synchronous generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, with outages coordinated to minimize the number out of service at any one time. All synchronous generators with automatic voltage control equipment shall normally be operated in voltage control mode and set to respond effectively to voltage deviations. (Source: WECC Criterion) |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000 | [6 empty] | GOP
Inactive | VAR | VAR-STD | VAR-STD-002a-1 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000
Inactive | VAR | VAR-STD | VAR-STD-002b-1 | W1. | Power System Stabilizers on generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, and shall be properly tuned in accordance with WECC requirements. (Source: WECC Criterion) |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000 | [6 empty] | GOP
Inactive | VAR | VAR-STD | VAR-STD-002b-1 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RR07-_-000