## US Effective Date Status - Func
Status | Family | Standard | Standard Version | Requirement / Part | Requirement Text | Measure | Time Horizons | Board Adoption Date of Standard | Filing Date of Standard | Regulatory Approval Order Issuance Date | Regulatory Order Effective Date | Effective Date of Requirement | Effective Date of Part | Phased-In Compliance | Additional Effective Date Details Requirement | Additional Effective Date Details Part | Inactive Date of Requirement / Part | Public Notes | BA | DP | DP-UFLS | FRSG | GO | GO-2 | GOP | GOP-2 | IA | LSE | PA | PC | PSE | RC | RE | RP | RRO | RRSG | RSG | TO | TOP | TP | TSP
Inactive | BAL | BAL-001 | BAL-001-0 | 1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. See Standard for Formula |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 | BA
Inactive | BAL | BAL-001 | BAL-001-0 | No Parts for 1. |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. See Standard for Formula |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1
Inactive | BAL | BAL-001 | BAL-001-0 | 2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE A compliance percentage is calculated as follows: See Standard for formula |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 | BA
Inactive | BAL | BAL-001 | BAL-001-0 | No Parts for 2. |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE A compliance percentage is calculated as follows: See Standard for formula |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1
Inactive | BAL | BAL-001 | BAL-001-0 | 3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 | BA
Inactive | BAL | BAL-001 | BAL-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1
Inactive | BAL | BAL-001 | BAL-001-0 | 4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 | BA
Inactive | BAL | BAL-001 | BAL-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 WECC Request for Interpretation of BAL-001-0, Requirement 1
Inactive | BAL | BAL-001 | BAL-001-0.1a | 1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. · IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-001 | BAL-001-0.1a | No Parts for 1. |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-001 | BAL-001-0.1a | 2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-001 | BAL-001-0.1a | No Parts for 2. |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-001 | BAL-001-0.1a | 3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-001 | BAL-001-0.1a | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-001 | BAL-001-0.1a | 4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-001 | BAL-001-0.1a | No Parts for 4. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-001 | BAL-001-0a | 1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See standard for equation. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change | BA
Inactive | BAL | BAL-001 | BAL-001-0a | No Parts for 1. |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change
Inactive | BAL | BAL-001 | BAL-001-0a | 2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See standard for formula. E10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, e10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change | BA
Inactive | BAL | BAL-001 | BAL-001-0a | No Parts for 2. |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change
Inactive | BAL | BAL-001 | BAL-001-0a | 3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement M1 (i.e., Control Performance Standard 1 or CPS1) and Requirement M2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change | BA
Inactive | BAL | BAL-001 | BAL-001-0a | No Parts for 3. |  |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change
Inactive | BAL | BAL-001 | BAL-001-0a | 4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change | BA
Inactive | BAL | BAL-001 | BAL-001-0a | No Parts for 4. |  |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 WECC Request for Interpretation of BAL-001-0, Requirement 1 and Errata change
Inactive | BAL | BAL-001 | BAL-001-1 | E.B.1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit e-1-2 is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee.(please see standard for formulas) | M.E.B.1. Each Balancing Authority shall achieve, as a minimum, Requirement E.B.1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement E.B.1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | Real-Time Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for E.B.1. |  | M.E.B.1. Each Balancing Authority shall achieve, as a minimum, Requirement E.B.1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement E.B.1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | Real-Time Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Inactive | BAL | BAL-001 | BAL-001-1 | E.B.2. | Each Balancing Authority shall limit the absolute value of I-ATEC, the Automatic Time Error Correction term as follows:(please see standard for formula) | M.E.B.2. Forms of acceptable evidence for Requirement E.B.2 may include, but are not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | Real-Time Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for E.B.2. |  | M.E.B.2. Forms of acceptable evidence for Requirement E.B.2 may include, but are not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | Real-Time Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Inactive | BAL | BAL-001 | BAL-001-1 | E.B.3. | Each Balancing Authority shall set L-max within the limits as follows:(please see standard for formula) | M.E.B.3. Forms of acceptable evidence for Requirement E.B.3 may include, but is not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | Operations Planning | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for E.B.3. |  | M.E.B.3. Forms of acceptable evidence for Requirement E.B.3 may include, but is not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | Operations Planning | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Inactive | BAL | BAL-001 | BAL-001-1 | 1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas) The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: (See standard for formula) where:E1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas) The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for 1. |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: (See standard for formula) where:E1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas) The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Inactive | BAL | BAL-001 | BAL-001-1 | 2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas) ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas) The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for 2. |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas) The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Inactive | BAL | BAL-001 | BAL-001-1 | 3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for 3. |  |  |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Inactive | BAL | BAL-001 | BAL-001-1 | 4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000 | BA
Inactive | BAL | BAL-001 | BAL-001-1 | No Parts for 4. |  |  |  | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No, RD13-11-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-2 | 1. | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | Real-Time Operations | 2013-08-15 | 2014-04-02 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-10-000 | BA | [16 empty] | RRSG | RSG
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-2 | No Parts for 1. |  | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | Real-Time Operations | 2013-08-15 | 2014-04-02 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-10-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-2 | 2. | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | Real-Time Operations | 2013-08-15 | 2014-04-02 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-10-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-2 | No Parts for 2. |  | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | Real-Time Operations | 2013-08-15 | 2014-04-02 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-10-000
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 1. | The BA shall identify Frequency Measurable Events (FMEs), and within 14 calendar days after each FME the BA shall notify the Compliance Enforcement Authority and make FME information (time of FME (t(0)), pre-perturbation average frequency, post- perturbation average frequency) publicly available. | M1. The BA shall have evidence it reported each FME to the Compliance Enforcement Authority and that it made FME information publicly available within 14 calendar days after the FME as required in Requirement R1. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | No Parts for 1. |  | M1. The BA shall have evidence it reported each FME to the Compliance Enforcement Authority and that it made FME information publicly available within 14 calendar days after the FME as required in Requirement R1. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes.
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 2. | The BA shall calculate the Primary Frequency Response of each generating unit/generating facility in accordance with this standard and the Primary Frequency Response Reference Document. This calculation shall provide a 12-month rolling average of initial and sustained Primary Frequency Response performance. This calculation shall be completed each month for the preceding 12 calendar months. [Please see the standard for more information] | M2. The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 2.1. | The performance of a combined cycle facility will be determined using an expected performance droop of 5.78%. | M2. The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 2.2. | The calculation results shall be submitted to the Compliance Enforcement Authority and made available to the GO by the end of the month in which they were completed. | M2. The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 2.3. | If a generating unit/generating facility has not participated in a minimum of (8) eight FMEs in a 12-month period, its performance shall be based on a rolling eight FME average response. | M2. The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 3. | The BA shall determine the Interconnection minimum Frequency Response (IMFR) in December of each year for the following year, and make the IMFR, the methodology for calculation and the criteria for determination of the IMFR publicly available. | M3. The BA shall demonstrate that the IMFR was determined in December of each year per Requirement R3. The BA shall demonstrate that the IMFR, the methodology for calculation and the criteria for determination of the IMFR are publicly available. | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | No Parts for 3. |  | M3. The BA shall demonstrate that the IMFR was determined in December of each year per Requirement R3. The BA shall demonstrate that the IMFR, the methodology for calculation and the criteria for determination of the IMFR are publicly available. | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes.
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 4. | After each calendar month in which one or more FMEs occurs, the BA shall determine and make publicly available the Interconnection’s combined Frequency Response performance for a rolling average of the last six (6) FMEs by the end of the following calendar month. | M4. The BA shall provide evidence that the rolling average of the Interconnection’s combined Frequency Response performance for the last six (6) FMEs was calculated and made public per Requirement R4. | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | No Parts for 4. |  | M4. The BA shall provide evidence that the rolling average of the Interconnection’s combined Frequency Response performance for the last six (6) FMEs was calculated and made public per Requirement R4. | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes.
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 5. | Following any FME that causes the Interconnection’s six-FME rolling average combined Frequency Response performance to be less than the IMFR, the BA shall direct any necessary actions to improve Frequency Response, which may include, but are not limited to, directing adjustment of Governor deadband and/or droop settings. | M5. The BA shall provide evidence that actions were taken to improve the Interconnection’s Frequency Response if the Interconnection’s six-FME rolling average combined Frequency Response performance was less than the IMFR, per Requirement R5. | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | No Parts for 5. |  | M5. The BA shall provide evidence that actions were taken to improve the Interconnection’s Frequency Response if the Interconnection’s six-FME rolling average combined Frequency Response performance was less than the IMFR, per Requirement R5. | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes.
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 6. | Each GO shall set its Governor parameters as follows: [Please see the standard for more information] | M6. Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 6.1. | Limit Governor deadbands within those listed in Table 6.1, unless directed otherwise by the BA. (see standard for table) | M6. Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 6.2. | Limit Governor droop settings such that they do not exceed those listed in Table 6.2, unless directed otherwise by the BA. (see standard for table) | M6. Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 6.3. | For digital and electronic Governors, once frequency deviation has exceeded the Governor deadband from 60.000 Hz, the Governor setting shall follow the slope derived from the formula below.(see standard for formula) where MWGCS is the maximum megawatt control range of the Governor control system. For mechanical Governors, droop will be proportional from the deadband by design. | M6. Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | Operations Planning | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 7. | Each GO shall operate each generating unit/generating facility that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit/generating facility is online and released for dispatch, unless the GO has a valid reason for operating with the Governor not in service and the GOP has been notified that the Governor is not in service. | M7. Each GO shall have evidence that it notified the GOP as soon as practical each time it discovered a Governor not in service when the generating unit/generating facility was online and released for dispatch. Evidence may include but not be limited to: operator logs, voice logs, or electronic communications. | Real-Time Operations | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | No Parts for 7. |  | M7. Each GO shall have evidence that it notified the GOP as soon as practical each time it discovered a Governor not in service when the generating unit/generating facility was online and released for dispatch. Evidence may include but not be limited to: operator logs, voice logs, or electronic communications. | Real-Time Operations | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes.
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 8. | Each GOP shall notify the BA as soon as practical but within 30 minutes of the discovery of a status change (in service, out of service) of a Governor. | M8. Each GOP shall have evidence that it notified the BA within 30 minutes of each discovery of a status change (in service, out of service) of a Governor. | Real-Time Operations | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | No Parts for 8. |  | M8. Each GOP shall have evidence that it notified the BA within 30 minutes of each discovery of a status change (in service, out of service) of a Governor. | Real-Time Operations | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes.
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 9. | Each GO shall meet a minimum 12-month rolling average initial Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | M9. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 9.1. | The initial Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the initial measurement period following the FME. | M9. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 9.2. | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight-FME average. | M9. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 9.3. | A generating unit/generating facility’s initial Primary Frequency Response performance during an FME may be excluded from the rolling average calculation due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include: • Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, pulverizers, and forced draft fans); • Data telemetry failure. The Compliance Enforcement Authority may request raw data from the GO as a substitute. | M9. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-04-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. |  |  |  |  | GO
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 10. | Each GO shall meet a minimum 12-month rolling average sustained Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | M10. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 10.1. | The sustained Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the sustained measurement period following the FME. | M10. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. |  |  |  |  | GO
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 10.2. | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight- FME average. | M10. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Inactive | BAL | BAL-001 | BAL-001-TRE-1 | 10.3. | A generating unit/generating facility’s sustained Primary Frequency Response performance during an FME may be excluded from the rolling average calculation due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include: Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, pulverizers, and forced draft fans); Data telemetry failure. The Compliance Enforcement Authority may request raw data from the GO as a substitute. | M10. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | Operations Assessment | 2013-08-15 | 2013-09-18 | 2014-01-16 | 2014-01-16 | 2014-04-01 | 2014-01-16 |  |  |  | 2020-06-30 | Filing/Order Docket No. ​RD13-12-000​ ​ Refer to the implementation plan for specific compliance dates and timeframes. | BA |  |  |  | GO |  | GOP
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 1. | The Balancing Authority shall identify Frequency Measurable Events (FMEs), and within 14 calendar days after each FME the Balancing Authority shall notify the Compliance Enforcement Authority and make FME information (time of FME (t(0)), pre-perturbation average frequency, post- perturbation average frequency) publicly available. | M1. The Balancing Authority shall have evidence it reported each FME to the Compliance Enforcement Authority and that it made FME information publicly available within 14 calendar days after the FME as required in Requirement R1. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | No Parts for 1. |  | M1. The Balancing Authority shall have evidence it reported each FME to the Compliance Enforcement Authority and that it made FME information publicly available within 14 calendar days after the FME as required in Requirement R1. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 2. | The Balancing Authority shall calculate the Primary Frequency Response of each generating unit/generating facility in accordance with this standard and the Primary Frequency Response Reference Document. This calculation shall provide a 12-month rolling average of initial and sustained Primary Frequency Response performance. This calculation shall be completed each month for the preceding 12 calendar months. The Primary Frequency Response Reference Document contains the calculations that the Balancing Authority will use to determine Primary Frequency Response performance of generating units/generating facilities. This reference document is a Texas RE-controlled document that is subject to revision by the Texas RE Board of Directors. | M2. The Balancing Authority shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 2.1. | The performance of a combined cycle facility will be determined using an expected performance droop of 5.78%., | M2. The Balancing Authority shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 2.2. | The calculation results shall be submitted to the Compliance Enforcement Authority and made available to the Generator Owner by the end of the month in which they were completed. | M2. The Balancing Authority shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 2.3. | If a generating unit/generating facility has not participated in a minimum of (8) eight FMEs in a 12-month period, its performance shall be based on a rolling eight FME average response. | M2. The Balancing Authority shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 3. | The Balancing Authority shall determine the Interconnection minimum Frequency Response (IMFR) in December of each year for the following year, and make the IMFR, the methodology for calculation and the criteria for determination of the IMFR publicly available. | M3. The Balancing Authority shall demonstrate that the IMFR was determined in December of each year per per Requirement R3. The Balancing Authority shall demonstrate that the IMFR, the methodology for calculation and the criteria for determination of the IMFR are publicly available. | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | No Parts for 3. |  | M3. The Balancing Authority shall demonstrate that the IMFR was determined in December of each year per per Requirement R3. The Balancing Authority shall demonstrate that the IMFR, the methodology for calculation and the criteria for determination of the IMFR are publicly available. | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 4. | After each calendar month in which one or more FMEs occurs, the Balancing Authority shall determine and make publicly available the Interconnection’s combined Frequency Response performance for a rolling average of the last six (6) FMEs by the end of the following calendar month. | M4. The Balancing Authority shall provide evidence that the rolling average of the Interconnection’s combined Frequency Response performance for the last six (6) FMEs was calculated and made public per Requirement R4. | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | No Parts for 4. |  | M4. The Balancing Authority shall provide evidence that the rolling average of the Interconnection’s combined Frequency Response performance for the last six (6) FMEs was calculated and made public per Requirement R4. | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 5. | Following any FME that causes the Interconnection’s six-FME rolling average combined Frequency Response performance to be less than the IMFR, the Balancing Authority shall direct any necessary actions to improve Frequency Response, which may include, but are not limited to, directing adjustment of Governor deadband and/or droop settings. | M5. The Balancing Authority shall provide evidence that actions were taken to improve the Interconnection’s Frequency Response if the Interconnection’s six-FME rolling average combined Frequency Response performance was less than the IMFR, per Requirement R5. | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | No Parts for 5. |  | M5. The Balancing Authority shall provide evidence that actions were taken to improve the Interconnection’s Frequency Response if the Interconnection’s six-FME rolling average combined Frequency Response performance was less than the IMFR, per Requirement R5. | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 6. | Each Generator Owner shall set its Governor parameters as follows: [Please see the standard for more information] | M6. Each Generator Owner shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to:  Governor test reports  Governor setting sheets  Performance monitoring reports | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO | GO-2
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 6.1. | Limit Governor deadbands within those listed in Table 6.1, unless directed otherwise by the Balancing Authority. (see standard for table) | M6. Each Generator Owner shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to:  Governor test reports  Governor setting sheets  Performance monitoring reports | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 6.2. | 6.2. Limit Governor droop settings such that they do not exceed those listed in Table 6.2, unless directed otherwise by the Balancing Authority. (see standard for table) | M6. Each Generator Owner shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to:  Governor test reports  Governor setting sheets  Performance monitoring reports | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 6.3. | For digital and electronic Governors, once frequency deviation has exceeded the Governor deadband from 60.000 Hz, the Governor setting shall follow the slope derived from the formula below.(see standard for formula) where MWGCS is the maximum megawatt control range of the Governor control system. For mechanical Governors, droop will be proportional from the deadband by design. | M6. Each Generator Owner shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to:  Governor test reports  Governor setting sheets  Performance monitoring reports | Operations Planning | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 7. | Each Generator Owner shall operate each generating unit/generating facility that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit/generating facility is online and released for dispatch, unless the Generator Owner has a valid reason for operating with the Governor not in service and the Generator Operator has been notified that the Governor is not in service. | M7. Each Generator Owner shall have evidence that it notified the Generator Operator as soon as practical each time it discovered a Governor not in service when the generating unit/generating facility was online and released for dispatch. Evidence may include but not be limited to: operator logs, voice logs, or electronic communications. | Real-Time Operations | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO | GO-2
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | No Parts for 7. |  | M7. Each Generator Owner shall have evidence that it notified the Generator Operator as soon as practical each time it discovered a Governor not in service when the generating unit/generating facility was online and released for dispatch. Evidence may include but not be limited to: operator logs, voice logs, or electronic communications. | Real-Time Operations | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 8. | Each Generator Operator shall notify the Balancing Authority as soon as practical but within 30 minutes of the discovery of a status change (in service, out of service) of a Governor. | M8. Each Generator Operator shall have evidence that it notified the Balancing Authority within 30 minutes of each discovery of a status change (in service, out of service) of a Governor. | Real-Time Operations | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 | [7 empty] | GOP-2
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | No Parts for 8. |  | M8. Each Generator Operator shall have evidence that it notified the Balancing Authority within 30 minutes of each discovery of a status change (in service, out of service) of a Governor. | Real-Time Operations | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 9. | Each Generator Owner shall meet a minimum 12-month rolling average initial Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | M9. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each Generator Owner shall have documented evidence of any FMEs where the generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO | GO-2
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 9.1. | The initial Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the initial measurement period following the FME. | M9. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each Generator Owner shall have documented evidence of any FMEs where the generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 9.2. | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight-FME average. | M9. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each Generator Owner shall have documented evidence of any FMEs where the generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 9.3. | A generating unit/generating facility’s initial Primary Frequency Response performance during an FME may be excluded from the rolling average calculation by the Balancing Authority due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include, but are not limited to: • Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, • Data telemetry failure. The Balancing Authority may request raw data from the Generator Owner as a substitute. pulverizers, and forced draft fans); | M9. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each Generator Owner shall have documented evidence of any FMEs where the generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 10. | Each Generator Owner shall meet a minimum 12-month rolling average sustained Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | M10. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each Generator Owner shall have documented evidence of any Frequency Measurable Events where generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | [5 empty] | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO | GO-2
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 10.1. | The sustained Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the sustained measurement period following the FME. | M10. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each Generator Owner shall have documented evidence of any Frequency Measurable Events where generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 10.2. | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight- FME average. | M10. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each Generator Owner shall have documented evidence of any Frequency Measurable Events where generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | BAL | BAL-001 | BAL-001-TRE-2 | 10.3. | A generating unit/generating facility’s sustained Primary Frequency Response performance during an FME may be excluded from the rolling average calculation by the Balancing Authority due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include, , but are not limited to: • Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, pulverizers, and forced draft fans); • Data telemetry failure. The Balancing Authority may request raw data from the Generator Owner as a substitute. | M10. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each Generator Owner shall have documented evidence of any Frequency Measurable Events where generating unit performance was excluded from the rolling average calculation. | Operations Assessment | 2020-02-06 | 2020-03-11 | 2020-05-19 | 2020-05-19 | 2020-07-01 | 2020-05-19 |  |  |  |  | Filing/Order Docket No. RD20-5-000 |  |  |  |  | GO
Inactive | BAL | BAL-002 | BAL-002-0 | 1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2.1. | The minimum reserve requirement for the group. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2.2. | Its allocation among members. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2.3. | The permissible mix of Operating Reserve - Spinning and Operating Reserve - Supplemental that may be included in Contingency Reserve. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2.4. | The procedure for applying Contingency Reserve in practice. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2.5. | The limitations, if any, upon the amount of interruptible load that may be included. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 2.6. | The same portion of resource capacity (e.g., reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. This period may be adjusted to better suit the needs of an Interconnection based on analysis approved by the NERC Operating Committee. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. Or |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-0 | 6.2. | The default Contingency Reserve Restoration Period is 90 minutes. This period may be adjusted to better suit the reliability targets of the Interconnection based on analysis approved by the NERC Operating Committee. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-03-31 | Filing/Order Docket No. RM06-16-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then if ACEA > 0 then where: • MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss, • ACEA is the pre-disturbance ACE, • ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then if ACEA > 0 then where: • MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss, • ACEA is the pre-disturbance ACE, • ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2.1. | The minimum reserve requirement for the group. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2.2. | Its allocation among members. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2.3. | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2.4. | The procedure for applying Contingency Reserve in practice. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2.5. | The limitations, if any, upon the amount of interruptible load that may be included. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 2.6. | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | [16 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. or |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1 | 6.2. | The default Contingency Reserve Restoration Period is 90 minutes. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2012-04-01 | 2011-01-10 |  |  |  | 2017-12-31 | Filing/Order Docket No. RD10-15-000 | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then MW ACE ACE R    if ACEA > 0 then *100% max(0, ) Loss Loss M i MW MW ACE R    where:  MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss,  ACEA is the pre-disturbance ACE,  ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then MW ACE ACE R    if ACEA > 0 then *100% max(0, ) Loss Loss M i MW MW ACE R    where:  MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss,  ACEA is the pre-disturbance ACE,  ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2.1. | The minimum reserve requirement for the group. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2.2. | Its allocation among members. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2.3. | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2.4. | The procedure for applying Contingency Reserve in practice. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2.5. | The limitations, if any, upon the amount of interruptible load that may be included. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 2.6. | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | [16 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  |  | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | Real-Time Operations | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. or |  | Real-Time Operations | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | Real-Time Operations | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | Real-Time Operations | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | Real-Time Operations | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-1a | 6.2. | The default Contingency Reserve Restoration Period is 90 minutes. |  | Real-Time Operations | 2012-11-07 | 2013-02-12 | [7 empty] | 2017-02-17 | BAL-002-1a was never approved or amended by FERC; notice of withdrawal filed 2/2/2017 following FERC approval of BAL-002-2. | BA | [15 empty] | RRO |  | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 |  | 2017-04-03 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 1.2. | document all Reportable Balancing Contingency Events using CR Form 1. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 |  | 2017-04-03 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 |  | 2017-04-03 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 1.3.1. | 1.3.1 the Responsible Entity: • is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 1.3.2. | 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | 2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Operations Planning | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | No Parts for 2. |  | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Operations Planning | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000
Inactive | BAL | BAL-002 | BAL-002-2 | 3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2 | No Parts for 3. |  | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | Real-Time Operations | 2015-11-05 | 2016-01-29 | 2017-01-19 | 2017-04-03 | [5 empty] | 2017-12-31 | Filing/Order Docket No. RM16-7-000
Inactive | BAL | BAL-002 | BAL-002-2(i) | 1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | 1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 | 2017-10-02 |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | 1.2. | document all Reportable Balancing Contingency Events using CR Form 1. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 | 2017-10-02 |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | 1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 | 2017-10-02 |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | 1.3.1. | the Responsible Entity: • is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 | 2018-01-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | 1.3.2. | the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 | 2018-01-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | 2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Operations Planning | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | No Parts for 2. |  | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Operations Planning | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000
Inactive | BAL | BAL-002 | BAL-002-2(i) | 3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-2(i) | No Parts for 3. |  | Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | Real-Time Operations | 2017-08-10 | 2017-08-14 | 2017-10-02 | 2017-10-02 | 2018-01-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RD17-6-000
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 1.2. | document all Reportable Balancing Contingency Events using CR Form 1. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 1.3.1. | is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 1.3.2. | the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Operations Planning | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | No Parts for 2. |  | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | Operations Planning | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RD18-7-000
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | 3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RD18-7-000 | BA | [17 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002 | BAL-002-3 | No Parts for 3. |  | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | Real-Time Operations | 2018-08-16 | 2018-08-17 | 2018-09-25 | 2018-09-25 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RD18-7-000
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 1. | Each Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall maintain as a minimum Contingency Reserve that is the sum of the following: | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 1.1. | The greater of the following: | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 1.1.1. | An amount of reserve equal to the loss of the most severe single contingency; or | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 1.1.2. | An amount of reserve equal to the sum of three percent of the load (generation minus station service minus Net Actual Interchange) and three percent of net generation (generation minus station service). | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 1.2. | If the Source Balancing Authority designates an Interchange Transaction(s) as part of its Non-Spinning Contingency Reserve, the Sink Balancing Authority shall carry an amount of additional Non-Spinning Contingency Reserve equal to the Interchange Transaction(s). This type of transaction cannot be designated as Spinning Reserves by the source BA. If the Source Balancing Authority does not designate the Interchange Transaction as part of its Contingency Reserve, the Sink Balancing Authority is not required to carry any additional Contingency Reserves under this Requirement. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 1.3. | If the Sink Balancing Authority is designating an Interchange Transaction(s) as part of its Contingency Reserve either Spinning or Non-Spinning, the Source Balancing Authority shall increase its Contingency Reserves equal in amount and type, to the capacity transaction(s) where the Sink Balancing Authority is designating the transaction(s) as a resource to meet its Contingency Reserve requirements. These types of transactions could be designated as either spinning or non-spinning reserves. If designated as Spinning Reserves, all of the requirements of section R2.1 & R2.2 must be met. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 2. | Each Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall maintain at least half of the Contingency Reserve in R1.1 as Spinning Reserve. Any Spinning Reserve specified in R1 shall meet the following requirements. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained at least 100% of minimum Spinning Contingency Reserve required based upon data averaged over each clock hour except within the first 105 minutes following an event requiring the activation of Contingency Reserves. For each hour, Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall have and provide upon request the Spinning Reserve Requirement in MW and amount of Spinning Reserve available in MW that is automatically responsive to frequency and can be fully deployed in 10 minutes. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 2.1. | Immediately and automatically responds proportionally to frequency deviations, e.g. through the action of a governor or other control systems. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained at least 100% of minimum Spinning Contingency Reserve required based upon data averaged over each clock hour except within the first 105 minutes following an event requiring the activation of Contingency Reserves. For each hour, Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall have and provide upon request the Spinning Reserve Requirement in MW and amount of Spinning Reserve available in MW that is automatically responsive to frequency and can be fully deployed in 10 minutes. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 2.2. | Capable of fully responding within ten minutes. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained at least 100% of minimum Spinning Contingency Reserve required based upon data averaged over each clock hour except within the first 105 minutes following an event requiring the activation of Contingency Reserves. For each hour, Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall have and provide upon request the Spinning Reserve Requirement in MW and amount of Spinning Reserve available in MW that is automatically responsive to frequency and can be fully deployed in 10 minutes. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3. | Each Reserve Sharing Group or Balancing Authority shall use the following acceptable types of reserve which must be fully deployable within 10 minutes of notification to meet R1: | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3.1. | Spinning Reserve | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3.2. | Interruptible Load; | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3.3. | Interchange Transactions designated by the source Balancing Authority as non-spinning contingency reserve; | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3.4. | Reserve held by other entities by agreement that is deliverable on Firm Transmission Service; | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3.5. | An amount of off-line generation which can be synchronized and generating; or | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-1 | 3.6. | Load, other than Interruptible Load, once the Reliability Coordinator has declared a capacity or energy emergency. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. | Real-Time Operations | 2008-10-29 | 2009-03-25 | [7 empty] | 2010-11-26 | Docket No. RM09-15-000; Order No. 740 Remanded by FERC in an October 21, 2010 Order, effective November 26, 2010. | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 1. | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 |  |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 1.1. | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 | 2014-01-28 |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 1.2. | Comprised of any combination of the reserve types specified below: • Operating Reserve – Spinning • Operating Reserve - Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve – Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service • A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement. • All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 | 2014-01-28 |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 1.3. | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 | 2014-01-28 |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 1.4. | An amount of capacity from a resource that is deployable within ten minutes. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 | 2014-01-28 |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 2. | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 |  |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 2.1. | Reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system; | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 | 2014-01-28 |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 2.2. | Reserve that is capable of fully responding within ten minutes. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 | 2014-01-28 |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 3. | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 |  |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | No Parts for 3. |  | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 |  |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | 4. | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 |  |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2 | No Parts for 4. |  | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | Real-Time Operations | 2012-11-07 | 2013-04-12 | 2013-11-21 | 2014-01-28 | 2014-10-01 |  |  |  |  | 2017-01-23 | Filing/Order Docket No. RM13-13-000
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 1. | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 1.1. | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 1.2. | Comprised of any combination of the reserve types specified below: • Operating Reserve – Spinning • Operating Reserve - Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve – Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service • A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement. • All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 1.3. | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 1.4. | An amount of capacity from a resource that is deployable within ten minutes. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 2. | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 2.1. | Reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system; | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 2.2. | Reserve that is capable of fully responding within ten minutes. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 3. | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | No Parts for 3. |  | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | 4. | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-2a | No Parts for 4. |  | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | Real-Time Operations | 2016-11-02 | 2016-11-09 | 2017-01-24 | 2017-01-24 | 2017-01-24 |  |  |  |  | 2021-06-27 | Filing/Order Docket No. RD17-3-000
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 1. | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 1.1. | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 | 2021-06-28 |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 1.2. | Composed of any combination of the reserve types specified below: • Operating Reserve—Spinning • Operating Reserve—Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve—Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service • A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement. • All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 | 2021-06-28 |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 1.3. | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 | 2021-06-28 |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 1.4. | An amount of capacity from a resource that is deployable within ten minutes. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 | 2021-06-28 |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 2. | Reserved. | Reserved |  | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | No Parts for 2. |  | Reserved |  | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 3. | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | No Parts for 3. |  | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | 4. | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-002 | BAL-002-WECC-3 | No Parts for 4. |  | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | Real-Time Operations | 2019-08-15 | 2019-09-06 | 2021-04-15 | 2021-04-15 | 2021-06-28 |  |  |  |  | 2026-07-01 | Filing/Order Docket No. ​RM19-20-000 FERC approved the retirement of the standard 4/14/2026 - RD26-5-000
Inactive | BAL | BAL-003 | BAL-003-0 | 1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000
Inactive | BAL | BAL-003 | BAL-003-0 | 4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. See Standard for Graphic. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | 6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket Nos. RM06-16-000, RM08-15-000, RM08-16-000
Inactive | BAL | BAL-003 | BAL-003-0.1a | 1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-003 | BAL-003-0.1a | 4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | 6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1a | No Parts for 6. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2009-06-28 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-003 | BAL-003-0.1b | 1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-003 | BAL-003-0.1b | 4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 | 2009-05-13 |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | 6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0.1b | No Parts for 6. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-06-29 |  |  |  |  | 2015-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-003 | BAL-003-0a | 1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | No Parts for 3. |  |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-003 | BAL-003-0a | 4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  |  | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | Real-Time Operations | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | Real-Time Operations | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | 6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | Operations Planning | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0a | No Parts for 6. |  |  | Operations Planning | 2007-10-23 | 2007-12-19 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-003 | BAL-003-0b | 1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | Operations Planning | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | Operations Planning | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | Operations Planning | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | No Parts for 3. |  |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000
Inactive | BAL | BAL-003 | BAL-003-0b | 4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 |  | 2009-06-29 |  |  |  | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | 6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000 | BA
Inactive | BAL | BAL-003 | BAL-003-0b | No Parts for 6. |  |  |  | 2008-02-12 | 2008-07-28 | 2009-05-21 | 2009-06-29 | [5 empty] | 2009-06-28 | Filing/Order Docket No. RM06-16-000, RM08-15-000, RM08-16-000
Inactive | BAL | BAL-003 | BAL-003-1 | 1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | Real-Time Operations | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable. | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1 | No Parts for 1. |  | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | Real-Time Operations | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable.
Inactive | BAL | BAL-003 | BAL-003-1 | 2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable. | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1 | No Parts for 2. |  | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable.
Inactive | BAL | BAL-003 | BAL-003-1 | 3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable. | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1 | 3.1. | Less than zero at all times, and | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 | 2014-03-24 | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable. | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1 | 3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 | 2014-03-24 | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable. | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1 | 4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable. | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1 | No Parts for 4. |  | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | Operations Planning | 2013-02-07 | 2013-03-29 | 2014-01-16 | 2014-03-24 | 2015-04-01 |  | X |  |  | 2015-11-12 | Filing/Order Docket No. ​RM13-11-000 ​ See the implementation plan for guidance on phased-in enforcement dates. Requirement R1 will never become enforceable.. Disregard the dates for R1 it is non enforceable.
Inactive | BAL | BAL-003 | BAL-003-1.1 | 1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | Real-Time Operations | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000 | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1.1 | No Parts for 1. |  | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | Real-Time Operations | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000
Inactive | BAL | BAL-003 | BAL-003-1.1 | 2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000 | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1.1 | No Parts for 2. |  | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000
Inactive | BAL | BAL-003 | BAL-003-1.1 | 3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000 | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1.1 | 3.1. | Less than zero at all times, and | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000 | BA
Inactive | BAL | BAL-003 | BAL-003-1.1 | 3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000 | BA
Inactive | BAL | BAL-003 | BAL-003-1.1 | 4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000 | BA |  |  | FRSG | [14 empty] | RSG
Inactive | BAL | BAL-003 | BAL-003-1.1 | No Parts for 4. |  | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | Operations Planning | 2013-02-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  | X | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | 2020-11-30 | Filing/Order Docket No. RD15-6-000
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | 1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | Real-Time Operations | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000 | BA |  |  | FRSG | [14 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | No Parts for 1. |  | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | Real-Time Operations | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | 2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | No Parts for 2. |  | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | 3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | 3.1. | Less than zero at all times, and | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | 2020-07-15 |  |  |  |  | Filing/Order Docket No. RD20-9-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | 3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | 2020-07-15 |  |  |  |  | Filing/Order Docket No. RD20-9-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | 4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-003 | BAL-003-2 | No Parts for 4. |  | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | Operations Planning | 2019-11-05 | 2019-12-19 | 2020-07-15 | 2020-07-15 | 2020-10-01 | [5 empty] | Filing/Order Docket No. RD20-9-000
Inactive | BAL | BAL-004 | BAL-004-0 | 1. | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard.
Inactive | BAL | BAL-004 | BAL-004-0 | 2. | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard.
Inactive | BAL | BAL-004 | BAL-004-0 | 3. | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-0 | 3.1. | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-0 | 3.2. | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e. 20% of the Frequency Bias Setting). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-0 | 4. | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-0 | 4.1. | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2017-04-01 | Filing/Order Docket No. RM06-16-000 The retirement of BAL-004-0 is contingent upon the retirement of NAESB WEQ-006 Manual Time Error Correction Business Practice Standard. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-1 | 1. | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-1 | No Parts for 1. |  |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012.
Inactive | BAL | BAL-004 | BAL-004-1 | 2. | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-1 | 2.1. | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-1 | 2.2. | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e., 20% of the Frequency Bias Setting). |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-1 | 3. | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-1 | 3.1. | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  |  | 2008-03-26 | 2011-08-11 | [7 empty] | 2012-08-16 | Filing/Order Docket No. RM09-13-000 The NERC BOT withdrew its approval of this standard at its meeting on August 16, 2012. | BA | [12 empty] | RC
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 1. | Each BA that operates synchronously to the Western Interconnection shall continuously operate utilizing Automatic Time Error Correction (ATEC) in its Automatic Generation Control (AGC) system. (See standard for formulas.) |  |  | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 1.1. | The absolute value of the WECC Automatic Time Error Correction term is limited as follows: Where Lmax is chosen by the Balancing Authority and is bounded as follows: 0.20 * ¦Bi¦ <= Lmax<= L10. L10 is the Balancing Authority CPS2 limit in MW. If the WECC Automatic Time Error Correction term is less than the upper limit, use the calculated WECC Automatic Time Error Correction term. |  |  | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 | 2009-06-29 |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 1.2. | Large accumulations of primary inadvertent point to an invalid implementation of ATEC, loose control, metering or accounting errors. A BA in such a situation should identify the source of the error(s) and make the corrections, recalculate the primary inadvertent from the time of the error, adjust the accumulated primary inadvertent caused by the error(s), validate the implementation of ATEC, set Lmax equal to L10 and continue to operate with ATEC reducing the accumulation as system parameters allow. |  |  | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 | 2009-06-29 |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 2. | Each BA that is synchronously connected to the Western Interconnection and operates in any AGC operating mode other than ATEC shall notify all other BAs of its operating mode through the designated Interconnection communication system. Each BA while synchronously connected to the Western Interconnection will be allowed to have ATEC out of service for a maximum of 24 hours per calendar quarter, for reasons including maintenance and testing. [Risk Factor: Lower] |  | Operations Assessment | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | No Parts for 2. |  |  | Operations Assessment | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 3. | BAs in the Western Interconnection shall be able to change their AGC operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; Tie Line Bias plus Time Error control (used in ATEC mode). The ACE used for NERC reports shall be the same ACE as the AGC operating mode in use. | For Requirement R3, a BA in the Western Interconnection must be able to demonstrate its ability to change its AGC operating mode when requested or during compliance audits and readiness reviews. | Operations Assessment | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | No Parts for 3. |  | For Requirement R3, a BA in the Western Interconnection must be able to demonstrate its ability to change its AGC operating mode when requested or during compliance audits and readiness reviews. | Operations Assessment | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 4. | Regardless of the AGC operating mode each BA in the Western Interconnection shall compute its hourly Primary Inadvertent Interchange when hourly checkout is complete. If hourly checkout is not complete by 50 minutes after the hour, compute Primary Inadvertent Interchange with best available data. This hourly value shall be added to the appropriate accumulated Primary Inadvertent Interchange balance for either On-Peak or Off-Peak periods. | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | Same-Day Operations | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 |  |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 4.1. | Each BA in the Western Interconnection shall use the change in Time Error distributed by the Interconnection Time Monitor. | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | Same-Day Operations | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 | 2009-06-29 |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 4.2. | All corrections to any previous hour Primary Inadvertent Interchange shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange. | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | Same-Day Operations | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 | 2009-06-29 |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 4.3. | Month end Inadvertent Adjustments are 100% Primary Inadvertent Interchange and shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange, unless such adjustments can be pinpointed to specific hours in which case R4.2 applies. | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | Same-Day Operations | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 | 2009-06-29 |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-01 | 4.4. | Each BA in the Western Interconnection shall synchronize its Time Error to the nearest 0.001 seconds of the system Time Error by comparing its reading at the designated time each day to the reading broadcast by the Interconnection Time Monitor. Any difference shall be applied as an adjustment to its current Time Error. | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | Same-Day Operations | 2008-03-26 | 2008-07-29 | 2009-05-21 | 2009-06-29 | 2009-07-01 | 2009-06-29 |  |  |  | 2014-03-31 | Filing/Order Docket No. RM08-12-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 1. | Following the conclusion of each month each Balancing Authority shall verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PII-accum) for both the monthly On-Peak period and the monthly Off-Peak period are each individually less than or equal to: | M1. Forms of acceptable evidence of compliance with Requirement R1include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT), • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 1.1. | For load-serving Balancing Authorities, 150% of the previous calendar year’s integrated hourly Peak Demand, | M1. Forms of acceptable evidence of compliance with Requirement R1include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT), • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 | 2013-10-16 |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 1.2. | For generation-only Balancing Authorities, 150% of the previous calendar year’s integrated hourly peak generation. | M1. Forms of acceptable evidence of compliance with Requirement R1include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT), • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 | 2013-10-16 |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 2. | Each Balancing Authority shall, upon discovery of an error in the calculation of PII-hourly, recalculate within 90 days, the value of PII-hourly and adjust the PII-accum from the time of the error. | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WIT, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | No Parts for 2. |  | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WIT, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 3. | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | Same-Day Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | No Parts for 3. |  | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | Same-Day Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 4. | Each Balancing Authority shall compute the following by 50 minutes after each hour: | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from internal Balancing Authority tool that demonstrate compliance, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 4.1. | PIIhourly, | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from internal Balancing Authority tool that demonstrate compliance, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 | 2013-10-16 |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 4.2. | PIIaccum, | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from internal Balancing Authority tool that demonstrate compliance, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 | 2013-10-16 |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 4.3. | Automatic Time Error Correction term (IATEC). | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from internal Balancing Authority tool that demonstrate compliance, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 | 2013-10-16 |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 5. | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | Real-Time Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | No Parts for 5. |  | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | Real-Time Operations | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 6. | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | No Parts for 6. |  | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 7. | Each Balancing Authority shall make the same adjustment to the PII-accum as it did for any month-end meter reading adjustments to Inadvertent Interchange. | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | No Parts for 7. |  | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | 8. | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-02 | No Parts for 8. |  | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | Operations Assessment | 2012-12-19 | 2013-08-20 | 2013-10-16 | 2013-10-16 | 2014-04-01 |  |  |  |  | 2018-09-30 | Filing/Order Docket No. RD13-11-000
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 1. | Each Balancing Authority shall operate its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, are each individually less than or equal to: | M1. Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 1.1. | For load-serving Balancing Authorities, 150% of the previous calendar year’s integrated hourly Peak Demand, | M1. Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 | 2018-05-30 |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 1.2. | For generation-only Balancing Authorities, 150% of the previous calendar year’s integrated hourly peak generation. | M1. Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 | 2018-05-30 |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 2. | Each Balancing Authority shall, upon discovery of an error in the calculation of PIIhourly, recalculate within 90 days, the value of PIIhourly and adjust the PIIaccum from the time of the error. | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | No Parts for 2. |  | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 3. | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | Same-Day Operations | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | No Parts for 3. |  | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | Same-Day Operations | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 4. | Each Balancing Authority shall compute each of the following using the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, no later than 50 minutes after each hour, | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 4.1. | PIIhourly, | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 | 2018-05-30 |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 4.2. | PIIaccum, | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 | 2018-05-30 |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 4.3. | Automatic Time Error Correction term (IATEC). | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 | 2018-05-30 |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 5. | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | Real-Time Operations | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | No Parts for 5. |  | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | Real-Time Operations | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 6. | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | No Parts for 6. |  | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 7. | Each Balancing Authority shall make the same adjustment to the PIIaccum as it did for any month-end meter reading adjustments to Inadvertent Interchange. | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance; or, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | No Parts for 7. |  | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance; or, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | 8. | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000 | BA
Inactive | BAL | BAL-004 | BAL-004-WECC-3 | No Parts for 8. |  | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | Operations Assessment | 2018-02-08 | 2018-03-08 | 2018-05-30 | 2018-05-30 | 2018-10-01 |  |  |  |  | 2025-09-30 | Filing/Order Docket No. RD18-2-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 1. | Each Balancing Authority shall use the Interchange Software as the sole source of data to calculate its ATEC. [ | Each Balancing Authority will have evidence that it used the Interchange Software as the sole source of data to calculate its ATEC, as required in Requirement R1. Evidence may include, but is not limited to production of a corporate attestation or operating procedure indicating use of the Interchange Software as the sole source for calculating ATEC. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 1. |  | Each Balancing Authority will have evidence that it used the Interchange Software as the sole source of data to calculate its ATEC, as required in Requirement R1. Evidence may include, but is not limited to production of a corporate attestation or operating procedure indicating use of the Interchange Software as the sole source for calculating ATEC. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 2. | Each Balancing Authority shall operate its system such that, the month-end absolute value of its On-Peak and Off-Peak, accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the Interchange Software, are each individually less than or equal to 150% of the previous calendar year’s integrated hourly peak demand where peak demand is total load plus total exports. | M2. Each Balancing Authority will have evidence that it operated its system such that the month-end absolute value of its On-Peak and Off-Peak, accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the Interchange Software, are each individually less than or equal to 150% of the previous calendar year’s integrated hourly peak demand where peak demand is total load plus total exports, average load in those hours, as calculated by the Interchange Software, per Requirement R2, or per the exception allowed in R2.1. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 2.1. | For new Balancing Authorities, the peak demand will be the maximum hourly integrated peak demand as it increases during the first year of operation. | M2. Each Balancing Authority will have evidence that it operated its system such that the month-end absolute value of its On-Peak and Off-Peak, accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the Interchange Software, are each individually less than or equal to 150% of the previous calendar year’s integrated hourly peak demand where peak demand is total load plus total exports, average load in those hours, as calculated by the Interchange Software, per Requirement R2, or per the exception allowed in R2.1. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 3. | Each Balancing Authority shall, upon discovery of an error in its On-Peak or Off-Peak Inadvertent Interchange calculation, recalculate and correct the Inadvertent Interchange values within 90 days from the time the error is discovered. | M3. Each Balancing Authority discovering an error in its On-Peak or Off-Peak Inadvertent Interchange calculation will have evidence that it recalculated and corrected the Inadvertent Interchange values, within 90 days from the time the error is discovered, as required in Requirement R3. Evidence may include, but is not limited to: • Screen shots from the Interchange Software; • Screen shots from the Balancing Authority’s internal software functions such as internal databases, spreadsheets, and displays; • Dated archive files; and • Historic data. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 3. |  | M3. Each Balancing Authority discovering an error in its On-Peak or Off-Peak Inadvertent Interchange calculation will have evidence that it recalculated and corrected the Inadvertent Interchange values, within 90 days from the time the error is discovered, as required in Requirement R3. Evidence may include, but is not limited to: • Screen shots from the Interchange Software; • Screen shots from the Balancing Authority’s internal software functions such as internal databases, spreadsheets, and displays; • Dated archive files; and • Historic data. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 4. | Each Balancing Authority shall keep ATEC in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. This period is separate from any period during which the Interchange Software was unavailable. | M4. Each Balancing Authority will have evidence that it kept ATEC in service as required in Requirement R4, subject to the allowable exceptions provided. Evidence may include, but is not limited to: • Screen shots from the Interchange Software; • Screen shots from the Balancing Authority’s internal software functions such as internal databases, spreadsheets, and displays; • Dated archive files; and • Historical data. | Same-Day Operations | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 4. |  | M4. Each Balancing Authority will have evidence that it kept ATEC in service as required in Requirement R4, subject to the allowable exceptions provided. Evidence may include, but is not limited to: • Screen shots from the Interchange Software; • Screen shots from the Balancing Authority’s internal software functions such as internal databases, spreadsheets, and displays; • Dated archive files; and • Historical data. | Same-Day Operations | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 5. | Each Balancing Authority shall be able to change its Automatic Generation Control (AGC) operating mode to correspond to current operating conditions. [Violation Risk Factor: Medium] [Time Horizon: Real-Time Operations] | M5. Each Balancing Authority will have evidence that its AGC is able to change operating modes to correspond to current operating conditions, as required in R5. Evidence may include, but is not limited to: • Screen shots from Energy Management System; and • Demonstration using an off-line system. | Real-Time Operations | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 5. |  | M5. Each Balancing Authority will have evidence that its AGC is able to change operating modes to correspond to current operating conditions, as required in R5. Evidence may include, but is not limited to: • Screen shots from Energy Management System; and • Demonstration using an off-line system. | Real-Time Operations | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 6. | Each Balancing Authority shall upload hourly Actual Net Interchange (NIA) to the Interchange Software no later than 50 minutes after each hour. | M6. Each Balancing Authority will have evidence that it uploaded hourly Actual Net Interchange (NIA) to the Interchange Software no later than 50 minutes after each hour, as required in Requirement R6. Evidence may include, but is not limited to: • Screen shots from the Interchange Software; • Screen shots from the Balancing Authority’s internal software functions such as internal databases, spreadsheets, and displays; • Dated archive files; and • Historical data. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 6. |  | M6. Each Balancing Authority will have evidence that it uploaded hourly Actual Net Interchange (NIA) to the Interchange Software no later than 50 minutes after each hour, as required in Requirement R6. Evidence may include, but is not limited to: • Screen shots from the Interchange Software; • Screen shots from the Balancing Authority’s internal software functions such as internal databases, spreadsheets, and displays; • Dated archive files; and • Historical data. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 7. | Each Balancing Authority making a month-end adjustment shall input that value as part of its Actual Net Interchange (NIA). | M7. Each Balancing Authority making a month-end adjustment will have evidence that it input that value as part of its Actual Net Interchange (NIA), as required in Requirement R7. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 7. |  | M7. Each Balancing Authority making a month-end adjustment will have evidence that it input that value as part of its Actual Net Interchange (NIA), as required in Requirement R7. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | 8. | Each Balancing Authority making a month-end adjustment shall ensure that value is added to its accumulated Primary Inadvertent Interchange. | M8. Each Balancing Authority making a month-end adjustment will have evidence that the value was added to its accumulated Primary Inadvertent Interchange, as required in Requirement R8. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-004 | BAL-004-WECC-4 | No Parts for 8. |  | M8. Each Balancing Authority making a month-end adjustment will have evidence that the value was added to its accumulated Primary Inadvertent Interchange, as required in Requirement R8. | Operations Assessment | 2025-02-13 | 2025-03-12 | 2025-04-23 | 2025-04-23 | 2025-10-01 | [5 empty] | Filing/Order Docket No. ​RD25-6-000
Inactive | BAL | BAL-005 | BAL-005-0 | 1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 10. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 11. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | 13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 13. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 14. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 15. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 16. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0 | 17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0 | No Parts for 17. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 2. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 4. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 5. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 6. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 7. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 10. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 11. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | 13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 13. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 14. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 15. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 16. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.1b | 17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.1b | No Parts for 17. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 2. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 3. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 4. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 5. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 6. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 7. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 10. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 11. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | 13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 13. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 14. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 15. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 16. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0.2b | 17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0.2b | No Parts for 17. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD12-4-000
Inactive | BAL | BAL-005 | BAL-005-0a | 1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 2. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 3. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 4. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 5. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 6. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 7. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 10. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 11. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | 13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 13. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 14. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 15. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 16. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0a | 17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0a | No Parts for 17. |  |  |  | 2007-05-02 | 2007-12-19 | [7 empty] | 2008-04-15 | Withdrawn
Inactive | BAL | BAL-005 | BAL-005-0b | 1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 2. |  |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 3. |  |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 4. |  |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 5. |  |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 6. |  |  | Real-Time Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | Operations Assessment | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 7. |  |  | Operations Assessment | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | Same-Day Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | Same-Day Operations | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | Operations Planning | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | Operations Planning | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 10. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 11. | Balancing Authorities shall include the effect of Ramp Rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 11. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | 13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 13. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 14. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 15. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 16. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Inactive | BAL | BAL-005 | BAL-005-0b | 17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000 | BA | [5 empty] | GOP |  |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005 | BAL-005-0b | No Parts for 17. |  |  |  | 2008-02-12 | 2008-04-15 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM08-7-000
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 1. | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | No Parts for 1. |  | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 2. | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | No Parts for 2. |  | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 3. | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 3.1. | that is available a minimum of 99.95% for each calendar year; and, | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2017-11-27 |  |  |  |  | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 3.2. | with a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2017-11-27 |  |  |  |  | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 4. | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | No Parts for 4. |  | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | Real-Time Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 5. | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | Operations Assessment | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | No Parts for 5. |  | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | Operations Assessment | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 6. | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | Same-Day Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | No Parts for 6. |  | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | Same-Day Operations | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 7. | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | Operations Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | [5 empty] | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 7.1. | a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | Operations Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2017-11-27 |  |  |  |  | Filing/Order Docket No. RM16-13-000 | BA
Mandatory Subject to Enforcement | BAL | BAL-005 | BAL-005-1 | 7.2. | a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | Operations Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2017-11-27 |  |  |  |  | Filing/Order Docket No. RM16-13-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-0 | 2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-0 | 3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-0 | 4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 4.1.1. | The hourly values of Net Interchange Schedule. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and OffPeak hours of the month. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | 5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-05-01 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-1 | 1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | No Parts for 1. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-1 | 2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-1 | 3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | No Parts for 3. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-1 | 4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | 4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | 4.1.1. | The hourly values of Net Interchange Schedule. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | 4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | 4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | 4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | 5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | Long-Term Planning | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1 | No Parts for 5. |  |  | Long-Term Planning | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000
Inactive | BAL | BAL-006 | BAL-006-1.1 | 1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | No Parts for 1. |  |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-006 | BAL-006-1.1 | 2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | No Parts for 2. |  |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-006 | BAL-006-1.1 | 3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | No Parts for 3. |  |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-006 | BAL-006-1.1 | 4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | 4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | 4.1.1. | The hourly values of Net Interchange Schedule. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | 4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | 4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | 4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | 5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | BAL | BAL-006 | BAL-006-1.1 | No Parts for 5. |  |  | Long-Term Planning | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | BAL | BAL-006 | BAL-006-2 | 1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | No Parts for 1. |  |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000
Inactive | BAL | BAL-006 | BAL-006-2 | 2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | No Parts for 2. |  |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000
Inactive | BAL | BAL-006 | BAL-006-2 | 3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | No Parts for 3. |  |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000
Inactive | BAL | BAL-006 | BAL-006-2 | 4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | 4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | 4.1.1. | The hourly values of Net Interchange Schedule. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | 4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | 4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | 4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | 5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | BAL | BAL-006 | BAL-006-2 | No Parts for 5. |  |  | Long-Term Planning | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD10-4-000
Inactive | BAL | BAL-007 | BAL-007-1 | 1. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, document a process for conducting Near-Term Energy Reliability Assessments (ERA). | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.1. | The Near-Term ERA process shall account for: | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.1.1. | Forecasted or assumed Demand profiles; | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.1.2. | Resource capabilities and operational limitations, including fuel supply; | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.1.3. | Energy transfers with other Balancing Authorities; and | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.1.4. | Known Bulk Electric System (BES) Transmission constraints that limit the ability of generation to deliver their output to Load. | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.2. | The Near-Term ERA process shall specify the duration of the Balancing Authority’s Near-Term ERAs. | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.3. | The Near-Term ERA process shall specify the frequency at which the Balancing Authority will conduct Near-Term ERAs, subject to the following: | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.3.1. | Each Balancing Authority will conduct Near-Term ERAs for all time periods unless the Balancing Authority demonstrates, via a documented methodology, that a Near-Term ERA is not necessary for a specified time period(s) because there is a low risk of an Energy Emergency occurring during that specified time period(s). | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 1.3.2. | The documented methodology for identifying time periods for which the Balancing Authority will not conduct a Near-Term ERA must (i) define the criteria used to determine when there is a low risk of an Energy Emergency occurring, and (ii) account for the items listed in 1.1.1 – 1.1.4 and other conditions associated with Energy Emergencies. | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 2. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, document a set of Scenarios, or a method for developing Scenarios, for use in performing Near-Term ERAs. | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 2.1. | The set of Scenarios must include (i) a base Scenario with expected system conditions, and (ii) other Scenarios that stress the system due to the following conditions, as applicable to the Balancing Authority’s system: | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 2.1.1. | Higher than forecasted or assumed Demand profiles; | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 2.1.2. | The effects of an energy supply contingency; | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 2.1.3. | The effects of a fuel supply contingency; and | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 2.1.4. | Other stressed conditions that have a historical precedent of occurring, as defined by the Balancing Authority, based on the information available at the time of Scenario development. | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | 3. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, document one or more Operating Plan(s) to implement in response to forecasted Energy Emergencies, including provisions for notification to their Reliability Coordinator of the forecasted Energy Emergency and the Operating Plan(s). | M3. Each Balancing Authority shall have evidence that it documented its Operating Plan(s) in accordance with Requirement R3. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | No Parts for 3. |  | M3. Each Balancing Authority shall have evidence that it documented its Operating Plan(s) in accordance with Requirement R3. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata
Inactive | BAL | BAL-007 | BAL-007-1 | 4. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, perform Near-Term ERAs according to the process documented in Requirement R1 using the Scenarios or methods documented in Requirement R2. | M4. Each Balancing Authority shall have evidence that it performed the Near-Term ERAs in accordance with Requirement R4. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | No Parts for 4. |  | M4. Each Balancing Authority shall have evidence that it performed the Near-Term ERAs in accordance with Requirement R4. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata
Inactive | BAL | BAL-007 | BAL-007-1 | 5. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, implement its Operating Plan(s), as documented in Requirement R3, when Near-Term ERAs identify any of the following forecasted Energy Emergencies: • Forecasted EEA2 circumstances as defined in EOP-011 Attachment 1 Section B; or • Forecasted EEA3 circumstances as defined in EOP-011 Attachment 1 Section B. | M5. Each Balancing Authority shall have evidence that it has implemented an Operating Plan(s) in accordance with Requirement R5. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | No Parts for 5. |  | M5. Each Balancing Authority shall have evidence that it has implemented an Operating Plan(s) in accordance with Requirement R5. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata
Inactive | BAL | BAL-007 | BAL-007-1 | 6. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, review, update, as necessary, and provide to the applicable Reliability Coordinator its Near-term ERA process, Scenarios or methods, and Operating Plan(s), documented under Requirements R1 through R3, at least once every 24 calendar months. | M6. Each Balancing Authority shall have evidence that it reviewed and provided its Near term ERA process, Scenarios or methods, and Operating Plan(s) to its Reliability Coordinator, in accordance with Requirement R6. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata | BA
Inactive | BAL | BAL-007 | BAL-007-1 | No Parts for 6. |  | M6. Each Balancing Authority shall have evidence that it reviewed and provided its Near term ERA process, Scenarios or methods, and Operating Plan(s) to its Reliability Coordinator, in accordance with Requirement R6. | Operations Planning | 2024-12-10 | 2025-01-06 | 2025-02-26 | 2025-02-26 | [5 empty] | 2026-03-26 | Filing/Order Docket No. RD25-5-000 Replaced by BAL-007-1 - Errata
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, document a process for conducting Near-Term Energy Reliability Assessments (ERA). | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.1. | The Near-Term ERA process shall account for: | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.1.1. | Forecasted or assumed Demand profiles; | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.1.2. | Resource capabilities and operational limitations, including fuel supply; | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.1.3. | Energy transfers with other Balancing Authorities; and | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.1.4. | Known Bulk Electric System (BES) Transmission constraints that limit the ability of generation to deliver their output to Load. | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.2. | The Near-Term ERA process shall specify the duration of the Balancing Authority’s Near-Term ERAs. | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.3. | The Near-Term ERA process shall specify the frequency at which the Balancing Authority will conduct Near-Term ERAs, subject to the following: | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.3.1. | Each Balancing Authority will conduct Near-Term ERAs for all time periods unless the Balancing Authority demonstrates, via a documented methodology, that a Near-Term ERA is not necessary for a specified time period(s) because there is a low risk of an Energy Emergency occurring during that specified time period(s). | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 1.3.2. | The documented methodology for identifying time periods for which the Balancing Authority will not conduct a Near-Term ERA must (i) define the criteria used to determine when there is a low risk of an Energy Emergency occurring, and (ii) account for the items listed in 1.1.1 – 1.1.4 and other conditions associated with Energy Emergencies. | M1. Each Balancing Authority shall have evidence that it documented a process for conducting Near-Term ERAs in accordance with Requirement R1. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 2. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, document a set of Scenarios, or a method for developing Scenarios, for use in performing Near-Term ERAs. | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 2.1. | The set of Scenarios must include (i) a base Scenario with expected system conditions, and (ii) other Scenarios that stress the system due to the following conditions, as applicable to the Balancing Authority’s system: | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 2.1.1. | Higher than forecasted or assumed Demand profiles; | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 2.1.2. | The effects of an energy supply contingency; | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 2.1.3. | The effects of a fuel supply contingency; and | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 2.1.4. | Other stressed conditions that have a historical precedent of occurring, as defined by the Balancing Authority, based on the information available at the time of Scenario development. | M2. Each Balancing Authority shall have evidence that it documented the Scenarios, or the method of developing Scenarios, for use in performing Near-Term ERAs. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | 2027-04-01 |  |  |  |  | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 3. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, document one or more Operating Plan(s) to implement in response to forecasted Energy Emergencies, including provisions for notification to their Reliability Coordinator of the forecasted Energy Emergency and the Operating Plan(s). [ | M3. Each Balancing Authority shall have evidence that it documented its Operating Plan(s) in accordance with Requirement R3. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | No Parts for 3. |  | M3. Each Balancing Authority shall have evidence that it documented its Operating Plan(s) in accordance with Requirement R3. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata)
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 4. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, perform Near-Term ERAs according to the process documented in Requirement R1 using the Scenarios or methods documented in Requirement R2. | M4. Each Balancing Authority shall have evidence that it performed the Near-Term ERAs in accordance with Requirement R4. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | No Parts for 4. |  | M4. Each Balancing Authority shall have evidence that it performed the Near-Term ERAs in accordance with Requirement R4. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata)
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 5. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, implement its Operating Plan(s), as documented in Requirement R3, when Near-Term ERAs identify any of the following forecasted Energy Emergencies: - Forecasted EEA2 circumstances as defined in EOP-011 Attachment 1 Section B; or - Forecasted EEA3 circumstances as defined in EOP-011 Attachment 1 Section B. | M5. Each Balancing Authority shall have evidence that it has implemented an Operating Plan(s) in accordance with Requirement R5. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | No Parts for 5. |  | M5. Each Balancing Authority shall have evidence that it has implemented an Operating Plan(s) in accordance with Requirement R5. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata)
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | 6. | Each Balancing Authority shall, individually or jointly with other Balancing Authorities, review, update, as necessary, and provide to the applicable Reliability Coordinator its Near-Term ERA process, Scenarios or methods, and Operating Plan(s), documented under Requirements R1 through R3, at least once every 24 calendar months. | M6. Each Balancing Authority shall have evidence that it reviewed and provided its Near- Term ERA process, Scenarios or methods, and Operating Plan(s) to its Reliability Coordinator, in accordance with Requirement R6. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata) | BA
Subject to Future Enforcement | BAL | BAL-007 | BAL-007-1.1 | No Parts for 6. |  | M6. Each Balancing Authority shall have evidence that it reviewed and provided its Near- Term ERA process, Scenarios or methods, and Operating Plan(s) to its Reliability Coordinator, in accordance with Requirement R6. | Operations Planning |  | 2026-02-23 | 2026-03-26 | 2026-03-26 | 2027-04-01 | [5 empty] | Filing/Order Docket No. RD26-4-000 Replaces BAL-007-1 (Errata)
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1. | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | [5 empty] | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.1. | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion). | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.1.1. | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.1.2. | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median forecast peak Net Internal Demand (planning reserve margin). | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.2. | Be performed or verified separately for each of the following planning years: | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.2.1. | Perform an analysis for Year One. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.2.2. | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.2.2.1. | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3. | Include the following subject matter and documentation of its use: | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1. | Load forecast characteristics: | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1.1. | Median (50:50) forecast peak Load. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1.2. | Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1.3. | Load diversity. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1.4. | Seasonal Load variations. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1.5. | Daily demand modeling assumptions (firm, interruptible). | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.1.6. | Contractual arrangements concerning curtailable/Interruptible Demand. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2. | Resource characteristics: | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2.1. | Historic resource performance and any projected changes | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2.2. | Seasonal resource ratings | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2.3. | Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2.4. | Resource planned outage schedules, deratings, and retirements. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2.5. | Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.2.6. | Criteria for including planned resource additions in the analysis | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.3. | Transmission limitations that prevent the delivery of generation reserves | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.3.1. | Criteria for including planned Transmission Facility additions in the analysis | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.3.4. | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4. | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.1. | Availability and deliverability of fuel. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.2. | Common mode outages that affect resource availability | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.3. | Environmental or regulatory restrictions of resource availability. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.4. | Any other demand (Load) response programs not included in R1.3.1. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.5. | Sensitivity to resource outage rates. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.6. | Impacts of extreme weather/drought conditions that affect unit availability. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.7. | Modeling assumptions for emergency operation procedures used to make reserves available. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.4.8. | Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2018-01-01 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.5. | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.6. | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 1.7. | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 2. | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis | M2. Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | [5 empty] | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 2.1. | This documentation shall cover each of the years in Year One through ten. | M2. Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 2.2. | This documentation shall include the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis. | M2. Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 2.3. | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. | M2. Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | 2017-10-16 |  |  |  |  | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | 3. | The Planning Coordinator shall identify any gaps between the needed amount of planning reserves defined in Requirement R1, Part 1.1 and the projected planning reserves documented in Requirement R2 | M3. Each Planning Coordinator shall possess the documentation identifying any gaps between the needed amounts of planning reserves and projected planning reserves in accordance with R3. | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | [5 empty] | Filing/Order Docket No. RD17-8-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | BAL | BAL-502 | BAL-502-RF-03 | No Parts for 3. |  | M3. Each Planning Coordinator shall possess the documentation identifying any gaps between the needed amounts of planning reserves and projected planning reserves in accordance with R3. | Long-Term Planning | 2017-08-10 | 2017-09-07 | 2017-10-16 | 2017-10-16 | 2018-01-01 | [5 empty] | Filing/Order Docket No. RD17-8-000
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1. | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall: [See Standard pdf for requirements of the Resource Adequacy analysis] | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.1. | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year1 analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion). | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.1.1. | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.1.2. | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median2 forecast peak Net Internal Demand (planning reserve margin). Note: The median forecast is expected to have a 50% probability of being too high and 50% probability of being too low (50:50). | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.2. | Be performed or verified separately for each of the following planning years: | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.2.1. | Perform an analysis for Year One. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.2.2. | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.2.2.1. | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.3. | Include the following subject matter and documentation of its use: | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.3.1. | Load forecast characteristics: • Median (50:50) forecast peak Load. • Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). • Load diversity. • Seasonal Load variations. • Daily demand modeling assumptions (firm, interruptible). • Contractual arrangements concerning curtailable/Interruptible Demand. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.3.2. | Resource characteristics: • Historic resource performance and any projected changes • Seasonal resource ratings • Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. • Resource planned outage schedules, deratings, and retirements. • Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration. • Criteria for including planned resource additions in the analysis | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.3.3. | Transmission limitations that prevent the delivery of generation reserves | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.3.3.1. | Criteria for including planned Transmission Facility additions in the analysis | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.3.4. | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.4. | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: • Availability and deliverability of fuel. • Common mode outages that affect resource availability • Environmental or regulatory restrictions of resource availability. • Any other demand (Load) response programs not included in R1.3.1. • Sensitivity to resource outage rates. • Impacts of extreme weather/drought conditions that affect unit availability. • Modeling assumptions for emergency operation procedures used to make reserves available. • Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.5. | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.6. | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 1.7. | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 2. | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis. [See Standard pdf for the requirements of the documentation] | M2 Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 |  |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 2.1. | This documentation shall cover each of the years in Year One through ten. | M2 Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 2.2. | This documentation shall include the planning reserve margin calculated per requirement R1.1 for each of the three years in the analysis. | M2 Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-502 | BAL-502-RFC-02 | 2.3. | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. | M2 Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. |  | 2009-08-05 | 2009-12-14 | 2011-03-17 | 2011-05-23 | 2011-05-23 | 2011-05-23 |  |  |  | 2017-12-31 | Filing/Order Docket No. RM10-10-000 | [10 empty] | PA | PC
Inactive | BAL | BAL-STD | BAL-STD-002-0 | W1. | The reliable operation of the interconnected power system requires that adequate generating capacity be available at all times to maintain scheduled frequency and avoid loss of firm load following transmission or generation contingencies. This generating capacity is necessary to: -supply requirements for load variations. -replace generating capacity and energy lost due to forced outages of generation or transmission equipment. -meet on-demand obligations. -replace energy lost due to curtailment of interruptible imports. a. Minimum Operating Reserve. Each Balancing Authority shall maintain minimum Operating Reserve which is the sum of the following: (i) Regulating reserve. Sufficient Spinning Reserve, immediately responsive to Automatic Generation Control (AGC) to provide sufficient regulating margin to allow the Balancing Authority to meet NERC’s Control Performance Criteria (see BAL-001-0). (ii) Contingency reserve. An amount of Spinning Reserve and Nonspinning Reserve (at least half of which must be Spinning Reserve), sufficient to meet the NERC Disturbance Control Standard BAL-002-0, equal to the greater of: (a) The loss of generating capacity due to forced outages of generation or transmission equipment that would result from the most severe single contingency; or (b) The sum of five percent of the load responsibility served by hydro generation and seven percent of the load responsibility served by thermal generation. The combined unit ramp rate of each Balancing Authority’s on-line, unloaded generating capacity must be capable of responding to the Spinning Reserve requirement of that Balancing Authority within ten minutes (iii) Additional reserve for interruptible imports. An amount of reserve, which can be made effective within ten minutes, equal to interruptible imports. (iv) Additional reserve for on-demand obligations. An amount of reserve, which can be made effective within ten minutes, equal to on-demand obligations to other entities or Balancing Authorities b. Acceptable types of Nonspinning Reserve. The Nonspinning Reserve obligations identified in subsections a (ii), a (iii), and a (iv), if any, can be met by use of the following: (i) interruptible load; (ii) interruptible exports; (iii) on-demand rights from other entities or Balancing Authorities; (iv) Spinning Reserve in excess of requirements in subsections a (i) and a (ii); or (v) off-line generation which qualifies as Nonspinning Reserve. c. Knowledge of Operating Reserve. Operating Reserves shall be calculated such that the amount available which can be fully activated in the next ten minutes will be known at all times. d. Restoration of Operating Reserve. After the occurrence of any event necessitating the use of Operating Reserve, that reserve shall be restored as promptly as practicable. The time taken to restore reserves shall not exceed 60 minutes (Source: WECC Criterion) |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RR07-11-000 | BA | [17 empty] | RSG
Inactive | BAL | BAL-STD | BAL-STD-002-0 | No Parts for W1. |  |  |  | 2007-03-12 | 2007-03-26 | 2007-06-08 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RR07-11-000
Inactive | CIP | CIP-001 | CIP-001-0 | 1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable) | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable)
Inactive | CIP | CIP-001 | CIP-001-0 | 2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable) | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable)
Inactive | CIP | CIP-001 | CIP-001-0 | 3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable) | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable)
Inactive | CIP | CIP-001 | CIP-001-0 | 4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable) | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Replaced with CIP-001-1 (CIP-001-0 was never enforceable)
Inactive | CIP | CIP-001 | CIP-001-1 | 1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | CIP | CIP-001 | CIP-001-1 | 2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | CIP | CIP-001 | CIP-001-1 | 3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | CIP | CIP-001 | CIP-001-1 | 4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | CIP | CIP-001 | CIP-001-1a | 1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1a | No Parts for 1. |  |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000
Inactive | CIP | CIP-001 | CIP-001-1a | 2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1a | No Parts for 2. |  |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000
Inactive | CIP | CIP-001 | CIP-001-1a | 3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1a | No Parts for 3. |  |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000
Inactive | CIP | CIP-001 | CIP-001-1a | 4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001 | CIP-001-1a | No Parts for 4. |  |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD10-11-000
Inactive | CIP | CIP-001 | CIP-001-2a | EA.1. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for EA.1. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | EA.2. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for EA.2. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | EA.3. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for EA.3. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | EA.4. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall establish communications contacts with local Federal Bureau of Investigation (FBI) officials and develop reporting procedures as appropriate to their circumstances. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for EA.4. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | 1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for 1. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | 2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for 2. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | 3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for 3. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-001 | CIP-001-2a | 4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000 | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001 | CIP-001-2a | No Parts for 4. |  |  |  | 2011-02-17 | 2011-06-21 | 2011-08-02 | 2011-08-02 | 2011-10-01 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RD11-6-000
Inactive | CIP | CIP-002 | CIP-002-1 | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2. | The risk-based assessment shall consider the following assets: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-04-07 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 2. | Critical Asset Identification - The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000
Inactive | CIP | CIP-002 | CIP-002-1 | 3. | Critical Cyber Asset Identification - Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 3.3. | The Cyber Asset is dial-up accessible. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | 4. | Annual Approval - A senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-1 | No Parts for 4. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000 RM06-22-000
Inactive | CIP | CIP-002 | CIP-002-2 | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2. | The risk-based assessment shall consider the following assets: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | No Parts for 2. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-002 | CIP-002-2 | 3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-2, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 3.3. | The Cyber Asset is dial-up accessible. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | 4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-2 | No Parts for 4. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-002 | CIP-002-3 | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets.. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2. | The risk-based assessment shall consider the following assets: | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | No Parts for 2. |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-002 | CIP-002-3 | 3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 3.3. | The Cyber Asset is dial-up accessible. | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | 4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3 | No Parts for 4. |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-002 | CIP-002-3a | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2. | The risk-based assessment shall consider the following assets: |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | No Parts for 2. |  |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13
Inactive | CIP | CIP-002 | CIP-002-3a | 3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 3.3. | The Cyber Asset is dial-up accessible. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | 4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3a | No Parts for 4. |  |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-5-000 FERC remanded the interpretation of R3 in an order issued on 3/21/13
Inactive | CIP | CIP-002 | CIP-002-3b | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2. | The risk-based assessment shall consider the following assets: | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | No Parts for 2. |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30
Inactive | CIP | CIP-002 | CIP-002-3b | 3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 3.3. | The Cyber Asset is dial-up accessible. | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | 4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3b | No Parts for 4. |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. | Operations Planning | 2013-02-07 | [8 empty] | 2016-06-30
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2. | The risk-based assessment shall consider the following assets: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | CIP | CIP-002 | CIP-002-3(i) | 3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i), Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 3.3. | The Cyber Asset is dial-up accessible. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | 4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i) | No Parts for 4. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. See Standard for Requirement Parts |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2. | The risk-based assessment shall consider the following assets: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i)b, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 3.3. | The Cyber Asset is dial-up accessible. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | 4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-3(i)b | No Parts for 4. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | CIP | CIP-002 | CIP-002-4 | 1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-4 | No Parts for 1. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-002 | CIP-002-4 | 2. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-4 | No Parts for 2. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-002 | CIP-002-4 | 3. | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-4 | No Parts for 3. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-002 | CIP-002-4a | 1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-4a | No Parts for 1. |  |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | FERC remanded the interpretation of R3 in an order issued on 3/21/13
Inactive | CIP | CIP-002 | CIP-002-4a | 2. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-4a | No Parts for 2. |  |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | FERC remanded the interpretation of R3 in an order issued on 3/21/13
Inactive | CIP | CIP-002 | CIP-002-4a | 3. | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | FERC remanded the interpretation of R3 in an order issued on 3/21/13 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002 | CIP-002-4a | No Parts for 3. |  |  |  | 2012-05-09 | 2012-08-01 | [7 empty] | 2013-03-21 | FERC remanded the interpretation of R3 in an order issued on 3/21/13
Inactive | CIP | CIP-002 | CIP-002-5 | 1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5 | 1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5 | 1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5 | 1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5 | 2. | The Responsible Entity shall: [See Standard for sub-req's] |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5 | 2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5 | 2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  |  | 2012-11-26 | 2013-01-31 | [7 empty] | 2014-02-03 | Replaced with CIP-002-5.1 (Errata) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 2. | The Responsible Entity shall: [See Standard for sub-req's] | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-5.1 | 2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2016-12-26 | Filing/Order Docket No. RM13-5-000 Errata approved by the SC on 9/27/2013 | BA | DP | DP-UFLS |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 2. | The Responsible Entity shall: | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002 | CIP-002-5.1a | 2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2016-11-02 | 2016-11-28 | 2016-12-27 | 2016-12-27 | 2016-12-27 | 2016-12-27 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD17-2-000 CIP-002-5.1a replaced CIP-002-5.1 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Remedial Action Schemes that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 1.1. | Identify each of the high impact BES Cyber System according to Attachment 1, Section 1, if any, at each asset; | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 1.2. | Identify each of the medium impact BES Cyber System according to Attachment 1, Section 2, if any, at each asset; and | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 1.3. | 1.3. Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 2. | Each Responsible Entity shall: | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002 | CIP-002-6 | 2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2020-05-14 | 2020-06-12 | [7 empty] | 2021-02-04 | This standard was withdrawn by NERC per request to FERC on 2/5/21 and will never be effective. It was approved by the NERC BOT on 2/4/21. | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of Parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. RAS that support the reliable operation of the BES; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | [5 empty] | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 1.1. | Identify each of the high impact BCS according to Attachment 1, Section 1, if any, at each asset; | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | 2028-07-01 |  |  |  |  | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 1.2. | Identify each of the medium impact BCS according to Attachment 1, Section 2, if any, at each asset; and | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | 2028-07-01 |  |  |  |  | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 1.3. | Identify each asset that contains a low impact BCS according to Attachment 1, Section 3, if any (a discrete list of low impact BCS is not required). | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | 2028-07-01 |  |  |  |  | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 2. | Each Responsible Entity shall: | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | [5 empty] | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | 2028-07-01 |  |  |  |  | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-7 | 2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-03-19 | 2028-07-01 | 2028-07-01 |  |  |  |  | Approved/superseded by CIP-002-8 Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of Parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. RAS that support the reliable operation of the BES; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 1.1. | Identify each of the high impact BCS according to Attachment 1, Section 1, if any, at each asset; | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 1.2. | Identify each of the medium impact BCS according to Attachment 1, Section 2, if any, at each asset; and | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 1.3. | Identify each asset that contains a low impact BCS according to Attachment 1, Section 3, if any (a discrete list of low impact BCS is not required). | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 2. | Each Responsible Entity shall: | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-002 | CIP-002-8 | 2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-1 | 1. | Cyber Security Policy - The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 1.1. | The cyber security policy addresses the requirements in Standards CIP-002 through CIP-009, including provision for emergency situations. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 2. | Leadership - The Responsible Entity shall assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009 |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 2.1. | The senior manager shall be identified by name, title, business phone, business address, and date of designation. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 2.3. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 3. | Exceptions - Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures, or a statement accepting risk. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 4. | Information Protection - The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 5.1.1. | Personnel shall be identified by name, title, business phone and the information for which they are responsible for authorizing access. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | 6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-1 | No Parts for 6. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 Replaced with CIP-003-2
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1. | For its high impact and medium impact BCS, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.1. | Personnel and training (CIP-004); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.2.1. | Cyber security awareness; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.3. | Physical security of BCS (CIP-006); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.4. | System security management (CIP-007); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.5. | Incident reporting and response planning (CIP-008); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.6. | Recovery plans for BCS (CIP-009); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.7. | Configuration change management and vulnerability assessments (CIP-010); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.8. | Information protection (CIP-011); and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2. | For its assets identified in CIP-002 containing low impact BCS, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.1. | Cyber security awareness; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.2. | Physical security controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.3. | Electronic access controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.4. | Cyber Security Incident response; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.5. | Transient Cyber Assets (TCA) and Removable Media malicious code risk mitigation; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.6. | Vendor electronic remote access security controls; and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 1.2.7. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BCS shall implement one or more documented cyber security plan(s) for its low impact BCS, and Shared Cyber Infrastructure (SCI) that supports a low impact BCS, that include the sections in Attachment 1. | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | No Parts for 2. |  | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | No Parts for 3. |  | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | 4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-10 | No Parts for 4. |  | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 |  |  |  |  | 2029-06-30 | Filing/Order Docket No. RM24-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1. | For its high impact and medium impact BCS, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.1. | Personnel and training (CIP-004); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.3. | Physical security of BCS (CIP-006); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.4. | System security management (CIP-007); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.5. | Incident reporting and response planning (CIP-008); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.6. | Recovery plans for BCS (CIP-009); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.7. | Configuration change management and vulnerability assessments (CIP-010); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.8. | Information protection (CIP-011); and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2. | For its assets identified in CIP-002 containing low impact BCS, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2.1. | Cyber security awareness; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2.2. | Physical security controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2.3. | Electronic access controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2.4. | Cyber Security Incident response; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2.5. | Transient Cyber Assets (TCA) and Removable Media malicious code risk mitigation; and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 1.2.6. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | 2029-07-01 |  |  |  |  | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BCS shall implement one or more documented cyber security plan(s) for its low impact BCS, and Shared Cyber Infrastructure (SCI) that supports a low impact BCS, that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BCS or their BES Cyber Assets (BCA) is not required. Lists of authorized users are not required. | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | No Parts for 2. |  | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high-level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | No Parts for 3. |  | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high-level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | 4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003 | CIP-003-11 | No Parts for 4. |  | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2024-12-10 | 2024-12-20 | 2026-03-19 | 2026-05-26 | 2029-07-01 | [5 empty] | Filing/Order Docket No. RM25-8-000
Inactive | CIP | CIP-003 | CIP-003-2 | 1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 1.1. | The cyber security policy addresses the requirements in Standards CIP-002-2 through CIP-009-2, including provision for emergency situations. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 2.1. | The senior manager shall be identified by name, title, and date of designation. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 2.3. | Where allowed by Standards CIP-002-2 through CIP-009-2, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-2, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | 6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-2 | No Parts for 6. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 Replaced with CIP-003-3
Inactive | CIP | CIP-003 | CIP-003-3 | 1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 2.1. | The senior manager shall be identified by name, title, and date of designation. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | 6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3 | No Parts for 6. |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-003 | CIP-003-3a | 1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 2.1. | The senior manager shall be identified by name, title, and date of designation. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | M3. The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). | M3. The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. | M3. The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. | M3. The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | 6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-3a | No Parts for 6. |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30
Inactive | CIP | CIP-003 | CIP-003-4 | 1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 1.1. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 2.1. | The senior manager shall be identified by name, title, and date of designation. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 2.3. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-01-21 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-01-21 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-01-21 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-01-21 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | 6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4 | No Parts for 6. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-003 | CIP-003-4a | 1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 1.1. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 2.1. | The senior manager shall be identified by name, title, and date of designation. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 2.3. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | 6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | Operations Planning | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003 | CIP-003-4a | No Parts for 6. |  |  | Operations Planning | 2013-11-07 | [8 empty] | 2014-02-03
Inactive | CIP | CIP-003 | CIP-003-5 | 1. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.1. | Personnel & training (CIP-004); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.3. | Physical security of BES Cyber Systems (CIP-006); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.4. | System security management (CIP-007); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.5. | Incident reporting and response planning (CIP-008); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.6. | Recovery plans for BES Cyber Systems (CIP-009); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.7. | Configuration change management and vulnerability assessments (CIP-010); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.8. | Information protection (CIP-011); and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 1.9. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 2. | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 2.1. | Cyber security awareness; | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 2.2. | Physical security controls; | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 2.3. | Electronic access controls for external routable protocol connections and Dial-up Connectivity; and | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 2.4. | Incident response to a Cyber Security Incident. | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | No Parts for 3. |  | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6.
Inactive | CIP | CIP-003 | CIP-003-5 | 4. | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-5 | No Parts for 4. |  | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2017-03-31 | Filing/Order Docket No. RM13-5-000 CIP-003-5 will be superseded by CIP-003-6.
Inactive | CIP | CIP-003 | CIP-003-6 | 1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1. | For its high impact and medium impact BES Cyber Systems, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.1. | Personnel and training (CIP-004); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.3. | Physical security of BES Cyber Systems (CIP-006); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.4. | System security management (CIP-007); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.5. | Incident reporting and response planning (CIP-008); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.7. | Configuration change management and vulnerability assessments (CIP-010); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.8. | Information protection (CIP-011); and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-04-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.2.1. | Cyber security awareness; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-04-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.2.2. | Physical security controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-04-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.2.3. | Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity; and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-04-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 1.2.4. | Cyber Security Incident response | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-04-01 | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | 2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. | Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X | R2, Attachment 1, Sections 1 and 4 are effective on 4/1/2017 ¦ Attachment 1 - Sections 2 and 3 are effective on 9/1/2018* |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | No Parts for 2. |  | Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X | R2, Attachment 1, Sections 1 and 4 are effective on 4/1/2017 ¦ Attachment 1 - Sections 2 and 3 are effective on 9/1/2018* |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie
Inactive | CIP | CIP-003 | CIP-003-6 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | No Parts for 3. |  | An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie
Inactive | CIP | CIP-003 | CIP-003-6 | 4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-6 | No Parts for 4. |  | An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2019-12-31 | Filing/Order Docket No. RM15-14-000 With the approval of CIP-003-7 and its associated Implementation Plan, entities will not be required to implement CIP-003-6, Requirement R2, Attachment 1, Sections 2 and 3. Instead, entitie
Inactive | CIP | CIP-003 | CIP-003-7 | 1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1. | For its high impact and medium impact BES Cyber Systems, if any: | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2018-06-25 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.1. | Personnel and training (CIP-004); | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.3. | Physical security of BES Cyber Systems (CIP-006); | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.4. | System security management (CIP-007); | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.5. | Incident reporting and response planning (CIP-008); | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.7. | Configuration change management and vulnerability assessments (CIP-010); | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.8. | Information protection (CIP-011); and | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2018-06-25 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2.1. | Cyber security awareness; | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2.2. | Physical security controls; | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2.3. | Electronic access controls; | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2.4. | Cyber Security Incident response; | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; and | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 1.2.6. | Declaring and responding to CIP Exceptional Circumstances. | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 | 2020-01-01 |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | 2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | No Parts for 2. |  | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000
Inactive | CIP | CIP-003 | CIP-003-7 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | No Parts for 3. |  | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000
Inactive | CIP | CIP-003 | CIP-003-7 | 4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-7 | No Parts for 4. |  | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2017-02-10 | 2017-03-03 | 2018-04-19 | 2018-06-25 | 2020-01-01 |  |  |  |  | 2020-03-31 | Filing/Order Docket No. RM17-11-000
Inactive | CIP | CIP-003 | CIP-003-8 | 1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1. | For its high impact and medium impact BES Cyber Systems, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.1. | Personnel and training (CIP-004); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.3. | Physical security of BES Cyber Systems (CIP-006); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.4. | System security management (CIP-007); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.5. | Incident reporting and response planning (CIP-008); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.7. | Configuration change management and vulnerability assessments (CIP-010); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.8. | Information protection (CIP-011); and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2.1. | Cyber security awareness; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2.2. | Physical security controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2.3. | Electronic access controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2.4. | Cyber Security Incident response; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 1.2.6. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 | 2020-04-01 |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | 2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | No Parts for 2. |  | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000
Inactive | CIP | CIP-003 | CIP-003-8 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | No Parts for 3. |  | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000
Inactive | CIP | CIP-003 | CIP-003-8 | 4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003 | CIP-003-8 | No Parts for 4. |  | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2019-05-09 | 2019-05-21 | 2019-07-31 | 2019-07-31 | 2020-04-01 |  |  |  |  | 2026-03-31 | Filing/Order Docket No. RD19-5-000
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1. | For its high impact and medium impact BES Cyber Systems, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.1. | Personnel and training (CIP‐004); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.2. | Electronic Security Perimeters (CIP‐005) including Interactive Remote Access; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.3. | Physical security of BES Cyber Systems (CIP‐006); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.4. | System security management (CIP‐007); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.5. | Incident reporting and response planning (CIP‐008); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.6. | Recovery plans for BES Cyber Systems(CIP‐009); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.7. | Configuration change management and vulnerability assessments (CIP‐ 010); | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.8. | Information protection (CIP‐011); and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2. | For its assets identified in CIP‐002 containing low impact BES Cyber Systems, if any: | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.1. | Cyber security awareness; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.2. | Physical security controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.3. | Electronic access controls; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.4. | Cyber Security Incident response; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.6. | Vendor electronic remote access security controls; and | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 1.2.7. | Declaring and responding to CIP Exceptional Circumstances. | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 | 2026-04-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 2. | Each Responsible Entity with at least one asset identified in CIP‐002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | No Parts for 2. |  | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager.M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | No Parts for 3. |  | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager.M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | 4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003 | CIP-003-9 | No Parts for 4. |  | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | Operations Planning | 2022-11-16 | 2022-12-06 | 2023-03-16 | 2023-03-16 | 2026-04-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD23-3-000
Inactive | CIP | CIP-004 | CIP-004-1 | 1. | Awareness — The Responsible Entity shall establish, maintain, and document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g., emails, memos, computer based training, etc.); Indirect communications (e.g., posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | No Parts for 1. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-004 | CIP-004-1 | 2. | Training — The Responsible Entity shall establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and review the program annually and update as necessary. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained within ninety calendar days of such authorization. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-04-07 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-04-07 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.2.1. | The proper use of Critical Cyber Assets; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.2.3. | The proper handling of Critical Cyber Asset information; and, |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. A personnel risk assessment shall be conducted pursuant to that program within thirty days of such personnel being granted such access. Such program shall at a minimum include: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-1 | 4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-04-07 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g. emails, memos, computer based training, etc.); Indirect communications (e.g. posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | No Parts for 1. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-004 | CIP-004-2 | 2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-2, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.2.1. | The proper use of Critical Cyber Assets; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.2.3. | The proper handling of Critical Cyber Asset information; and, |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-2 | 4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | No Parts for 1. |  |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-004 | CIP-004-3 | 2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.2.1. | The proper use of Critical Cyber Assets; |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.2.3. | The proper handling of Critical Cyber Asset information; and, |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3 | 4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2012-12-11 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | M1. The Responsible Entity shall make available documentation of its security awareness and reinforcement program as specified in Requirement R1. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | No Parts for 1. |  | M1. The Responsible Entity shall make available documentation of its security awareness and reinforcement program as specified in Requirement R1. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000
Inactive | CIP | CIP-004 | CIP-004-3a | 2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.2.1. | The proper use of Critical Cyber Assets; | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.2.2. | Physical and electronic access controls to Critical Cyber Assets; | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.2.3. | The proper handling of Critical Cyber Asset information; and, | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-3a | 4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2012-12-12 | 2012-12-12 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | No Parts for 1. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-004 | CIP-004-4 | 2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.2.1. | The proper use of Critical Cyber Assets; |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.2.3. | The proper handling of Critical Cyber Asset information; and, |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4 | 4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 |  | 2012-06-25 |  |  |  | 2012-12-11 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | No Parts for 1. |  |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000
Inactive | CIP | CIP-004 | CIP-004-4a | 2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.2.1. | The proper use of Critical Cyber Assets; |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2014-10-01 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2014-10-01 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.2.3. | The proper handling of Critical Cyber Asset information; and, |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2014-10-01 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2014-10-01 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 |  |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-4a | 4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  |  | 2012-05-24 | 2012-08-01 | 2012-12-12 | 2012-12-12 | 2014-10-01 | 2012-12-12 |  |  |  | 2014-02-03 | Filing/Order Docket No. RD12-6-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004 | CIP-004-5 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | Operations Planning | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5 | No Parts for 1. |  |  | Operations Planning | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000
Inactive | CIP | CIP-004 | CIP-004-5 | 2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | Operations Planning | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5 | No Parts for 2. |  |  | Operations Planning | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000
Inactive | CIP | CIP-004 | CIP-004-5 | 3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5 Table R3 – Personnel Risk Assessment Program. |  | Operations Planning | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5 | No Parts for 3. |  |  | Operations Planning | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000
Inactive | CIP | CIP-004 | CIP-004-5 | 4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R4 – Access Management Program. |  | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5 | No Parts for 4. |  |  | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000
Inactive | CIP | CIP-004 | CIP-004-5 | 5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R5 – Access Revocation. |  | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5 | No Parts for 5. |  |  | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | [7 empty] | 2013-09-30 | Filing/Order Docket No. RM13-5-000
Inactive | CIP | CIP-004 | CIP-004-5.1 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1. | Training content on: | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.1. | Cyber security policies; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.2. | Physical access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.3. | Electronic access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.4. | The visitor control program; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.5. | Handling of BES Cyber System Information and its storage; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.7. | Recovery plans for BES Cyber Systems; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.8. | Response to Cyber Security Incidents; and | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.4. | The visitor control program; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 2.5. | The visitor control program; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.1. | Process to confirm identity. | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.2.1. | current residence, regardless of duration; and | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.1.1. | Electronic access; | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.1.2. | Unescorted physical access into a Physical Security Perimeter; and | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.1.3. | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 4.4. | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 5.3. | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 5.4. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-5.1 | 5.5. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2013-09-27 | 2013-09-30 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 CIP-004-5.1 will be superseded by CIP-004-6. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1. | Training content on: | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.1. | Cyber security policies; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.2. | Physical access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.3. | Electronic access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.4. | The visitor control program; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.5. | Handling of BES Cyber System Information and its storage; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.7. | Recovery plans for BES Cyber Systems; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.8. | Response to Cyber Security Incidents; and | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.1. | Process to confirm identity. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: 3.2.1. current residence, regardless of duration; and 3.2.2. other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.2.1. | current residence, regardless of duration; and | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 3.5. | Process to ensure that individuals with unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.1.1. | Electronic access; | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.1.2. | Unescorted physical access into a Physical Security Perimeter; and | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.1.3. | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-10-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.2. (Delete) | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-10-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 4.4. | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 5.3. | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 5.4. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004 | CIP-004-6 | 5.5. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1. | Training content on: | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.1. | Cyber security policies; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.2. | Physical access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.3. | Electronic access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.4. | The visitor control program; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.5. | Handling of BES Cyber System Information and its storage; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.7. | Recovery plans for BES Cyber Systems; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.8. | Response to Cyber Security Incidents; and | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.1. | Process to confirm identity. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.2.1. | current residence, regardless of duration; and | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 4.1.1. | Electronic access; and | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 4.1.2. | Unescorted physical access into a Physical Security Perimeter | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 5.3. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Part 5.1) within 30 calendar days of the effective date of the termination action. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 5.4. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6. | Each Responsible Entity shall implement one or more documented access management program(s) to authorize, verify, and revoke provisioned access to BCSI pertaining to the “Applicable Systems” identified in CIP-004-7 Table R6 – Access Management for BES Cyber System Information that collectively include each of the applicable requirement parts in CIP‐004‐X Table R6 – Access Management for BES Cyber System Information. To be considered access to BCSI in the context of this requirement, an individual has both the ability to obtain and use BCSI. Provisioned access is to be considered the result of the specific actions taken to provide an individual(s) the means to access BCSI (e.g., may include physical keys or access cards, user accounts and associated rights and privileges, encryption keys). | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.1. | Prior to provisioning, authorize (unless already authorized according to Part 4.1.) based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.1.1 | Provisioned electronic access to electronic BCSI; and | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.1.2 | Provisioned physical access to physical BCSI. | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.2. | Verify at least once every 15 calendar months that all individuals with provisioned access to BCSI: | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.2.1 | have an authorization record; and | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.2.2 | still need the provisioned access to perform their current work functions, as determined by the Responsible Entity. | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004 | CIP-004-7 | 6.3. | For termination actions, remove the individual’s ability to use provisioned access to BCSI (unless already revoked according to Part 5.1) by the end of the next calendar day following the effective date of the termination action. | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R1 – Security Awareness Program. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to Applicable Systems. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1. | Training content on: | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.1. | Cyber security policies; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.2. | Physical access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.3. | Electronic access controls; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.4. | The visitor control program; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.5. | Handling of BES Cyber System Information (BCSI) and its storage; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.7. | Recovery plans for BCS; | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.8. | Response to Cyber Security Incidents; and | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.1.9. | Cyber security risks associated with a BCS electronic interconnectivity and interoperability with other Cyber Systems, including Transient Cyber Assets (TCA), and with Removable Media. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to Applicable Systems, except during CIP Exceptional Circumstances. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to Applicable Systems that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.1. | Process to confirm identity. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.2.1. | current residence, regardless of duration; and | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed, except during CIP Exceptional Circumstances, according to Parts 3.1 through 3.4 within the last seven years. | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 4.1.1. | Electronic access; and | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 4.1.2. | Unescorted physical access into a Physical Security Perimeter (PSP) (except for medium impact BCS without ERC). | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 5.1. | A process to initiate removal of an individual’s ability for unescorted physical access (except for medium impact BCS without ERC) and Interactive Remote Access (IRA) upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts; and authorized unescorted physical access (except for medium impact BCS without ERC) that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 5.3. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Part 5.1) within 30 calendar days of the effective date of the termination action. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 5.4. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6. | Each Responsible Entity shall implement one or more documented access management program(s) to authorize, verify, and revoke provisioned access to BCSI pertaining to the Applicable Systems identified in CIP-004-8 Table R6 – Access Management for BES Cyber System Information that collectively include each of the applicable requirement parts in CIP‐004‐8 Table R6 – Access Management for BES Cyber System Information. To be considered access to BCSI in the context of this requirement, an individual has both the ability to obtain and use BCSI. Provisioned access is to be considered the result of the specific actions taken to provide an individual(s) the means to access BCSI (e.g., may include physical keys or access cards, user accounts and associated rights and privileges, encryption keys). | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.1. | Prior to provisioning, authorize (unless already authorized according to Part 4.1) based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.1.1. | Provisioned electronic access to electronic BCSI; and | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.1.2. | Provisioned physical access to physical BCSI (except for BCSI at a medium impact BCS without ERC). | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.2. | Verify at least once every 15 calendar months that all individuals with provisioned access to BCSI: | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.2.1. | have an authorization record; and | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.2.2. | still need the provisioned access to perform their current work functions, as determined by the Responsible Entity. | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-004 | CIP-004-8 | 6.3. | For termination actions, remove the individual’s ability to use provisioned access to BCSI (unless already revoked according to Part 5.1) (except for BCSI at a medium impact BCS without ERC) by the end of the next calendar day following the effective date of the termination action. | M6. Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-1 | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 1.5. | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.3. | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.5. | The required documentation shall, at least, identify and describe: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.5.1. | The processes for access request and authorization. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.5.2. | The authentication methods. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.5.4. | The controls used to secure dial-up accessible connections. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 4.1. | A document identifying the vulnerability assessment process; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 4.3. | The discovery of all access points to the Electronic Security Perimeter; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 4.4. | A review of controls for default accounts, passwords, and network management community strings; and, |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1 | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1.5. | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.3. | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.5. | The required documentation shall, at least, identify and describe: |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.5.1. | The processes for access request and authorization. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.5.2. | The authentication methods. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.5.4. | The controls used to secure dial-up accessible connections. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 4.1. | A document identifying the vulnerability assessment process; |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 4.3. | The discovery of all access points to the Electronic Security Perimeter; |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 4.4. | A review of controls for default accounts, passwords, and network management community strings; and, |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-1a | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  |  | 2010-02-16 | [8 empty] | 2011-02-01 | Replaced with CIP-005-3a | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.5. | The required documentation shall, at least, identify and describe: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.5.1. | The processes for access request and authorization. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.5.2. | The authentication methods. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.5.4. | The controls used to secure dial-up accessible connections. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 4.1. | A document identifying the vulnerability assessment process; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 4.3. | The discovery of all access points to the Electronic Security Perimeter; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 4.4. | A review of controls for default accounts, passwords, and network management community strings; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2 | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.5. | The required documentation shall, at least, identify and describe: |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.5.1. | The processes for access request and authorization. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.5.2. | The authentication methods. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.5.4. | The controls used to secure dial-up accessible connections. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 4.1. | A document identifying the vulnerability assessment process; |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 4.3. | The discovery of all access points to the Electronic Security Perimeter; |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 4.4. | A review of controls for default accounts, passwords, and network management community strings; |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | [5 empty] | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-2a | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 |  | 2011-02-02 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.5. | The required documentation shall, at least, identify and describe: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.5.1. | The processes for access request and authorization. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.5.2. | The authentication methods. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.5.4. | The controls used to secure dial-up accessible connections. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 4.1. | A document identifying the vulnerability assessment process; |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 4.3. | The discovery of all access points to the Electronic Security Perimeter; |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 4.4. | A review of controls for default accounts, passwords, and network management community strings; |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3 | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2011-02-01 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.5. | The required documentation shall, at least, identify and describe: | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.5.1. | The processes for access request and authorization. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.5.2. | The authentication methods. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.5.4. | The controls used to secure dial-up accessible connections. | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. (Retirement approved by FERC effective January 21, 2014.) | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 4.1. | A document identifying the vulnerability assessment process; | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 4.3. | The discovery of all access points to the Electronic Security Perimeter; | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 4.4. | A review of controls for default accounts, passwords, and network management community strings; | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-3a | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. |  | 2010-02-16 | 2010-04-21 | 2011-02-02 | 2011-02-02 | 2011-02-02 | 2011-02-02 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD10-12-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.5. | The required documentation shall, at least, identify and describe: |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.5.1. | The processes for access request and authorization. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.5.2. | The authentication methods. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.5.4. | The controls used to secure dial-up accessible connections. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | Operations Planning | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 4.1. | A document identifying the vulnerability assessment process; |  | Operations Planning | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | Operations Planning | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | Operations Planning | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 4.4. | A review of controls for default accounts, passwords, and network management community strings; |  | Operations Planning | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | Operations Planning | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4 at least annually. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-4a | 5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | Operations Planning, Same-Day Operations | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005 | CIP-005-5 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 2. | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 2.1. | Utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-5 | 2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 2.1. | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 2.4. | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005 | CIP-005-6 | 2.5. | Have one or more method(s) to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 2.1. | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 2.4. | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 2.5. | Have one or more method(s) to disable active vendor remote access including Interactive Remote Access and system-to-system remote access). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 3. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. | M3. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 3.1. | Have one or more method(s) to determine authenticated vendor-initiated remote connections. | M3. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005 | CIP-005-7 | 3.2. | Have one or more method(s) to terminate authenticated vendor-initiated remote connections and control the ability to reconnect. | M3. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1.1. | Applicable Systems connected to a network via a routable protocol must be protected by an ESP. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1.2. | Permit only needed routable protocol communications, documenting the reason, and deny all other routable protocol communications, through the ESP; excluding time sensitive communications of Protection Systems. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1.3. | Protect ESP and SCI configurations by implementing methods to permit only needed network accessibility to Management Interfaces of Applicable Systems, per system capability. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1.4. | Perform authentication when establishing Dial-up Connectivity with Applicable Systems, if any, and per system capability. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1.5. | Have one or more methods for detecting known or suspected malicious routable protocol communications entering or leaving an ESP. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 1.6. | Protect the data traversing communication links used to span a single ESP between PSPs through the use of: - Confidentiality and integrity controls, or - Physical controls that restrict access to the cabling and other non-programmable communication components in those instances when such cabling and components are located outside of a PSP, Excluding: i. Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers subject to CIP-012; and ii.Time-sensitive communication of Protection Systems. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, per system capability, in CIP-005-8 Table R2 – Remote Access Management. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.1. | Permit Interactive Remote Access (IRA), if any, only through an Intermediate System. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.2. | Protect the confidentiality and integrity of IRA communications between the initiating Cyber Asset or Virtual Cyber Asset and the Intermediate System. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.3. | Require multi-factor authentication to the Intermediate System for IRA communications between the initiating Cyber Asset or Virtual Cyber Asset and the Intermediate System. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.4. | Have one or more methods for determining active vendor remote access sessions (including IRA and system-to-system remote access). | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.5. | Have one or more method(s) to disable active vendor remote access (including IRA and system-to-system remote access). | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.6. | Prevent Intermediate System(s) from sharing CPU resources and memory resources with any part of a high or medium impact BCS or associated PCAs. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 2.7. | Intermediate System(s) used to access an Applicable System in Part 2.1 | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 3. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-8 Table R3 –Vendor Remote Access Management for EACMS, PACS, and SCI. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R3 – Vendor Remote Access Management for EACMS, PACS, and SCI and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 3.1. | Have one or more method(s) to determine authenticated vendor-initiated remote connections. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R3 – Vendor Remote Access Management for EACMS, PACS, and SCI and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-005 | CIP-005-8 | 3.2. | Have one or more method(s) to terminate authenticated vendor-initiated remote connections and control the ability to reconnect. | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R3 – Vendor Remote Access Management for EACMS, PACS, and SCI and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-1 | 1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been pened without authorization. These alarms must provide for immediate notificationto personnel responsible for response. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 5. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | No Parts for 5. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-006 | CIP-006-1 | 6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1 | 6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 5. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | No Parts for 5. |  |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed
Inactive | CIP | CIP-006 | CIP-006-1a | 6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1a | 6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2008-02-12 | [8 empty] | 2009-12-22 | Replaced with CIP-006-1b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 5. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | No Parts for 5. |  |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed
Inactive | CIP | CIP-006 | CIP-006-1b | 6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1b | 6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2009-08-05 | [8 empty] | 2009-12-22 | Replaced with CIP-006-2b and included as part of CIP-006-2b filing; inactive as of the date CIP-006-2b was filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 5. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | No Parts for 5. |  |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed)
Inactive | CIP | CIP-006 | CIP-006-1c | 6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-1c | 6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2010-02-16 | [8 empty] | 2010-04-20 | Replaced with CIP-006-2c (filed as CIP-006-2c because CIP-006-1 was inactive as of the filing date and the interpretation equally applied to CIP-006-2; inactive as of the date CIP-006-2c was filed) | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 1.8. | Annual review of the physical security plan. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 2.1. | Be protected from unauthorized physical access. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | No Parts for 3. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-006 | CIP-006-2 | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | No Parts for 4. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-006 | CIP-006-2 | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | No Parts for 5. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-006 | CIP-006-2 | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | No Parts for 6. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-006 | CIP-006-2 | 7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | No Parts for 7. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-006 | CIP-006-2 | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2 | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-07-14 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 1.8. | Annual review of the physical security plan. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 2.1. | Be protected from unauthorized physical access. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | No Parts for 3. |  |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2a | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | No Parts for 4. |  |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2a | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | No Parts for 5. |  |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2a | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | No Parts for 6. |  |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2a | 7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | No Parts for 7. |  |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2a | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2a | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2009-05-06 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-07-15 | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 1.8. | Annual review of the physical security plan. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 2.1. | Be protected from unauthorized physical access. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | No Parts for 3. |  |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-2b | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | No Parts for 4. |  |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-2b | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | No Parts for 5. |  |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-2b | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | No Parts for 6. |  |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-2b | 7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | No Parts for 7. |  |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-2b | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2b | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2009-08-05 | 2009-12-22 | 2011-05-19 | [6 empty] | 2010-07-14 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 1.8. | Annual review of the physical security plan. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 2.1. | Be protected from unauthorized physical access. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | No Parts for 3. |  |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2c | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | No Parts for 4. |  |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2c | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | No Parts for 5. |  |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2c | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | No Parts for 6. |  |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2c | 7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | No Parts for 7. |  |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000
Inactive | CIP | CIP-006 | CIP-006-2c | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-2c | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2010-02-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 |  | 2010-07-15 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 1.8. | Annual review of the physical security plan. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 2.1. | Be protected from unauthorized physical access. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | No Parts for 3. |  |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-006 | CIP-006-3 | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | No Parts for 4. |  |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-006 | CIP-006-3 | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | No Parts for 5. |  |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-006 | CIP-006-3 | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | No Parts for 6. |  |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-006 | CIP-006-3 | 7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | No Parts for 7. |  |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-006 | CIP-006-3 | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | [5 empty] | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3 | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 |  | 2010-03-31 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-10-01 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 1.8. | Annual review of the physical security plan. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 2.1. | Be protected from unauthorized physical access. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | No Parts for 3. |  |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000
Inactive | CIP | CIP-006 | CIP-006-3a | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | No Parts for 4. |  |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000
Inactive | CIP | CIP-006 | CIP-006-3a | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | No Parts for 5. |  |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000
Inactive | CIP | CIP-006 | CIP-006-3a | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | No Parts for 6. |  |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000
Inactive | CIP | CIP-006 | CIP-006-3a | 7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | No Parts for 7. |  |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000
Inactive | CIP | CIP-006 | CIP-006-3a | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 |  |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3a | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2009-12-16 | 2010-04-20 | 2010-07-15 | 2010-07-15 | 2010-10-01 | 2010-07-15 |  |  |  | 2011-05-18 | RFiling/Order Docket No. D10-13-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 1.8. | Annual review of the physical security plan. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 2.1. | Be protected from unauthorized physical access. | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | M3. The Responsible Entity shall make available documentation that the electronic access control systems are located within an identified Physical Security Perimeter as specified in Requirement R3. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | No Parts for 3. |  | M3. The Responsible Entity shall make available documentation that the electronic access control systems are located within an identified Physical Security Perimeter as specified in Requirement R3. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-3c | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation identifying the methods for controlling physical access to each access point of a Physical Security Perimeter as specified in Requirement R4. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | No Parts for 4. |  | M4. The Responsible Entity shall make available documentation identifying the methods for controlling physical access to each access point of a Physical Security Perimeter as specified in Requirement R4. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-3c | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | M5. The Responsible Entity shall make available documentation identifying the methods for monitoring physical access as specified in Requirement R5. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | No Parts for 5. |  | M5. The Responsible Entity shall make available documentation identifying the methods for monitoring physical access as specified in Requirement R5. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-3c | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | M6. The Responsible Entity shall make available documentation identifying the methods for logging physical access as specified in Requirement R6. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | No Parts for 6. |  | M6. The Responsible Entity shall make available documentation identifying the methods for logging physical access as specified in Requirement R6. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-3c | 7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | M7. The Responsible Entity shall make available documentation to show retention of access logs as specified in Requirement R7. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | No Parts for 7. |  | M7. The Responsible Entity shall make available documentation to show retention of access logs as specified in Requirement R7. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000
Inactive | CIP | CIP-006 | CIP-006-3c | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3c | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. |  | 2010-02-16 | 2009-12-22 | 2011-05-19 | 2011-05-19 | 2011-05-19 | 2011-05-19 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RD10-8-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 1.8. | Annual review of the physical security plan. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 2.1. | Be protected from unauthorized physical access. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | No Parts for 3. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-3d | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | No Parts for 4. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-3d | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | No Parts for 5. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-3d | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | No Parts for 6. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-3d | 7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | No Parts for 7. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-3d | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-3d | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.7 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 1.8. | Annual review of the physical security plan. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 2.1. | Be protected from unauthorized physical access. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | No Parts for 3. |  |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000
Inactive | CIP | CIP-006 | CIP-006-4c | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | No Parts for 4. |  |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000
Inactive | CIP | CIP-006 | CIP-006-4c | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | No Parts for 5. |  |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000
Inactive | CIP | CIP-006 | CIP-006-4c | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | No Parts for 6. |  |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000
Inactive | CIP | CIP-006 | CIP-006-4c | 7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | No Parts for 7. |  |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000
Inactive | CIP | CIP-006 | CIP-006-4c | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4c | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  |  | 2011-01-24 | 2011-04-12 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 1.8. | Annual review of the physical security plan. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 2.1. | Be protected from unauthorized physical access. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | No Parts for 3. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-4d | 4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | No Parts for 4. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-4d | 5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | No Parts for 5. |  |  |  | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-4d | 6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | No Parts for 6. |  |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-4d | 7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | No Parts for 7. |  |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000
Inactive | CIP | CIP-006 | CIP-006-4d | 8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-4d | 8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | Long-Term Planning, Same-Day Operations | 2012-02-09 | 2012-05-23 | [7 empty] | 2013-03-21 | Filing/Order Docket No. RD12-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006 | CIP-006-5 | 1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.1. | Define operational or procedural controls to restrict physical access. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.3. | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.4. | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.6. | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 2.2. | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 2.3. | Retain visitor logs for at least ninety calendar days. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program. | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-5 | 3.1. | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1. | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.1. | Define operational or procedural controls to restrict physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.10. | Restrict physical access to cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. Where physical access restrictions to such cabling and components are not implemented, the Responsible Entity shall document and implement one or more of the following: • encryption of data that transits such cabling and components; or • monitoring the status of the communication link composed of such cabling and components and issuing an alarm or alert in response to detected communication failures to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection; or • an equally effective logical protection. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.2. DO NOT USE | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.3. | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.3. DO NOT USE | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.4. | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.6. | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 2. | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 2.2. | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 2.3. | Retain visitor logs for at least ninety calendar days. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006 | CIP-006-6 | 3.1. | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 See Implementation Plan for Compliance dates. | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1. | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.1. | Define operational or procedural controls to restrict physical access. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable PSP to only those individuals who have authorized unescorted physical access. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.3. | Utilize two or more different physical access controls (this does not require two completely independent PACS) to collectively allow unescorted physical access into PSPs to only those individuals who have authorized unescorted physical access, per system capability. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.4. | Monitor for unauthorized access through a physical access point into a PSP. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a PSP to the personnel identified in the Cyber Security Incident response plan within 15 minutes of detection. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.6. | Monitor each PACS for unauthorized physical access to a PACS. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a PACS to the personnel identified in the Cyber Security Incident response plan within 15 minutes of the detection. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each PSP, with information to identify the individual and date and time of entry. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each PSP for at least 90 calendar days. | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Operations Planning, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 2. | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each PSP. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 2.2. | Require manual or automated logging of visitor entry into and exit from each PSP that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 2.3. | Retain visitor logs for at least 90 calendar days. | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-7 Table R3 – Maintenance and Testing Program. | Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006 | CIP-006-7 | 3.1. | Maintenance and testing of each PACS and locally mounted hardware or devices at each PSP at least once every 24 calendar months to ensure they function properly. | Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-006-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1. | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.1. | Define operational or procedural controls to restrict physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable PSP to only those individuals who have authorized unescorted physical access. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.3. | Utilize two or more different physical access controls (this does not require two completely independent PACS) to collectively allow unescorted physical access into PSPs to only those individuals who have authorized unescorted physical access, per system capability. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.4. | Monitor for unauthorized access through a physical access point into a PSP. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a PSP to the personnel identified in the Cyber Security Incident response plan within 15 minutes of detection. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.6. | Monitor each PACS for unauthorized physical access to a PACS. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a PACS to the personnel identified in the Cyber Security Incident response plan within 15 minutes of the detection. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each PSP, with information to identify the individual and date and time of entry. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each PSP for at least 90 calendar days. | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7.1 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | Long-Term Planning, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 2. | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-7.1 Table R2 – Visitor Control Program. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each PSP. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 2.2. | Require manual or automated logging of visitor entry into and exit from each PSP that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 2.3. | Retain visitor logs for at least 90 calendar days. | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R3 – Maintenance and Testing Program. | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-006 | CIP-006-7.1 | 3.1. | Maintenance and testing of each PACS and locally mounted hardware or devices at each PSP at least once every 24 calendar months to ensure they function properly. | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-7.1 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-006-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-1 | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-04-07 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 1.3. | The Responsible Entity shall document test results. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 2. | Ports and Services — The Responsible Entity shall establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, shall establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003 Requirement R5. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement R4. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.3.1. | Each password shall be a minimum of six characters. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 7. | Disposal or Redeployment — The Responsible Entity shall establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 8.1. | A document identifying the vulnerability assessment process; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 8.3. | A review of controls for default accounts; and, |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2009-02-02 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007 at least annually. Changes resulting from modifications to the systems or controls shall be documented within ninety calendar days of the change. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-1 | No Parts for 9. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-007 | CIP-007-2 | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 1.3. | The Responsible Entity shall document test results. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.3.1. | Each password shall be a minimum of six characters. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 8.1. | A document identifying the vulnerability assessment process; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 8.3. | A review of controls for default accounts; and, |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 |  | 2009-09-30 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2 | No Parts for 9. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | [5 empty] | 2010-03-31 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-007 | CIP-007-2a | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 1.3. | The Responsible Entity shall document test results. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.3.1. | Each password shall be a minimum of six characters. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-04-01 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | Operations Planning, Same-Day Operations | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | Operations Planning, Same-Day Operations | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | Operations Planning, Same-Day Operations | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | Operations Planning, Same-Day Operations | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | Operations Planning, Same-Day Operations | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | Operations Planning, Same-Day Operations | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 8.1. | A document identifying the vulnerability assessment process; |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 8.3. | A review of controls for default accounts; and, |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 | 2010-03-18 |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-2a | No Parts for 9. |  |  |  | 2009-11-05 | 2009-11-17 | 2010-03-18 | 2010-03-18 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RD10-3-000
Inactive | CIP | CIP-007 | CIP-007-3 | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security testprocedures in a manner that minimizes adverse effects on the production system or its operation. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 1.3. | The Responsible Entity shall document test results. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.3.1. | Each password shall be a minimum of six characters. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP008-3. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 8.1. | A document identifying the vulnerability assessment process; | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 8.3. | A review of controls for default accounts; and, | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3 | No Parts for 9. |  | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  | 2009-12-16 | [8 empty] | 2016-06-30 | Never filed
Inactive | CIP | CIP-007 | CIP-007-3a | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 1.3. | The Responsible Entity shall document test results. | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.3.1. | Each password shall be a minimum of six characters. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-10-01 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 8.1. | A document identifying the vulnerability assessment process; | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 8.3. | A review of controls for default accounts; and, | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | M9. The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended. | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3a | No Parts for 9. |  | M9. The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 The version number was updated from CIP-007-3 to CIP-007-3a to incorporate the approved interpretation that should have previously been appended.
Inactive | CIP | CIP-007 | CIP-007-3b | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 1.3. | The Responsible Entity shall document test results. | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | The Responsible Entity shall make available documentation as specified in Requirement R2. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.3.1. | Each password shall be a minimum of six characters. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 8.1. | A document identifying the vulnerability assessment process; | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 8.3. | A review of controls for default accounts; and, | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  | 2013-11-07 | [8 empty] | 2016-06-30 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-3b | No Parts for 9. |  | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  | 2013-11-07 | [8 empty] | 2016-06-30
Inactive | CIP | CIP-007 | CIP-007-4a | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 1.3. | The Responsible Entity shall document test results. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.3.1. | Each password shall be a minimum of six characters. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 8.1. | A document identifying the vulnerability assessment process; |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 8.3. | A review of controls for default accounts; and, |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4a | No Parts for 9. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-007 | CIP-007-4b | 1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 1.3. | The Responsible Entity shall document test results. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.3.1. | Each password shall be a minimum of six characters. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 8.1. | A document identifying the vulnerability assessment process; |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 8.3. | A review of controls for default accounts; and, |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | 9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  |  | 2013-11-07 | [8 empty] | 2014-02-03 |  | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007 | CIP-007-4b | No Parts for 9. |  |  |  | 2013-11-07 | [8 empty] | 2014-02-03
Inactive | CIP | CIP-007 | CIP-007-5 | 1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R1 – Ports and Services. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-5 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 1.1. | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-5 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or removable media. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-5 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 2.1. | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 2.2. | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: • Apply the applicable patches; or • Create a dated mitigation plan; or • Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 3.1. | Deploy method(s) to deter, detect, or prevent malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 3.2. | Mitigate the threat of detected malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.1. | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.1.1. | Detected successful login attempts; | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.1.2. | Detected failed access attempts and failed login attempts; | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.1.3. | Detected malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.2.1. | Detected malicious code from Part 4.1; and | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.2.2. | Detected failure of Part 4.1 event logging. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.3. | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 4.4. | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R5 – System Access Controls. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.1. | Have a method(s) to enforce authentication of interactive user access, where technically feasible. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.3. | Identify individuals who have authorized access to shared accounts. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.4. | Change known default passwords, per Cyber Asset capability | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.6. | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-5 | 5.7. | Where technically feasible, either: • Limit the number of unsuccessful authentication attempts; or • Generate alerts after a threshold of unsuccessful authentication attempts. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 1.1. | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 2.1. | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 2.2. | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: • Apply the applicable patches; or • Create a dated mitigation plan; or • Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 3.1. | Deploy method(s) to deter, detect, or prevent malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 3.2. | Mitigate the threat of detected malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.1. | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.1.1. | Detected successful login attempts; | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.1.2. | Detected failed access attempts and failed login attempts; | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.1.3. | Detected malicious code. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.2.1. | Detected malicious code from Part 4.1; and | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.2.2. | Detected failure of Part 4.1 event logging. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.3. | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.3. DO NOT USE | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 4.4. | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-15 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.1. | Have a method(s) to enforce authentication of interactive user access, where technically feasible. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.3. | Identify individuals who have authorized access to shared accounts. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.4. | Change known default passwords, per Cyber Asset capability | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.6. | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.6. DO NOT USE | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.7. | Where technically feasible, either: • Limit the number of unsuccessful authentication attempts; or • Generate alerts after a threshold of unsuccessful authentication attempts. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007 | CIP-007-6 | 5.7. DO NOT USE | Where technically feasible, either:  Limit the number of unsuccessful authentication attempts; or  Generate alerts after a threshold of unsuccessful authentication attempts. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 1.1. | Disable or prevent unneeded routable protocol network accessibility on each Applicable System, per system capability. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 1.3. | Mitigate the risk of CPU or memory vulnerabilities by preventing the sharing of CPU resources and memory resources, excluding storage resources, between VCAs that are, or are associated with, a medium or high impact BCS, and VCAs that are not, or are not associated with, a medium or high impact BCS. | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 2.1. | A patch management process for tracking, evaluating, and installing cyber security patches. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for Applicable Systems that are updateable and for which a patching source exists | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 2.2. | At least once every 35 calendar days, evaluate cyber security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: • Apply the applicable patches; • Create a dated mitigation plan; or • Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each cyber security patch and a timeframe to complete these mitigations. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 3.1. | Deploy method(s) to deter, detect, or prevent malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 3.2. | Mitigate the threat of detected malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.1. | Log security events, per system capability, for identification of, and after-the-fact investigations of, Cyber Security Incidents that include, at a minimum, each of the types of events identified in Parts R4.1.1, R4.1.2, and R4.1.3. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.1.1. | Detected successful login attempts; | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.1.2. | Detected failed access attempts and failed login attempts; | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.1.3. | Detected malicious code. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert that includes, as a minimum, each of the types of events (per system capability) indicated in Parts R4.2.1 and R4.2.2. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.2.1. | Detected malicious code from Part 4.1; | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.2.2. | Detected failure of Part 4.1 event logging. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.3. | Retain applicable security event logs identified in Part 4.1 for at least the last 90 consecutive calendar days, per system capability, except under CIP Exceptional Circumstances. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 4.4. | Review a summarization or sampling of logged security events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R5 – System Access Controls. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.1. | Have a method(s) to enforce authentication of interactive user access, per system capability. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.3. | Identify individuals who have authorized access to shared accounts. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.4. | Change known default passwords, per system capability | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the password parameters indicated in Parts R5.5.1 and R5.5.2 | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Applicable Systems; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Applicable System. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.6. | For password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months, per system capability. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007 | CIP-007-7 | 5.7. | Limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts, per system capability. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-007-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R1 – System Hardening. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 1.1. | Disable or prevent unneeded routable protocol network accessibility on each Applicable System, per system capability. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 1.3. | Mitigate the risk of CPU or memory vulnerabilities by preventing the sharing of CPU resources and memory resources, excluding storage resources, between VCAs that are, or are associated with, a medium or high impact BCS, and VCAs that are not, or are not associated with, a medium or high impact BCS. | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R2 – Cyber Security Patch Management. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 2.1. | A patch management process for tracking, evaluating, and installing cyber security patches. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for Applicable Systems that are updateable and for which a patching source exists. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 2.2. | At least once every 35 calendar days, evaluate cyber security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: · Apply the applicable patches; · Create a dated mitigation plan; or · Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each cyber security patch and a timeframe to complete these mitigations. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R3 – Malicious Code Prevention. | M3. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 3.1. | Deploy method(s) to deter, detect, or prevent malicious code. | M3. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 3.2. | Mitigate the threat of detected malicious code. | M3. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. | M3. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.1. | Log security events, per system capability, for identification of, and after-the-fact investigations of, Cyber Security Incidents that include, at a minimum, each of the following types of events: | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.1.1. | Detected successful login attempts; | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.1.2. | Detected failed access attempts and failed login attempts; and | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.1.3. | Detected malicious code. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert that includes, as a minimum, each of the following types of events, per system capability: | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.2.1. | Detected malicious code from Part 4.1; and | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.2.2. | Detected failure of Part 4.1 event logging. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.3. | Retain applicable security event logs identified in Part 4.1 for at least the last 90 consecutive calendar days, per system capability, except under CIP Exceptional Circumstances. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 4.4. | Review a summarization or sampling of logged security events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7.1 Table R5 – System Access Controls. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.1. | Have a method(s) to enforce authentication of interactive user access, per system capability. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.3. | Identify individuals who have authorized access to shared accounts. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.4. | Change known default passwords, per system capability | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Applicable Systems; and | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Applicable System. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata)
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.6. | For password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months, per system capability. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-007 | CIP-007-7.1 | 5.7. | Limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts, per system capability. | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7.1 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-007-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-1 | 1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan. The Cyber Security Incident Response plan shall address, at a minimum, the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 1.2. | Response actions, including roles and responsibilities of incident response teams, incident handling procedures, and communication plans. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES ISAC either directly or through an intermediary. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 1.4. | Process for updating the Cyber Security Incident response plan within ninety calendar days of any changes. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | 2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-008 | CIP-008-2 | 1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. Testing the Cyber Security Incident response plan does not require removing a component or system from service during the test. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | 2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | Operations Planning, Real-Time Operations | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-2 | No Parts for 2. |  |  | Operations Planning, Real-Time Operations | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-008 | CIP-008-3 | 1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | Operations Planning, Real-Time Operations | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | 2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | The Responsible Entity shall make available all documentation as specified in Requirement R2. | Operations Assessment | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-3 | No Parts for 2. |  | The Responsible Entity shall make available all documentation as specified in Requirement R2. | Operations Assessment | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-008 | CIP-008-4 | 1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | Operations Assessment | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | 2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008 | CIP-008-4 | No Parts for 2. |  |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-008 | CIP-008-5 | 1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 1.2. | One or more processes to determine if an identified Cyber Security Incident is a Reportable Cyber Security Incident and notify the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), unless prohibited by law. Initial notification to the ES-ISAC, which may be only a preliminary notice, shall not exceed one hour from the determination of a Reportable Cyber Security Incident. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 1.4. | Incident handling procedures for Cyber Security Incidents. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or • With an operational exercise of a Reportable Cyber Security Incident. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2017-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 2.3. | Retain records related to Reportable Cyber Security Incidents. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 |  | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.1.1. | 3.1.1. Document any lessons learned or document the absence of any lessons learned; | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2014-02-03 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.2.1. | Update the Cyber Security Incident response plan(s); and | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-5 | 3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | 2016-07-01 | 2016-07-01 | X |  |  | 2020-12-31 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.2. | One or more processes: | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.2.1. | That include criteria to evaluate and define attempts to compromise; | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.2.2. | To determine if an identified Cyber Security Incident is: • A Reportable Cyber Security Incident; or • An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the “Applicable Systems” column for this Part; and | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.2.3. | To provide notification per Requirement R4. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 1.4. | Incident handling procedures for Cyber Security Incidents. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or • With an operational exercise of a Reportable Cyber Security Incident. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the “Applicable Systems” column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 2.3. | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the “Applicable Systems” column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.1.1. | Document any lessons learned or document the absence of any lessons learned; | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.2.1. | Update the Cyber Security Incident response plan(s); and | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.2.1. DO NOT USE | Update the Cyber Security Incident response plan(s); and | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4. | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4.1. | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4.1.1. | The functional impact; | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4.1.2. | The attack vector used; and | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4.1.3. | The level of intrusion that was achieved or attempted. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4.2. | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines: • One hour after the determination of a Reportable Cyber Security Incident. • By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the “Applicable Systems” column for this Part. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008 | CIP-008-6 | 4.3. | Provide updates, if any, within 7 calendar days of determination of new or changed attribute information required in Part 4.1. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment, Operations Planning | 2019-02-07 | 2019-03-07 | 2019-06-20 | 2019-06-20 | 2021-01-01 | 2021-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD19-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.2. | One or more processes indicated in Parts R1.2.1, R1.2.2, and R1.2.3 | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.2.1. | That include criteria to evaluate and define attempts to compromise; | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.2.2. | To determine if an identified Cyber Security Incident is: • A Reportable Cyber Security Incident; or • An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the Applicable Systems column for this Part; | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.2.3. | To provide notification per Requirement R4. | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 1.4. | Incident handling procedures for Cyber Security Incidents. | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or • With an operational exercise of a Reportable Cyber Security Incident. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the Applicable Systems column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 2.3. | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the Applicable Systems column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.1.1. | Document any lessons learned or document the absence of any lessons learned; | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.2.1. | Update the Cyber Security Incident response plan(s); | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4. | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States Cybersecurity & Infrastructure Security Agency (CISA), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the Applicable Systems column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4.1. | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4.1.1. | The functional impact; | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4.1.2. | The attack vector used; and | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4.1.3. | The level of intrusion that was achieved or attempted. | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4.2. | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines: • One hour after the determination of a Reportable Cyber Security Incident. • By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the Applicable Systems column for this Part. | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008 | CIP-008-7 | 4.3. | Provide updates, if any, within seven calendar days of determination of new or changed attribute information required in Part 4.1. | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-008-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.2. | One or more processes: | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.2.1. | That include criteria to evaluate and define attempts to compromise; | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.2.2. | To determine if an identified Cyber Security Incident is: - A Reportable Cyber Security Incident; or - An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the Applicable Systems column for this Part; and | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.2.3. | To provide notification per Requirement R4. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 1.4. | Incident handling procedures for Cyber Security Incidents. | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7.1 Table R1 – Cyber Security Incident Response Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-7.1 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7.1 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: - By responding to an actual Reportable Cyber Security Incident; - With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or - With an operational exercise of a Reportable Cyber Security Incident. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7.1 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the Applicable Systems column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7.1 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 2.3. | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the Applicable Systems column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7.1 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.1.1. | Document any lessons learned or document the absence of any lessons learned; | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.2.1. | Update the Cyber Security Incident response plan(s); and | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7.1 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4. | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States Cybersecurity & Infrastructure Security Agency (CISA), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the Applicable Systems column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4.1. | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4.1.1. | The functional impact; | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4.1.2. | The attack vector used; and | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4.1.3. | The level of intrusion that was achieved or attempted. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata)
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4.2. | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines: - One hour after the determination of a Reportable Cyber Security Incident. - By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the Applicable Systems column for this Part. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-008 | CIP-008-7.1 | 4.3. | Provide updates, if any, within seven calendar days of determination of new or changed attribute information required in Part 4.1. | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7.1 Table R4 – Notifications and Reporting for Cyber Security Incidents. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-008-7 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-1 | 1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | 1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | 1.2. | Define the roles and responsibilities of responders. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 | 2008-07-01 |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | 2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-009 | CIP-009-1 | 3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within ninety calendar days of the change. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | No Parts for 3. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-009 | CIP-009-1 | 4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | No Parts for 4. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-009 | CIP-009-1 | 5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-1 | No Parts for 5. |  |  |  | 2006-05-02 | 2006-08-28 | 2008-01-18 | 2008-04-07 | 2008-07-01 |  |  |  |  | 2010-03-31 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | CIP | CIP-009 | CIP-009-2 | 1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | 1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | 1.2. | Define the roles and responsibilities of responders. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 | 2009-09-30 |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | 2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | No Parts for 2. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-009 | CIP-009-2 | 3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | No Parts for 3. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-009 | CIP-009-2 | 4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | No Parts for 4. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-009 | CIP-009-2 | 5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-2 | No Parts for 5. |  |  |  | 2009-05-06 | 2009-05-22 | 2009-09-30 | 2009-09-30 | 2010-04-01 |  |  |  |  | 2010-09-30 | Filing/Order Docket No. RM06-22-000, RD09-7-000
Inactive | CIP | CIP-009 | CIP-009-3 | 1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | The Responsible Entity shall make available its recovery plan(s) as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | 1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | The Responsible Entity shall make available its recovery plan(s) as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | 1.2. | Define the roles and responsibilities of responders. | The Responsible Entity shall make available its recovery plan(s) as specified in Requirement R1. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 | 2010-03-31 |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | 2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | The Responsible Entity shall make available its records documenting required exercises as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | No Parts for 2. |  | The Responsible Entity shall make available its records documenting required exercises as specified in Requirement R2. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-009 | CIP-009-3 | 3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | The Responsible Entity shall make available its documentation of changes to the recovery plan(s), and documentation of all communications, as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | No Parts for 3. |  | The Responsible Entity shall make available its documentation of changes to the recovery plan(s), and documentation of all communications, as specified in Requirement R3. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-009 | CIP-009-3 | 4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | The Responsible Entity shall make available its documentation regarding backup and storage of information as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | No Parts for 4. |  | The Responsible Entity shall make available its documentation regarding backup and storage of information as specified in Requirement R4. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-009 | CIP-009-3 | 5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | The Responsible Entity shall make available its documentation of testing of backup media as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-3 | No Parts for 5. |  | The Responsible Entity shall make available its documentation of testing of backup media as specified in Requirement R5. |  | 2009-12-16 | 2009-12-29 | 2010-03-31 | 2010-03-31 | 2010-10-01 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-7-002
Inactive | CIP | CIP-009 | CIP-009-4 | 1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | 1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | 1.2. | Define the roles and responsibilities of responders. |  |  | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | 2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | No Parts for 2. |  | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-009 | CIP-009-4 | 3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | No Parts for 3. |  | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-009 | CIP-009-4 | 4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | No Parts for 4. |  | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-009 | CIP-009-4 | 5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009 | CIP-009-4 | No Parts for 5. |  | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | Long-Term Planning | 2011-01-24 | 2011-02-10 | 2012-04-19 | 2012-06-25 | [5 empty] | 2014-02-03 | Filing/Order Docket No. RM11-11-000
Inactive | CIP | CIP-009 | CIP-009-5 | 1. | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP-009-5 Table R1 – Recovery Plan Specifications. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 1.1. | Conditions for activation of the recovery plan(s). | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 1.2. | Roles and responsibilities of responders. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 1.3. | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 1.5. | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: • By recovering from an actual incident; • With a paper drill or tabletop exercise; or • With an operational exercise. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 2.2. | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3. | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.2.1. | Update the recovery plan; and | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-5 | 3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 1. | Each Responsible Entity shall have one or more documented recovery plan(s) that collectively include each of the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 1.1. | Conditions for activation of the recovery plan(s). | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 1.2. | Roles and responsibilities of responders. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 1.3. | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 1.5. | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 2. | Each Responsible Entity shall implement its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: • By recovering from an actual incident; • With a paper drill or tabletop exercise; or • With an operational exercise. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 2.2. | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2018-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3. | Each Responsible Entity shall maintain each of its recovery plan(s) in accordance with each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.1.2. DO NOT USE | Update the recovery plan based on any documented lessons learned associated with the plan; and | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.2.1. | Update the recovery plan; and | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.2.1. DO NOT USE | Update the recovery plan; and | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009 | CIP-009-6 | 3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2014-11-13 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 | X |  |  | 2028-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 1. | Each Responsible Entity shall have one or more documented recovery plan(s) that collectively include each of the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 1.1. | Conditions for activation of the recovery plan(s). | Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 1.2. | Roles and responsibilities of responders. | Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 1.3. | One or more processes for the backup and storage of information required to recover Applicable System functionality. | Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. | Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 1.5. | One or more processes to preserve data, per system capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. | Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 2. | Each Responsible Entity shall implement its documented recovery plan(s) to collectively include each of the applicable Requirement Parts in CIP-009-7 Table R2 – Recovery Plan Implementation and Testing. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: • By recovering from an actual incident; • With a paper drill or tabletop exercise; or • With an operational exercise. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 2.2. | Test a representative sample of information used to recover Applicable System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover Applicable System functionality substitutes for this test. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3. | Each Responsible Entity shall maintain each of its recovery plan(s) in accordance with each of the applicable Requirement Parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.2.1. | Update the recovery plan; and | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009 | CIP-009-7 | 3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. | Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 Replaced by CIP-009-7.1 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 1. | Each Responsible Entity shall have one or more documented recovery plan(s) that collectively include each of the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 1.1. | Conditions for activation of the recovery plan(s). | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 1.2. | Roles and responsibilities of responders. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 1.3. | One or more processes for the backup and storage of information required to recover Applicable System functionality. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 1.5. | One or more processes to preserve data, per system capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable Requirement Parts in CIP-009-7.1 Table R1 – Recovery Plan Specifications. | Long-Term Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 2. | Each Responsible Entity shall implement its documented recovery plan(s) to collectively include each of the applicable Requirement Parts in CIP-009-7.1 Table R2 – Recovery Plan Implementation and Testing. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7.1 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: · By recovering from an actual incident; · With a paper drill or tabletop exercise; or · With an operational exercise. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7.1 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 2.2. | Test a representative sample of information used to recover Applicable System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover Applicable System functionality substitutes for this test. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7.1 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable Requirement Parts in CIP-009-7.1 Table R2 – Recovery Plan Implementation and Testing. | Operations Planning, Real-Time Operations | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3. | Each Responsible Entity shall maintain each of its recovery plan(s) in accordance with each of the applicable Requirement Parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata)
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata)
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata)
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata) | BA | DP |  | FRSG |  |  | GOP | [6 empty] | RC |  |  |  |  | RSG | TO | TOP
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.2.1. | Update the recovery plan; and | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata)
Subject to Future Enforcement | CIP | CIP-009 | CIP-009-7.1 | 3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. | M3. Acceptable evidence includes, but is not limited to, each of the Applicable Requirement parts in CIP-009-7.1 Table R3 – Recovery Plan Review, Update and Communication. | Operations Assessment | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-009-7 (Errata)
Inactive | CIP | CIP-010 | CIP-010-1 | 1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-010-1 Table R1 – Configuration Change Management. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.1.3. | Any custom software installed; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.1.4. | Any logical network accessible ports; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.1.5. | Any security patches applied. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.2. | Authorize and document changes that deviate from the existing baseline configuration. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.4. | For a change that deviates from the existing baseline configuration: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.4.3. | Document the results of the verification. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-010-1 Table R2 – Configuration Monitoring. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-010-1 Table R3– Vulnerability Assessments. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3.2. | Where technically feasible, at least once every 36 calendar months: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-1 | 3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.1.3. | Any custom software installed; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.1.4. | Any logical network accessible ports; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.1.5. | Any security patches applied. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.2. | Authorize and document changes that deviate from the existing baseline configuration. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.4. | For a change that deviates from the existing baseline configuration: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.4.3. | Document the results of the verification. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R2 – Configuration Monitoring. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-08-05 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R3– Vulnerability Assessments. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2017-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3.2. | Where technically feasible, at least once every 36 calendar months: | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2018-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2018-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-2 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-07-01 |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | 4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | Evidence shall include each of the documented plan(s) for Transient Cyber Assets and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for Transient Cyber Assets and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use Transient Cyber Asset(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use Transient Cyber Asset(s) or Removable Media. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2017-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-2 | No Parts for 4. |  | Evidence shall include each of the documented plan(s) for Transient Cyber Assets and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for Transient Cyber Assets and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use Transient Cyber Asset(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use Transient Cyber Asset(s) or Removable Media. | Long-Term Planning, Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2017-04-01 |  |  |  |  | 2020-06-30 | Filing/Order Docket No. RM15-14-000
Inactive | CIP | CIP-010 | CIP-010-3 | 1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.1.3. | Any custom software installed; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.1.4. | Any logical network accessible ports; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.1.5. | Any security patches applied. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.2. | Authorize and document changes that deviate from the existing baseline configuration. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.4. | For a change that deviates from the existing baseline configuration: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.4.3. | Document the results of the verification. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.6. | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.6.1. | Verify the identity of the software source; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.6.1. DO NOT USE | Verify the identity of the software source; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.6.2. | Verify the integrity of the software obtained from the software source. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 1.6.2. DO NOT USE | Verify the integrity of the software obtained from the software source. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R2 – Configuration Monitoring. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.2. | Where technically feasible, at least once every 36 calendar months: | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.2. DO NOT USE | Where technically feasible, at least once every 36 calendar months: | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2018-12-26 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | 4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | M4. Evidence shall include each of the documented plan(s) for Transient Cyber Assets and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for Transient Cyber Assets and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use Transient Cyber Asset(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use Transient Cyber Asset(s) or Removable Media. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010 | CIP-010-3 | No Parts for 4. |  | M4. Evidence shall include each of the documented plan(s) for Transient Cyber Assets and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for Transient Cyber Assets and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use Transient Cyber Asset(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use Transient Cyber Asset(s) or Removable Media. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.1.3. | Any custom software installed; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.1.4. | Any logical network accessible ports; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.1.5. | Any security patches applied. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.2. | Authorize and document changes that deviate from the existing baseline configuration. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.4. | For a change that deviates from the existing baseline configuration: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.4.3. | Document the results of the verification. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.6. | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.6.1. | Verify the identity of the software source; and | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 1.6.2. | Verify the integrity of the software obtained from the software source. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-4 Table R2 – Configuration Monitoring | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-4 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3.2. | Where technically feasible, at least once every 36 calendar months: | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | M3. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-3 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | 4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | M4. Evidence shall include each of the documented plan(s) for Transient Cyber Assets and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for Transient Cyber Assets and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use Transient Cyber Asset(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use Transient Cyber Asset(s) or Removable Media. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010 | CIP-010-4 | No Parts for 4. |  | M4. Evidence shall include each of the documented plan(s) for Transient Cyber Assets and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for Transient Cyber Assets and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use Transient Cyber Asset(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use Transient Cyber Asset(s) or Removable Media. | Long-Term Planning, Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | ​Filing/Order Docket No. RD21-2-000
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1. | Each Responsible Entity shall implement one or more documented process(es) to manage configuration changes, individually or by group, that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 –Configuration Change Management. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.1. | Authorize changes that affect Applicable Systems where those changes alter the behavior of one or more cyber security controls, excluding procedural and physical controls, serving one or more requirement parts in CIP-005 or CIP-007, as defined by the Responsible Entity. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.2. | High impact BCS | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.2.1. | Prior to implementing any change from Part 1.1 in the production environment, except during a CIP Exceptional Circumstance, test the changes in a test environment that minimizes differences with the production environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.3. | Prior to the installation of operating systems, firmware, software, or software patches and when the method to do so is available to the Responsible Entity from the software source: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.3.1. | Verify the identity of the software source; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.3.2. | Verify the integrity of the software obtained from the software source. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 1.4. | As a part of the changes authorized per Part 1.1, verify that the behavior(s) of the altered cyber security controls were not adversely affected. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R1 – Configuration Change Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2. | Each Responsible Entity shall implement one or more documented process(es) to monitor configuration changes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1. | Methods to monitor, per system capability, at least once every 35 calendar days, for unauthorized changes that affect Applicable Systems, where those changes alter the behavior of one or more cyber security controls, excluding procedural and physical controls, serving one or more requirement parts in CIP-007, as defined by the Responsible Entity; that include at least one cyber security control for each of the following: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.1. | Configuration on each Applicable System that affects its routable protocol network accessibility; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.2. | Configuration of CPU or memory sharing of VCAs on SCI; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.3. | Installation, removal, and update of operating system, firmware, software, and cyber security patches. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.4. | Configuration of malicious code protection methods; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.5. | Configuration of security event logging or alerting; | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.6. | Configuration of authentication methods; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 2.1.7. | Changes to the enabled or disabled status of accounts. Document and investigate detected unauthorized changes. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R2 – Configuration Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-5 Table R3– Vulnerability Assessments. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3.2. | At least once every 36 calendar months, per system capability: | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3.2.1. | Perform an active vulnerability assessment in a test environment that minimizes differences with the production environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects; and | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3.3. | Prior to becoming a new Applicable System, perform an active vulnerability assessment of the new Applicable System, except for: • Like replacements or additions with a previously assessed configuration of an existing Applicable System; or • CIP Exceptional Circumstances. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-010-5 Table R3 – Vulnerability Assessments and additional evidence to demonstrate implementation as described in the Measures column of the table. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | 4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, associated PCA, and associated SCI, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets (TCA) and Removable Media that include the sections in Attachment 1. | Evidence shall include each of the documented plan(s) for TCAs and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for TCA and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use TCA(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use TCA(s) or Removable Media. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-010 | CIP-010-5 | No Parts for 4. |  | Evidence shall include each of the documented plan(s) for TCAs and Removable Media that collectively include each of the applicable sections in Attachment 1 and additional evidence to demonstrate implementation of plan(s) for TCA and Removable Media. Additional examples of evidence per section are located in Attachment 2. If a Responsible Entity does not use TCA(s) or Removable Media, examples of evidence include, but are not limited to, a statement, policy, or other document that states the Responsible Entity does not use TCA(s) or Removable Media. | Long-Term Planning, Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000
Inactive | CIP | CIP-011 | CIP-011-1 | 1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP-011-1 Table R1 – Information Protection. | Evidence for the information protection program must include the applicable requirement parts in CIP‐011‐1 Table R1– Information Protection and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-1 | 1.1. | Method(s) to identify information that meets the definition of BES Cyber System Information. | Evidence for the information protection program must include the applicable requirement parts in CIP‐011‐1 Table R1– Information Protection and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-1 | 1.2. | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. | Evidence for the information protection program must include the applicable requirement parts in CIP‐011‐1 Table R1– Information Protection and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-1 | 2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-011-1 Table R2 – BES Cyber Asset Reuse and Disposal. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐011‐1 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 | [5 empty] | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-1 | 2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐011‐1 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-1 | 2.2. | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP‐011‐1 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2012-11-26 | 2013-01-31 | 2013-11-22 | 2014-02-03 |  | 2014-02-03 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM13-5-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-2 | 1. | Each Responsible Entity shall implement one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP-011-2 Table R1 – Information Protection. | M1. Evidence for the information protection program must include the applicable requirement parts in CIP-011-2 Table R1 – Information Protection and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-2 | 1.1. | Method(s) to identify information that meets the definition of BES Cyber System Information. | M1. Evidence for the information protection program must include the applicable requirement parts in CIP-011-2 Table R1 – Information Protection and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-2 | 1.2. | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. | M1. Evidence for the information protection program must include the applicable requirement parts in CIP-011-2 Table R1 – Information Protection and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-2 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 |  | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-2 | 2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-2 | 2.2. | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2015-02-12 | 2015-02-13 | 2016-01-21 | 2016-03-31 | 2016-07-01 | 2016-03-31 | X |  |  | 2023-12-31 | Filing/Order Docket No. RM15-14-000 | BA | DP |  |  | GO |  | GOP |  | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011 | CIP-011-3 | 1. | Each Responsible Entity shall implement one or more documented information protection program(s) for BES Cyber System Information (BCSI) pertaining to “Applicable Systems” identified in CIP-011-3 Table R1 – Information Protection Program that collectively includes each of the applicable requirement parts in CIP-011-3 Table R1 – Information Protection Program. | M1. Evidence for the information protection program must include the applicable requirement parts in CIP-011-3 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011 | CIP-011-3 | 1.1. | Method(s) to identify BCSI. | M1. Evidence for the information protection program must include the applicable requirement parts in CIP-011-3 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011 | CIP-011-3 | 1.2. | Method(s) to protect and securely handle BCSI to mitigate risks of compromising confidentiality. | M1. Evidence for the information protection program must include the applicable requirement parts in CIP-011-3 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011 | CIP-011-3 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-3 Table R2 – BES Cyber Asset Reuse and Disposal. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-3 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011 | CIP-011-3 | 2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BCSI (except for reuse within other systems identified in the "Applicable Systems" column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BCSI from the Cyber Asset data storage media. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-3 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011 | CIP-011-3 | 2.2. | Prior to the disposal of applicable Cyber Assets that contain BCSI, the Responsible Entity shall take action to prevent the unauthorized retrieval of BCSI from the Cyber Asset or destroy the data storage media. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-3 Table R2 – BES Cyber Asset Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2021-08-12 | 2021-09-15 | 2021-12-07 | 2021-12-07 | 2024-01-01 | 2024-01-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-4 | 1. | Each Responsible Entity shall implement one or more documented information protection program(s) for BCSI pertaining to Applicable Systems identified in CIP-011-4 Table R1 – Information Protection Program that collectively includes each of the applicable requirement parts in CIP-011-4 Table R1 – Information Protection Program. | Evidence for the information protection program must include the applicable requirement parts in CIP-011-4 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-4 | 1.1. | Method(s) to identify BCSI. | Evidence for the information protection program must include the applicable requirement parts in CIP-011-4 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-4 | 1.2. | Method(s) to protect and securely handle BCSI to mitigate risks of compromising confidentiality. | Evidence for the information protection program must include the applicable requirement parts in CIP-011-4 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-4 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-4 Table R2 –Reuse and Disposal. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-4 Table R2 –Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011 | CIP-011-4 | 2.1. | Methods to prevent the unauthorized retrieval of BCSI from Applicable Systems containing BCSI, prior to their disposal or reuse (except for reuse within other systems identified in the Applicable Systems column). | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-4 Table R2 –Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2024-07-10 | [7 empty] | 2026-03-19 | Filing/Order Docket No. RM24-8-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-011 | CIP-011-4.1 | 1. | Each Responsible Entity shall implement one or more documented information protection program(s) for BCSI pertaining to Applicable Systems identified in CIP-011-4.1 Table R1 – Information Protection Program that collectively includes each of the applicable requirement parts in CIP-011-4.1 Table R1 – Information Protection Program. | Evidence for the information protection program must include the applicable requirement parts in CIP-011-4.1 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-011-4 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-011 | CIP-011-4.1 | 1.1. | Method(s) to identify BCSI. | Evidence for the information protection program must include the applicable requirement parts in CIP-011-4.1 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-011-4 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-011 | CIP-011-4.1 | 1.2. | Method(s) to protect and securely handle BCSI to mitigate risks of compromising confidentiality. | Evidence for the information protection program must include the applicable requirement parts in CIP-011-4.1 Table R1 – Information Protection Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-011-4 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-011 | CIP-011-4.1 | 2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011.1-4 Table R2 –Reuse and Disposal. | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-4.1 Table R2 –Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 Replaces CIP-011-4 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-011 | CIP-011-4.1 | 2.1. | Methods to prevent the unauthorized retrieval of BCSI from Applicable Systems containing BCSI, prior to their disposal or reuse (except for reuse within other systems identified in the Applicable Systems column). | M2. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-011-4.1 Table R2 –Reuse and Disposal and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Planning | 2024-05-09 | 2025-05-20 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 Replaces CIP-011-4 (Errata) | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-012 | CIP-012-1 | 1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | Operations Planning | 2018-08-16 | 2018-09-18 | 2020-01-23 | 2020-04-13 | 2022-07-01 |  |  |  |  | 2026-06-30 | Filing/Order Docket No. RM18-20-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-012 | CIP-012-1 | 1.1. | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | Operations Planning | 2018-08-16 | 2018-09-18 | 2020-01-23 | 2020-04-13 | 2022-07-01 | 2020-04-13 |  |  |  | 2026-06-30 | Filing/Order Docket No. RM18-20-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-012 | CIP-012-1 | 1.2. | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | Operations Planning | 2018-08-16 | 2018-09-18 | 2020-01-23 | 2020-04-13 | 2022-07-01 | 2020-04-13 |  |  |  | 2026-06-30 | Filing/Order Docket No. RM18-20-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-012 | CIP-012-1 | 1.3. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | Operations Planning | 2018-08-16 | 2018-09-18 | 2020-01-23 | 2020-04-13 | 2022-07-01 | 2020-04-13 |  |  |  | 2026-06-30 | Filing/Order Docket No. RM18-20-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012 | CIP-012-2 | 1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure, unauthorized modification, and loss of availability, of data used in Real-time Assessment and Real-time monitoring while such data is being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: | Examples of evidence may include, but are not limited to, documented plan(s) that meet the mitigation objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). Examples of methods identified in the plan(s) may include, but are not limited to, one or more of the following for each Part: Part 1.1 - Methods of mitigation used to protect against the unauthorized disclosure and unauthorized modification of the data (e.g., data masking, encryption/decryption) while such data is being transmitted between Control Centers - Physical access restrictions to unencrypted portions of the network Part 1.2 - Identification of alternative communication paths or methods between Control Centers - Procedures explaining the use of alternative systems or methods for providing for the availability of the data - Service level agreements with carriers containing high availability provisions - Availability or uptime reports for equipment supporting the transmission of Real- time Assessment and Real-time monitoring data Part 1.3 - Contract, memorandum of understanding, meeting minutes, agreement or other information outlining the methods used for recovery - Methods for the recovery of links such as standard operating procedures, applicable sections of CIP-009 recovery plan(s), or similar technical recovery plans - Documentation of the process to restore assets and systems that provide communications - Process or procedure to contact a communications link vendor to initiate and or verify restoration of service Part 1.4 - Descriptions or logical diagrams indicating where the implemented methods reside - Identification of points within the infrastructure where the implemented methods reside - Third party Agreements detailing where the methods are implemented if such methods are implemented by the third party Part 1.5 - Contract, memorandum of understanding, meeting minutes, agreement, or other documentation outlining the responsibilities of each entity | Operations Planning | 2023-12-12 | 2024-01-31 | 2024-05-23 | 2024-05-23 | 2026-07-01 | [5 empty] | Filing/Order Docket No. RD24-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012 | CIP-012-2 | 1.1. | Identification of method(s) used to mitigate the risk(s) posed by unauthorized disclosure and unauthorized modification of data used in Real-time Assessment and Real-time monitoring while such data is being transmitted between Control Centers; | Examples of evidence may include, but are not limited to, documented plan(s) that meet the mitigation objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). Examples of methods identified in the plan(s) may include, but are not limited to, one or more of the following for each Part: Part 1.1 - Methods of mitigation used to protect against the unauthorized disclosure and unauthorized modification of the data (e.g., data masking, encryption/decryption) while such data is being transmitted between Control Centers - Physical access restrictions to unencrypted portions of the network Part 1.2 - Identification of alternative communication paths or methods between Control Centers - Procedures explaining the use of alternative systems or methods for providing for the availability of the data - Service level agreements with carriers containing high availability provisions - Availability or uptime reports for equipment supporting the transmission of Real- time Assessment and Real-time monitoring data Part 1.3 - Contract, memorandum of understanding, meeting minutes, agreement or other information outlining the methods used for recovery - Methods for the recovery of links such as standard operating procedures, applicable sections of CIP-009 recovery plan(s), or similar technical recovery plans - Documentation of the process to restore assets and systems that provide communications - Process or procedure to contact a communications link vendor to initiate and or verify restoration of service Part 1.4 - Descriptions or logical diagrams indicating where the implemented methods reside - Identification of points within the infrastructure where the implemented methods reside - Third party Agreements detailing where the methods are implemented if such methods are implemented by the third party Part 1.5 - Contract, memorandum of understanding, meeting minutes, agreement, or other documentation outlining the responsibilities of each entity | Operations Planning | 2023-12-12 | 2024-01-31 | 2024-05-23 | 2024-05-23 | 2026-07-01 | 2026-07-01 |  |  |  |  | Filing/Order Docket No. RD24-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012 | CIP-012-2 | 1.2. | Identification of method(s) used to mitigate the risk(s) posed by the loss of the ability to communicate Real-time Assessment and Real-time monitoring data between Control Centers; | Examples of evidence may include, but are not limited to, documented plan(s) that meet the mitigation objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). Examples of methods identified in the plan(s) may include, but are not limited to, one or more of the following for each Part: Part 1.1 - Methods of mitigation used to protect against the unauthorized disclosure and unauthorized modification of the data (e.g., data masking, encryption/decryption) while such data is being transmitted between Control Centers - Physical access restrictions to unencrypted portions of the network Part 1.2 - Identification of alternative communication paths or methods between Control Centers - Procedures explaining the use of alternative systems or methods for providing for the availability of the data - Service level agreements with carriers containing high availability provisions - Availability or uptime reports for equipment supporting the transmission of Real- time Assessment and Real-time monitoring data Part 1.3 - Contract, memorandum of understanding, meeting minutes, agreement or other information outlining the methods used for recovery - Methods for the recovery of links such as standard operating procedures, applicable sections of CIP-009 recovery plan(s), or similar technical recovery plans - Documentation of the process to restore assets and systems that provide communications - Process or procedure to contact a communications link vendor to initiate and or verify restoration of service Part 1.4 - Descriptions or logical diagrams indicating where the implemented methods reside - Identification of points within the infrastructure where the implemented methods reside - Third party Agreements detailing where the methods are implemented if such methods are implemented by the third party Part 1.5 - Contract, memorandum of understanding, meeting minutes, agreement, or other documentation outlining the responsibilities of each entity | Operations Planning | 2023-12-12 | 2024-01-31 | 2024-05-23 | 2024-05-23 | 2026-07-01 | 2026-07-01 |  |  |  |  | Filing/Order Docket No. RD24-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012 | CIP-012-2 | 1.3. | Identification of method(s) used to initiate the recovery of communication links used to transmit Real-time Assessment and Real-time monitoring data between Control Centers; | Examples of evidence may include, but are not limited to, documented plan(s) that meet the mitigation objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). Examples of methods identified in the plan(s) may include, but are not limited to, one or more of the following for each Part: Part 1.1 - Methods of mitigation used to protect against the unauthorized disclosure and unauthorized modification of the data (e.g., data masking, encryption/decryption) while such data is being transmitted between Control Centers - Physical access restrictions to unencrypted portions of the network Part 1.2 - Identification of alternative communication paths or methods between Control Centers - Procedures explaining the use of alternative systems or methods for providing for the availability of the data - Service level agreements with carriers containing high availability provisions - Availability or uptime reports for equipment supporting the transmission of Real- time Assessment and Real-time monitoring data Part 1.3 - Contract, memorandum of understanding, meeting minutes, agreement or other information outlining the methods used for recovery - Methods for the recovery of links such as standard operating procedures, applicable sections of CIP-009 recovery plan(s), or similar technical recovery plans - Documentation of the process to restore assets and systems that provide communications - Process or procedure to contact a communications link vendor to initiate and or verify restoration of service Part 1.4 - Descriptions or logical diagrams indicating where the implemented methods reside - Identification of points within the infrastructure where the implemented methods reside - Third party Agreements detailing where the methods are implemented if such methods are implemented by the third party Part 1.5 - Contract, memorandum of understanding, meeting minutes, agreement, or other documentation outlining the responsibilities of each entity | Operations Planning | 2023-12-12 | 2024-01-31 | 2024-05-23 | 2024-05-23 | 2026-07-01 | 2026-07-01 |  |  |  |  | Filing/Order Docket No. RD24-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012 | CIP-012-2 | 1.4. | Identification of where the Responsible Entity implemented method(s) as required in Parts 1.1 and 1.2; and | Examples of evidence may include, but are not limited to, documented plan(s) that meet the mitigation objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). Examples of methods identified in the plan(s) may include, but are not limited to, one or more of the following for each Part: Part 1.1 - Methods of mitigation used to protect against the unauthorized disclosure and unauthorized modification of the data (e.g., data masking, encryption/decryption) while such data is being transmitted between Control Centers - Physical access restrictions to unencrypted portions of the network Part 1.2 - Identification of alternative communication paths or methods between Control Centers - Procedures explaining the use of alternative systems or methods for providing for the availability of the data - Service level agreements with carriers containing high availability provisions - Availability or uptime reports for equipment supporting the transmission of Real- time Assessment and Real-time monitoring data Part 1.3 - Contract, memorandum of understanding, meeting minutes, agreement or other information outlining the methods used for recovery - Methods for the recovery of links such as standard operating procedures, applicable sections of CIP-009 recovery plan(s), or similar technical recovery plans - Documentation of the process to restore assets and systems that provide communications - Process or procedure to contact a communications link vendor to initiate and or verify restoration of service Part 1.4 - Descriptions or logical diagrams indicating where the implemented methods reside - Identification of points within the infrastructure where the implemented methods reside - Third party Agreements detailing where the methods are implemented if such methods are implemented by the third party Part 1.5 - Contract, memorandum of understanding, meeting minutes, agreement, or other documentation outlining the responsibilities of each entity | Operations Planning | 2023-12-12 | 2024-01-31 | 2024-05-23 | 2024-05-23 | 2026-07-01 | 2026-07-01 |  |  |  |  | Filing/Order Docket No. RD24-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012 | CIP-012-2 | 1.5. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for implementing method(s) as required in Parts 1.1, 1.2, and 1.3. | Examples of evidence may include, but are not limited to, documented plan(s) that meet the mitigation objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). Examples of methods identified in the plan(s) may include, but are not limited to, one or more of the following for each Part: Part 1.1 - Methods of mitigation used to protect against the unauthorized disclosure and unauthorized modification of the data (e.g., data masking, encryption/decryption) while such data is being transmitted between Control Centers - Physical access restrictions to unencrypted portions of the network Part 1.2 - Identification of alternative communication paths or methods between Control Centers - Procedures explaining the use of alternative systems or methods for providing for the availability of the data - Service level agreements with carriers containing high availability provisions - Availability or uptime reports for equipment supporting the transmission of Real- time Assessment and Real-time monitoring data Part 1.3 - Contract, memorandum of understanding, meeting minutes, agreement or other information outlining the methods used for recovery - Methods for the recovery of links such as standard operating procedures, applicable sections of CIP-009 recovery plan(s), or similar technical recovery plans - Documentation of the process to restore assets and systems that provide communications - Process or procedure to contact a communications link vendor to initiate and or verify restoration of service Part 1.4 - Descriptions or logical diagrams indicating where the implemented methods reside - Identification of points within the infrastructure where the implemented methods reside - Third party Agreements detailing where the methods are implemented if such methods are implemented by the third party Part 1.5 - Contract, memorandum of understanding, meeting minutes, agreement, or other documentation outlining the responsibilities of each entity | Operations Planning | 2023-12-12 | 2024-01-31 | 2024-05-23 | 2024-05-23 | 2026-07-01 | 2026-07-01 |  |  |  |  | Filing/Order Docket No. RD24-3-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems. The plan(s) shall include: | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2. | One or more process(es) used in procuring BES Cyber Systems that address the following, as applicable: | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.5. DO NOT USE | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 1.2.6. | Coordination of controls for (i) vendor-initiated Interactive Remote Access, and (ii) system-to-system remote access with a vendor(s). | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 | 2020-07-01 |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | 2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. Note: Implementation of the plan does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Requirement R2: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | M2. Evidence shall include documentation to demonstrate implementation of the supply chain cyber security risk management plan(s), which could include, but is not limited to, correspondence, policy documents, or working documents that demonstrate use of the supply chain cyber security risk management plan. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | No Parts for 2. |  | M2. Evidence shall include documentation to demonstrate implementation of the supply chain cyber security risk management plan(s), which could include, but is not limited to, correspondence, policy documents, or working documents that demonstrate use of the supply chain cyber security risk management plan. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000
Inactive | CIP | CIP-013 | CIP-013-1 | 3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | M3. Evidence shall include the dated supply chain cyber security risk management plan(s) approved by the CIP Senior Manager or delegate(s) and additional evidence to demonstrate review of the supply chain cyber security risk management plan(s). Evidence may include, but is not limited to, policy documents, revision history, records of review, or workflow evidence from a document management system that indicate review of supply chain risk management plan(s) at least once every 15 calendar months; and documented approval by the CIP Senior Manager or delegate. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013 | CIP-013-1 | No Parts for 3. |  | M3. Evidence shall include the dated supply chain cyber security risk management plan(s) approved by the CIP Senior Manager or delegate(s) and additional evidence to demonstrate review of the supply chain cyber security risk management plan(s). Evidence may include, but is not limited to, policy documents, revision history, records of review, or workflow evidence from a document management system that indicate review of supply chain risk management plan(s) at least once every 15 calendar months; and documented approval by the CIP Senior Manager or delegate. | Long-Term Planning, Operations Planning | 2017-08-10 | 2017-09-26 | 2018-10-18 | 2018-12-26 | 2020-07-01 |  |  |  |  | 2022-09-30 | Filing/Order Docket No. RM17-13-000
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems and their associated Electronic Access Control or Monitoring Systems (EACMS) and Physical Access Control Systems (PACS). The plan(s) shall include: | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems and their associated EACMS and PACS to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2. | One or more process(es) used in procuring BES Cyber Systems, and their associated EACMS and PACS, that address the following, as applicable: | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System and their associated EACMS and PACS; and | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 1.2.6. | Coordination of controls for vendor-initiated remote access. | M1. Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 | 2022-10-01 |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. Note: Implementation of the plan does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Requirement R2: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | M2. Evidence shall include documentation to demonstrate implementation of the supply chain cyber security risk management plan(s), which could include, but is not limited to, correspondence, policy documents, or working documents that demonstrate use of the supply chain cyber security risk management plan. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | No Parts for 2. |  | M2. Evidence shall include documentation to demonstrate implementation of the supply chain cyber security risk management plan(s), which could include, but is not limited to, correspondence, policy documents, or working documents that demonstrate use of the supply chain cyber security risk management plan. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | 3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | M3. Evidence shall include the dated supply chain cyber security risk management plan(s) approved by the CIP Senior Manager or delegate(s) and additional evidence to demonstrate review of the supply chain cyber security risk management plan(s). Evidence may include, but is not limited to, policy documents, revision history, records of review, or workflow evidence from a document management system that indicate review of supply chain risk management plan(s) at least once every 15 calendar months; and documented approval by the CIP Senior Manager or delegate. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013 | CIP-013-2 | No Parts for 3. |  | M3. Evidence shall include the dated supply chain cyber security risk management plan(s) approved by the CIP Senior Manager or delegate(s) and additional evidence to demonstrate review of the supply chain cyber security risk management plan(s). Evidence may include, but is not limited to, policy documents, revision history, records of review, or workflow evidence from a document management system that indicate review of supply chain risk management plan(s) at least once every 15 calendar months; and documented approval by the CIP Senior Manager or delegate. | Operations Planning | 2020-11-05 | 2020-12-14 | 2021-03-18 | 2021-03-18 | 2022-10-01 |  |  |  |  | 2028-06-30 | Filing/Order Docket No. RD21-2-000
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BCS and their associated Electronic Access Control or Monitoring Systems (EACMS), Physical Access Control Systems (PACS), and Shared Cyber Infrastructure (SCI). The plan(s) shall include: | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.1. | One or more process(es) used in planning for the procurement of applicable systems listed in Requirement R1 to identify and assess cyber security risk(s) to the BES from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2. | One or more process(es) used in procuring applicable systems listed in Requirement R1 that address the following, as applicable: | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor; and | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 1.2.6. | Coordination of controls for vendor-initiated remote access. | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | 2028-07-01 |  |  |  |  | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. | Evidence shall include documentation to demonstrate implementation of the supply chain cyber security risk management plan(s), which could include, but is not limited to, correspondence, policy documents, or working documents that demonstrate use of the supply chain cyber security risk management plan. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | No Parts for 2. |  | Evidence shall include documentation to demonstrate implementation of the supply chain cyber security risk management plan(s), which could include, but is not limited to, correspondence, policy documents, or working documents that demonstrate use of the supply chain cyber security risk management plan. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | 3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | Evidence shall include the dated supply chain cyber security risk management plan(s) approved by the CIP Senior Manager or delegate(s) and additional evidence to demonstrate review of the supply chain cyber security risk management plan(s). Evidence may include, but is not limited to, policy documents, revision history, records of review, or workflow evidence from a document management system that indicate review of supply chain risk management plan(s) at least once every 15 calendar months; and documented approval by the CIP Senior Manager or delegate. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-013 | CIP-013-3 | No Parts for 3. |  | Evidence shall include the dated supply chain cyber security risk management plan(s) approved by the CIP Senior Manager or delegate(s) and additional evidence to demonstrate review of the supply chain cyber security risk management plan(s). Evidence may include, but is not limited to, policy documents, revision history, records of review, or workflow evidence from a document management system that indicate review of supply chain risk management plan(s) at least once every 15 calendar months; and documented approval by the CIP Senior Manager or delegate. | Operations Planning | 2024-05-09 | 2024-07-10 | 2026-03-19 | 2026-05-26 | 2028-07-01 | [5 empty] | Filing/Order Docket No. RM24-8-000
Inactive | CIP | CIP-014 | CIP-014-1 | 1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. [Please see the standard for more information] | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1.[Please see the standard for more information] | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [Please see the standard for more information] | Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-1 | 4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [Please see the standard for more information] | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [Please see the standard for more information] | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 5.2. | Law enforcement contact and coordination information. | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [Please see the standard for more information] | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-1 | 6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2014-05-13 | 2014-05-23 | 2014-11-20 | 2015-10-01 | [5 empty] | 2015-10-01 | Filing/Order Docket No. RM14-15-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | M1. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 |  | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | M1. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | M1. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 |  | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2 | M3. Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 |  | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | M3. Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO
Inactive | CIP | CIP-014 | CIP-014-2 | 4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 |  | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 |  | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 5.2. | Law enforcement contact and coordination information. | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 |  | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Inactive | CIP | CIP-014 | CIP-014-2 | 6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2015-05-07 | 2015-05-15 | 2015-07-14 | 2015-10-02 | 2015-10-02 | 2015-10-02 | X |  |  | 2022-06-15 | Filing/Order Docket No. RD15-4-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | M1. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | [5 empty] | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | M1. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | M1. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | [5 empty] | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | M2. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. | M3. Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | [5 empty] | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | M3. Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | [5 empty] | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | M4. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | Long-Term Planning, Operations Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | [5 empty] | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 5.2. | Law enforcement contact and coordination information. | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | M5. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | [5 empty] | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014 | CIP-014-3 | 6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | M6. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2022-02-10 | 2022-02-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 | 2022-06-16 |  |  |  |  | Filing/Order Docket No. RD22-3-000 | [19 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 1. | Each Transmission Owner shall, at least once every 36 calendar months, identify each applicable Transmission station and Transmission substation meeting any of the criteria in Attachment 1 that is either existing or planned to be in service within 36 calendar months. | M1. Examples of evidence may include, but are not limited to, dated written or electronic documentation of the Transmission station(s) and Transmission substation(s) (existing and those planned to be in service within 36 calendar months) that meet any of the criteria in Attachment 1. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | No Parts for 1. |  | M1. Examples of evidence may include, but are not limited to, dated written or electronic documentation of the Transmission station(s) and Transmission substation(s) (existing and those planned to be in service within 36 calendar months) that meet any of the criteria in Attachment 1. | Long-Term Planning | 2026-06-17 | 2026-07-16
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 2. | Each Transmission Owner with applicable Transmission station(s) or Transmission substation(s) identified in Requirement R1 shall identify proximate existing Bulk Electric System (BES) Transmission station(s) and BES Transmission substation(s), irrespective of ownership, within 1500 feet or 457 meters (the shortest distance, measured substation fence line to substation fence line) of an applicable Transmission station or Transmission substation identified in Requirement R1. | M2. Examples of evidence may include, but are not limited to, dated written or electronic documentation of the BES Transmission stations or BES Transmission substations identified in Requirement R2. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | No Parts for 2. |  | M2. Examples of evidence may include, but are not limited to, dated written or electronic documentation of the BES Transmission stations or BES Transmission substations identified in Requirement R2. | Long-Term Planning | 2026-06-17 | 2026-07-16
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3. | Each Transmission Owner shall have a documented risk assessment methodology for evaluating the loss of each applicable Transmission station or Transmission substation identified in Requirement R1. The methodology shall include, at a minimum, the following: | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.1. | Documented criteria for assessing instability, uncontrolled separation, or Cascading within an Interconnection. The criteria shall include, at a minimum, technically justified thresholds identifying unacceptable generation and load loss within an Interconnection. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.2. | A provision that steady-state and dynamic simulations shall each be performed using at a minimum one System peak Load case and one System Off-Peak Load case. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3. | Specifications for simulations at each applicable Transmission station or Transmission substation identified in accordance with Requirement R1 and, if applicable, at each associated proximate existing BES Transmission station(s) and BES Transmission substation(s) identified in accordance with Requirement R2, that include: | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.1. | At the applicable Transmission station or Transmission substation: | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.1.1. | Prior loss of communication and Protection Systems; | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.1.2. | Application of a Fault or Faults; and | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.1.3. | Delayed (remote) clearing times shall be used unless otherwise technically substantiated. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.2. | At each proximate existing BES station(s) and BES substation(s), as applicable: | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.2.1. | Application of a Fault or Faults, either simultaneous with or following the Fault or Faults applied under Part 3.3.1.2; and | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.2.2. | Normal clearing times shall be used unless otherwise technically substantiated. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.3. | A documented justification for the Fault(s) associated with physical attack to be simulated. A single justification may be used for multiple locations. The justification shall include at a minimum: | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.3.1. | The type of credible high-severity physical attack considered; and | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.3.2. | The type of Fault(s) selected based upon the attack considered. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.4. | Removal of all Elements that Protection Systems and other controls are expected to automatically disconnect. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 3.3.5. | Actual or more conservative clearing times shall be used. | M3. Each Transmission Owner shall provide dated evidence, such as electronic or hard copies, of a risk assessment methodology satisfying Requirement R3. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 4. | Each Transmission Owner with applicable Transmission station(s) and Transmission substation(s) identified in Requirement R1 jointly owned by multiple Transmission Owners shall coordinate with each appropriate Transmission Owner(s) to determine and document their individual and joint responsibilities under Requirement R3 and Requirement R5. | M4. Examples of acceptable evidence may include, but are not limited to, dated documentation, such as meeting minutes, agreements, and email correspondence, that identifies that agreement has been reached on individual and joint responsibilities for performing the required risk assessments. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | No Parts for 4. |  | M4. Examples of acceptable evidence may include, but are not limited to, dated documentation, such as meeting minutes, agreements, and email correspondence, that identifies that agreement has been reached on individual and joint responsibilities for performing the required risk assessments. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 5. | At least once every 36 calendar months, each Transmission Owner shall perform a risk assessment to identify applicable Transmission station(s) and Transmission substation(s) identified in Requirement R1, that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection, using the methodology established in Requirement R3. Jointly owned Transmission station(s) and Transmission substation(s) shall be assessed according to the responsibilities documented under Requirement R4. If proximate BES station(s) and BES Transmission substation(s) were identified in Requirement R2, they shall be included in the risk assessment according to Requirement R3, Part 3.3. | M5. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment satisfying Requirement R5 including the identified Transmission station(s) or Transmission substation(s). For Requirement R5, Part 5.3, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each identified Transmission station or Transmission substation. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 5.1. | If during a risk assessment, a Transmission station or Transmission substation is identified in either the dynamic or steady-state simulation as resulting in instability, uncontrolled separation, or Cascading within an Interconnection when rendered inoperable or damaged, then no further simulation is required. | M5. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment satisfying Requirement R5 including the identified Transmission station(s) or Transmission substation(s). For Requirement R5, Part 5.3, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each identified Transmission station or Transmission substation. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 5.2. | If a previous risk assessment has identified a Transmission station or Transmission substation as causing instability, uncontrolled separation, or Cascading within an Interconnection when rendered inoperable or damaged, then the Transmission Owner may forgo additional assessments on that Transmission station or Transmission substation. Requirement R5, Part 5.3 and Requirement R7 through Requirement R10 still apply to that Transmission station or Transmission substation until a new risk assessment demonstrates otherwise. | M5. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment satisfying Requirement R5 including the identified Transmission station(s) or Transmission substation(s). For Requirement R5, Part 5.3, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each identified Transmission station or Transmission substation. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 5.3. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified as resulting in instability, uncontrolled separation, or Cascading within an Interconnection when rendered inoperable or damaged in the Requirement R5 risk assessment. | M5. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment satisfying Requirement R5 including the identified Transmission station(s) or Transmission substation(s). For Requirement R5, Part 5.3, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each identified Transmission station or Transmission substation. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 6. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R5. The verification may occur concurrently with or after the risk assessment performed under Requirement R5. | M6. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R5 risk assessment and satisfied all of the applicable provisions of Requirement R6, including, if applicable, documenting the technical basis for not modifying the identification in Requirements R1, R2, R3, R4, and R5 as specified under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 6.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: - A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or - An entity that has transmission planning or analysis experience. | M6. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R5 risk assessment and satisfied all of the applicable provisions of Requirement R6, including, if applicable, documenting the technical basis for not modifying the identification in Requirements R1, R2, R3, R4, and R5 as specified under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 6.2. | The unaffiliated third-party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R5, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R5 risk assessment. | M6. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R5 risk assessment and satisfied all of the applicable provisions of Requirement R6, including, if applicable, documenting the technical basis for not modifying the identification in Requirements R1, R2, R3, R4, and R5 as specified under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 6.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station or Transmission substation from, its identification under Requirement R5, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: - Modify its identification under Requirement R5 consistent with the recommendation; or - Document the technical basis for not modifying the identification in accordance with the recommendation. | M6. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R5 risk assessment and satisfied all of the applicable provisions of Requirement R6, including, if applicable, documenting the technical basis for not modifying the identification in Requirements R1, R2, R3, R4, and R5 as specified under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 6.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third-party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | M6. Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R5 risk assessment and satisfied all of the applicable provisions of Requirement R6, including, if applicable, documenting the technical basis for not modifying the identification in Requirements R1, R2, R3, R4, and R5 as specified under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 7. | For a primary control center(s) identified by the Transmission Owner according to Requirement R5, Part 5.3 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R6, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R6, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R6. | M7. Examples of acceptable evidence may include, but are not limited to, written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R7. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 7.1. | If a Transmission station or Transmission substation previously identified under Requirements R1 and R5 and verified according to Requirement R6 is removed from the identification during a subsequent risk assessment performed according to Requirement R5 or a verification according to Requirement R6, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | M7. Examples of acceptable evidence may include, but are not limited to, written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R7. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 8. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R5 and verified according to Requirement R6, and each Transmission Operator notified by a Transmission Owner according to Requirement R7, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R5 and verified according to Requirement R6. The evaluation shall consider the following: | M8. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R8. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 8.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | M8. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R8. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 8.2. | Prior history of attack(s) on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | M8. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R8. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 8.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (E-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | M8. Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R8. | Long-Term Planning, Operations Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 9. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R5 and verified according to Requirement R6, and each Transmission Operator notified by a Transmission Owner according to Requirement R7, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R6 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: | M9. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R6, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 9.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R8. | M9. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R6, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 9.2. | Law enforcement contact and coordination information. | M9. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R6, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 9.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | M9. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R6, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 9.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | M9. Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R6, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 10. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R5 and verified according to Requirement R6, and each Transmission Operator notified by a Transmission Owner according to Requirement R7, shall have an unaffiliated third party review the evaluation performed under Requirement R8 and the security plan(s) developed under Requirement R9. The review may occur concurrently with or after completion of the evaluation performed under Requirement R8 and the security plan development under Requirement R9. | M10. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R8 and the security plan(s) developed under Requirement R9 as specified in Requirement R10 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 10.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 10.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 10.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third-party reviewer from the following: - An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification; - An entity or organization approved by the ERO; - A governmental agency with physical security expertise; or - An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | M10. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R8 and the security plan(s) developed under Requirement R9 as specified in Requirement R10 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 10.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 10.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 10.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third-party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R9. The unaffiliated third-party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R8 or the security plan(s) developed under Requirement R9. | M10. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R8 and the security plan(s) developed under Requirement R9 as specified in Requirement R10 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 10.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 10.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 10.3. | If the unaffiliated third-party reviewer recommends changes to the evaluation performed under Requirement R8 or security plan(s) developed under Requirement R9, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: - Modify its evaluation or security plan(s) consistent with the recommendation; or - Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | M10. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R8 and the security plan(s) developed under Requirement R9 as specified in Requirement R10 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 10.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 10.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-014 | CIP-014-4 | 10.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third-party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | M10. Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R8 and the security plan(s) developed under Requirement R9 as specified in Requirement R10 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 10.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 10.4. | Long-Term Planning | 2026-06-17 | 2026-07-16 | [28 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | 1. | Each Responsible Entity shall implement one or more documented process(es) for internal network security monitoring of networks protected by the Responsible Entity’s Electronic Security Perimeter(s) of high impact BES Cyber Systems and medium impact BES Cyber Systems with External Routable Connectivity to provide methods for detecting and evaluating anomalous network activity. The documented process(es) shall include each of the following requirement Parts | M1. Evidence must include each of the documented process(es) that collectively include each of the requirement Parts in Requirement R1 and evidence to demonstrate implementation of the process(es). Examples of evidence of implementation of the requirement Parts may include, but is not limited to: Part 1.1. - Documentation detailing network data feed(s) that includes a documented risk-based rationale that describes how network data feed(s) were selected for data collection. Part 1.2. - Documentation of anomalous network detection events; - Documentation of configuration settings of internal network security monitoring systems; - Documentation of network communication baseline used to detect anomalous network activity; or - Documentation of other methods used to detect anomalous network activity. Part 1.3. - Documentation of method(s) used to evaluate anomalous activity; - Documentation of actions in response to detected anomalies; or - Documentation of escalation process(es) that could include CIP-008 Cyber Security Incident response plan(s). | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | [5 empty] | Filing/Order Docket No. RM24-7-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | 1.1. | Implement, using a risk-based rationale, network data feed(s) to monitor network activity; including connections, devices, and network communications. | M1. Evidence must include each of the documented process(es) that collectively include each of the requirement Parts in Requirement R1 and evidence to demonstrate implementation of the process(es). Examples of evidence of implementation of the requirement Parts may include, but is not limited to: Part 1.1. - Documentation detailing network data feed(s) that includes a documented risk-based rationale that describes how network data feed(s) were selected for data collection. Part 1.2. - Documentation of anomalous network detection events; - Documentation of configuration settings of internal network security monitoring systems; - Documentation of network communication baseline used to detect anomalous network activity; or - Documentation of other methods used to detect anomalous network activity. Part 1.3. - Documentation of method(s) used to evaluate anomalous activity; - Documentation of actions in response to detected anomalies; or - Documentation of escalation process(es) that could include CIP-008 Cyber Security Incident response plan(s). | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | 2028-10-01 |  |  |  |  | Filing/Order Docket No. RM24-7-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | 1.2. | Implement one or more method(s) to detect anomalous network activity using the network data feed(s) from Part 1.1. | M1. Evidence must include each of the documented process(es) that collectively include each of the requirement Parts in Requirement R1 and evidence to demonstrate implementation of the process(es). Examples of evidence of implementation of the requirement Parts may include, but is not limited to: Part 1.1. - Documentation detailing network data feed(s) that includes a documented risk-based rationale that describes how network data feed(s) were selected for data collection. Part 1.2. - Documentation of anomalous network detection events; - Documentation of configuration settings of internal network security monitoring systems; - Documentation of network communication baseline used to detect anomalous network activity; or - Documentation of other methods used to detect anomalous network activity. Part 1.3. - Documentation of method(s) used to evaluate anomalous activity; - Documentation of actions in response to detected anomalies; or - Documentation of escalation process(es) that could include CIP-008 Cyber Security Incident response plan(s). | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | 2028-10-01 |  |  |  |  | Filing/Order Docket No. RM24-7-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | 1.3. | Implement one or more method(s) to evaluate anomalous network activity detected in Part 1.2. to determine further action(s). | M1. Evidence must include each of the documented process(es) that collectively include each of the requirement Parts in Requirement R1 and evidence to demonstrate implementation of the process(es). Examples of evidence of implementation of the requirement Parts may include, but is not limited to: Part 1.1. - Documentation detailing network data feed(s) that includes a documented risk-based rationale that describes how network data feed(s) were selected for data collection. Part 1.2. - Documentation of anomalous network detection events; - Documentation of configuration settings of internal network security monitoring systems; - Documentation of network communication baseline used to detect anomalous network activity; or - Documentation of other methods used to detect anomalous network activity. Part 1.3. - Documentation of method(s) used to evaluate anomalous activity; - Documentation of actions in response to detected anomalies; or - Documentation of escalation process(es) that could include CIP-008 Cyber Security Incident response plan(s). | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | 2028-10-01 |  |  |  |  | Filing/Order Docket No. RM24-7-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | 2. | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented process(es) to retain internal network security monitoring data associated with network activity determined to be anomalous by the Responsible Entity at a minimum until the action is complete in support of Requirement R1, Part 1.3. | Examples of evidence may include, but are not limited to, documentation of the internal network security monitoring data retention process(es), system configuration(s), or system-generated report(s) showing data retention with timelines sufficient to support Requirement R1, Part 1.3. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | [5 empty] | Filing/Order Docket No. RM24-7-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | No Parts for 2. |  | Examples of evidence may include, but are not limited to, documentation of the internal network security monitoring data retention process(es), system configuration(s), or system-generated report(s) showing data retention with timelines sufficient to support Requirement R1, Part 1.3. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | [5 empty] | Filing/Order Docket No. RM24-7-000
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | 3. | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented process(es) to protect internal network security monitoring data collected in support of Requirement R1 and data retained in support of Requirement R2 to mitigate the risks of unauthorized deletion or modification. | Evidence may include, but is not limited to, documentation demonstrating how internal network security monitoring data is being protected from the risk of unauthorized deletion or modification. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | [5 empty] | Filing/Order Docket No. RM24-7-000 | BA |  |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-015 | CIP-015-1 | No Parts for 3. |  | Evidence may include, but is not limited to, documentation demonstrating how internal network security monitoring data is being protected from the risk of unauthorized deletion or modification. | Operations Assessment, Same-Day Operations | 2024-05-09 | 2024-06-24 | 2025-06-26 | 2025-09-02 | 2028-10-01 | [5 empty] | Filing/Order Docket No. RM24-7-000
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | 1. | Each Responsible Entity shall implement one or more documented process(es) for internal network security monitoring of network activity between Cyber Systems that are part of any Applicable Systems identified in CIP-015-2 Table R1 – Internal Network Security Monitoring. The documented process(es) shall collectively include each of the applicable requirement parts in CIP-015-2 Table R1 – Internal Network Security Monitoring: Note: 1.) Network activity to or from non-CIP devices, 2.) network activity to or from low impact BES Cyber Systems (BCS), and 3.) the network activity between discrete Electronic Security Perimeters; are all out of scope. | M1. Evidence must include each of the applicable documented process(es) that collectively include each of the applicable requirement parts in CIP-015-2 Table R1 – Internal Network Security Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | 1.1. | Implement, using a risk-based rationale, network data feed(s) to monitor network activity; including connections, devices, and network communications. | M1. Evidence must include each of the applicable documented process(es) that collectively include each of the applicable requirement parts in CIP-015-2 Table R1 – Internal Network Security Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | 1.2. | Implement one or more method(s) to detect anomalous network activity using the network data feed(s) from Part 1.1. | M1. Evidence must include each of the applicable documented process(es) that collectively include each of the applicable requirement parts in CIP-015-2 Table R1 – Internal Network Security Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | 1.3. | Implement one or more method(s) to evaluate anomalous network activity detected in Part 1.2 to determine further action(s). | M1. Evidence must include each of the applicable documented process(es) that collectively include each of the applicable requirement parts in CIP-015-2 Table R1 – Internal Network Security Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | 2. | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented process(es) to retain internal network security monitoring data associated with network activity determined to be anomalous by the Responsible Entity at a minimum until the action is complete in support of Requirement R1, Part 1.3. Note: The Responsible Entity is not required to retain internal network security monitoring data that is not relevant to anomalous network activity detected in Requirement R1, Part 1.2. | M2. Examples of evidence may include, but are not limited to, documentation of the internal network security monitoring data retention process(es), system configuration(s), or system-generated report(s) showing data retention with timelines sufficient to support Requirement R1, Part 1.3. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | No Parts for 2. |  | M2. Examples of evidence may include, but are not limited to, documentation of the internal network security monitoring data retention process(es), system configuration(s), or system-generated report(s) showing data retention with timelines sufficient to support Requirement R1, Part 1.3. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | 3. | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented process(es) to protect internal network security monitoring data collected in support of Requirement R1 and data retained in support of Requirement R2 to mitigate the risks of unauthorized deletion or modification. | M3. Evidence may include, but is not limited to, documentation demonstrating how internal network security monitoring data is being protected from the risk of unauthorized deletion or modification. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-015 | CIP-015-2 | No Parts for 3. |  | M3. Evidence may include, but is not limited to, documentation demonstrating how internal network security monitoring data is being protected from the risk of unauthorized deletion or modification. | Operations Assessment, Same-Day Operations | 2026-06-17 | 2026-06-18 | [8 empty] | Filing/Order Docket No. RD26-6-000
Inactive | COM | COM-001 | COM-001-0 | 1. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | 1.1. | Internally. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | 1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | 1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | 1.4. | Where applicable, these facilities shall be redundant and diversely routed. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable
Inactive | COM | COM-001 | COM-001-0 | 3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable
Inactive | COM | COM-001 | COM-001-0 | 4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable
Inactive | COM | COM-001 | COM-001-0 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable
Inactive | COM | COM-001 | COM-001-0 | 6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM001-0, “NERCNet Security Policy.” |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-001-0 was never enforceable
Inactive | COM | COM-001 | COM-001-1 | 1. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | 1.1. | Internally. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | 1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | 1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | 1.4. | Where applicable, these facilities shall be redundant and diversely routed. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-001 | COM-001-1 | 3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-001 | COM-001-1 | 4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-001 | COM-001-1 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-001 | COM-001-1 | 6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM-001-0, “NERCNet Security Policy.” |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-001 | COM-001-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-001 | COM-001-1.1 | 1. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include, but is not limited to communication facility test-procedure documents, records of testing, and maintenance records for communication facilities or equivalent that will be used to confirm that it manages, alarms, tests and/or actively monitors vital telecommunications facilities. (Requirement 2 part 1) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | 1.1. | Internally. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include, but is not limited to communication facility test-procedure documents, records of testing, and maintenance records for communication facilities or equivalent that will be used to confirm that it manages, alarms, tests and/or actively monitors vital telecommunications facilities. (Requirement 2 part 1) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | 1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include, but is not limited to communication facility test-procedure documents, records of testing, and maintenance records for communication facilities or equivalent that will be used to confirm that it manages, alarms, tests and/or actively monitors vital telecommunications facilities. (Requirement 2 part 1) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | 1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include, but is not limited to communication facility test-procedure documents, records of testing, and maintenance records for communication facilities or equivalent that will be used to confirm that it manages, alarms, tests and/or actively monitors vital telecommunications facilities. (Requirement 2 part 1) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | 1.4. | Where applicable, these facilities shall be redundant and diversely routed. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include, but is not limited to communication facility test-procedure documents, records of testing, and maintenance records for communication facilities or equivalent that will be used to confirm that it manages, alarms, tests and/or actively monitors vital telecommunications facilities. (Requirement 2 part 1) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. | The Reliability Coordinator, Transmission Operator or Balancing Authority shall have and provide upon request evidence that could include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent, that will be used to determine compliance to Requirement 4. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | No Parts for 2. |  | The Reliability Coordinator, Transmission Operator or Balancing Authority shall have and provide upon request evidence that could include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent, that will be used to determine compliance to Requirement 4. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | COM | COM-001 | COM-001-1.1 | 3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request its current operating instructions and procedures, either electronic or hard copy that will be used to confirm that it meets Requirement 5. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | No Parts for 3. |  | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request its current operating instructions and procedures, either electronic or hard copy that will be used to confirm that it meets Requirement 5. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | COM | COM-001 | COM-001-1.1 | 4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. | The NERCnet User Organization shall have and provide upon request evidence that could include, but is not limited to documented procedures, operator logs, voice recordings or transcripts of voice recordings, electronic communications, etc that will be used to determine if it adhered to the (User Accountability and Compliance) requirements in Attachment 1-COM001. (Requirement 6) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | No Parts for 4. |  | The NERCnet User Organization shall have and provide upon request evidence that could include, but is not limited to documented procedures, operator logs, voice recordings or transcripts of voice recordings, electronic communications, etc that will be used to determine if it adhered to the (User Accountability and Compliance) requirements in Attachment 1-COM001. (Requirement 6) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RD09-2-000
Inactive | COM | COM-001 | COM-001-1.1 | 5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-1.1 | No Parts for 5. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | COM | COM-001 | COM-001-1.1 | 6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM-001, “NERCNet Security Policy.” |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM 001, “NERCNet Security Policy.” See Standard and Implementation Plan for more information |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | COM | COM-001 | COM-001-1.1 | No Parts for 6. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM 001, “NERCNet Security Policy.” See Standard and Implementation Plan for more information |  | 2015-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | COM | COM-001 | COM-001-2 | 1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2 | 1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2 | 1.2. | Each adjacent Reliability Coordinator within the same Interconnection. | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2 | 2. | R2. Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2 | 2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2 | 2.2. | Each adjacent Reliability Coordinator within the same Interconnection. | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3. | R3. Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3.1. | Its Reliability Coordinator. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3.2. | Each Balancing Authority within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3.3. | Each Distribution Provider within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3.4. | Each Generator Operator within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3.5. | Each adjacent Transmission Operator synchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 3.6. | Each adjacent Transmission Operator asynchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 4.1. | Its Reliability Coordinator. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 4.2. | Each Balancing Authority within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 4.3. | Each adjacent Transmission Operator synchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 4.4. | Each adjacent Transmission Operator asynchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | 5. | R5. Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 5.1. | Its Reliability Coordinator. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 5.3. | Each Distribution Provider within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 5.5. | Each Adjacent Balancing Authority. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 6.1. | Its Reliability Coordinator. | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 6.3. | Each Adjacent Balancing Authority. | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA
Inactive | COM | COM-001 | COM-001-2 | 7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 |  | DP
Inactive | COM | COM-001 | COM-001-2 | 7.1. | Its Balancing Authority. | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 |  | DP
Inactive | COM | COM-001 | COM-001-2 | 7.2. | Its Transmission Operator. | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 |  | DP
Inactive | COM | COM-001 | COM-001-2 | 8. | R8. Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [6 empty] | GOP
Inactive | COM | COM-001 | COM-001-2 | 8.1. | Its Balancing Authority. | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [6 empty] | GOP
Inactive | COM | COM-001 | COM-001-2 | 8.2. | Its Transmission Operator. | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 | 2015-06-22 |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | [6 empty] | GOP
Inactive | COM | COM-001 | COM-001-2 | 9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it tested, at least once each calendar month, its Alternative Interpersonal Communication capability designated in Requirements R2, R4, or R6. If the test was unsuccessful, the entity shall have and provide upon request evidence that it initiated action to repair or designated a replacement Alternative Interpersonal Communication capability within 2 hours. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R9.) | Real-Time Operations, Same-Day Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | No Parts for 9. |  | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it tested, at least once each calendar month, its Alternative Interpersonal Communication capability designated in Requirements R2, R4, or R6. If the test was unsuccessful, the entity shall have and provide upon request evidence that it initiated action to repair or designated a replacement Alternative Interpersonal Communication capability within 2 hours. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R9.) | Real-Time Operations, Same-Day Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000
Inactive | COM | COM-001 | COM-001-2 | 10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it notified entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasted 30 minutes or longer. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R10.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-06-22 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-2 | No Parts for 10. |  | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it notified entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasted 30 minutes or longer. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R10.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-06-22 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000
Inactive | COM | COM-001 | COM-001-2 | 11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | Each Distribution Provider and Generator Operator that detected a failure of its Interpersonal Communication capability shall have and provide upon request evidence that it consulted with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine mutually agreeable action to restore the Interpersonal Communication capability. Evidence could include, but is not limited to: dated operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R11.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000 |  | DP |  |  |  |  | GOP
Inactive | COM | COM-001 | COM-001-2 | No Parts for 11. |  | Each Distribution Provider and Generator Operator that detected a failure of its Interpersonal Communication capability shall have and provide upon request evidence that it consulted with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine mutually agreeable action to restore the Interpersonal Communication capability. Evidence could include, but is not limited to: dated operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R11.) | Real-Time Operations | 2012-11-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2015-10-01 |  |  |  |  | 2015-11-12 | Filing/Order Docket No. RM14-13-000
Inactive | COM | COM-001 | COM-001-2.1 | 1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2.1 | 1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2.1 | 1.2. | Each adjacent Reliability Coordinator within the same Interconnection. | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2.1 | 2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2.1 | 2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2.1 | 2.2. | Each adjacent Reliability Coordinator within the same Interconnection. | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [13 empty] | RC
Inactive | COM | COM-001 | COM-001-2.1 | 3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 3.1. | Its Reliability Coordinator. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 3.2. | Each Balancing Authority within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 3.3. | Each Distribution Provider within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 3.4. | Each Generator Operator within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 3.5. | Each adjacent Transmission Operator synchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 3.6. | Each adjacent Transmission Operator asynchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 4.1. | Its Reliability Coordinator. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 4.2. | Each Balancing Authority within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 4.3. | Each adjacent Transmission Operator synchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 4.4. | Each adjacent Transmission Operator asynchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [20 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | 5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 5.1. | Its Reliability Coordinator. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 5.3. | Each Distribution Provider within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 5.5. | Each Adjacent Balancing Authority. | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 6.1. | Its Reliability Coordinator. | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 6.3. | Each Adjacent Balancing Authority. | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA
Inactive | COM | COM-001 | COM-001-2.1 | 7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) |  | DP
Inactive | COM | COM-001 | COM-001-2.1 | 7.1. | Its Balancing Authority. | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) |  | DP
Inactive | COM | COM-001 | COM-001-2.1 | 7.2. | Its Transmission Operator. | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) |  | DP
Inactive | COM | COM-001 | COM-001-2.1 | 8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | COM | COM-001 | COM-001-2.1 | 8.1. | Its Balancing Authority. | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | COM | COM-001 | COM-001-2.1 | 8.2. | Its Transmission Operator. | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | [6 empty] | GOP
Inactive | COM | COM-001 | COM-001-2.1 | 9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it tested, at least once each calendar month, its Alternative Interpersonal Communication capability designated in Requirements R2, R4, or R6. If the test was unsuccessful, the entity shall have and provide upon request evidence that it initiated action to repair or designated a replacement Alternative Interpersonal Communication capability within 2 hours. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R9.) | Real-Time Operations, Same-Day Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | No Parts for 9. |  | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it tested, at least once each calendar month, its Alternative Interpersonal Communication capability designated in Requirements R2, R4, or R6. If the test was unsuccessful, the entity shall have and provide upon request evidence that it initiated action to repair or designated a replacement Alternative Interpersonal Communication capability within 2 hours. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R9.) | Real-Time Operations, Same-Day Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | COM | COM-001 | COM-001-2.1 | 10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it notified entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasted 30 minutes or longer. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R10.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001 | COM-001-2.1 | No Parts for 10. |  | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it notified entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasted 30 minutes or longer. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R10.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Inactive | COM | COM-001 | COM-001-2.1 | 11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | Each Distribution Provider and Generator Operator that detected a failure of its Interpersonal Communication capability shall have and provide upon request evidence that it consulted with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine mutually agreeable action to restore the Interpersonal Communication capability. Evidence could include, but is not limited to: dated operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R11.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000) |  | DP |  |  |  |  | GOP
Inactive | COM | COM-001 | COM-001-2.1 | No Parts for 11. |  | Each Distribution Provider and Generator Operator that detected a failure of its Interpersonal Communication capability shall have and provide upon request evidence that it consulted with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine mutually agreeable action to restore the Interpersonal Communication capability. Evidence could include, but is not limited to: dated operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R11.) | Real-Time Operations | 2012-11-07 | 2015-08-25 | 2015-11-13 | 2015-11-13 | 2015-11-13 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RD15-6-000 (RM13-11-000, RM14-13-000, RD14-11-000 and RD15-3-000)
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | M1. Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | [13 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | M1. Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [13 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 1.2. | Each adjacent Reliability Coordinator within the same Interconnection. | M1. Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [13 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | M2. Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | [13 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | M2. Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [13 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 2.2. | Each adjacent Reliability Coordinator within the same Interconnection. | M2. Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [13 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3.1. | Its Reliability Coordinator. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3.2. | Each Balancing Authority within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3.3. | Each Distribution Provider within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3.4. | Each Generator Operator within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3.5. | Each adjacent Transmission Operator synchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 3.6. | Each adjacent Transmission Operator asynchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 4.1. | Its Reliability Coordinator. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 4.2. | Each Balancing Authority within its Transmission Operator Area. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 4.3. | Each adjacent Transmission Operator synchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 4.4. | Each adjacent Transmission Operator asynchronously connected. | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | M5. Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 5.1. | Its Reliability Coordinator. | M5. Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | M5. Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 5.3. | Each Distribution Provider within its Balancing Authority Area. | M5. Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. | M5. Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 5.5. | Each Adjacent Balancing Authority. | M5. Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | M6. Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 6.1. | Its Reliability Coordinator. | M6. Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | M6. Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 6.3. | Each Adjacent Balancing Authority. | M6. Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | BA
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | M7. Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 |  | DP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 7.1. | Its Balancing Authority. | M7. Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 |  | DP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 7.2. | Its Transmission Operator. | M7. Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 |  | DP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | M8. Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 8.1. | Its Balancing Authority. | M8. Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 8.2. | Its Transmission Operator. | M8. Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | 2016-10-28 |  |  |  |  | Filing/Order Docket No. RD16-9-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | M9. Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it tested, at least once each calendar month, its Alternative Interpersonal Communication capability designated in Requirements R2, R4, or R6. If the test was unsuccessful, the entity shall have and provide upon request evidence that it initiated action to repair or designated a replacement Alternative Interpersonal Communication capability within 2 hours. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations, Same-Day Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | No Parts for 9. |  | M9. Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that it tested, at least once each calendar month, its Alternative Interpersonal Communication capability designated in Requirements R2, R4, or R6. If the test was unsuccessful, the entity shall have and provide upon request evidence that it initiated action to repair or designated a replacement Alternative Interpersonal Communication capability within 2 hours. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations, Same-Day Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | No Parts for 10. |  | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | M11. Each Distribution Provider and Generator Operator that detected a failure of its Interpersonal Communication capability shall have and provide upon request evidence that it consulted with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine mutually agreeable action to restore the Interpersonal Communication capability. Evidence could include, but is not limited to: dated operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 |  | DP |  |  |  |  | GOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | No Parts for 11. |  | M11. Each Distribution Provider and Generator Operator that detected a failure of its Interpersonal Communication capability shall have and provide upon request evidence that it consulted with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine mutually agreeable action to restore the Interpersonal Communication capability. Evidence could include, but is not limited to: dated operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 12. | Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | M12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have and provide upon request evidence that it has internal Interpersonal Communication capability, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, operating procedures, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 | BA | [5 empty] | GOP | [6 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | No Parts for 12. |  | M12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have and provide upon request evidence that it has internal Interpersonal Communication capability, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, operating procedures, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | 13. | Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | M13. Each Distribution Provider shall have and provide upon request evidence that it has internal Interpersonal Communication capability, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, operating procedures, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000 |  | DP
Mandatory Subject to Enforcement | COM | COM-001 | COM-001-3 | No Parts for 13. |  | M13. Each Distribution Provider shall have and provide upon request evidence that it has internal Interpersonal Communication capability, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, operating procedures, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. | Real-Time Operations | 2016-08-11 | 2016-08-15 | 2016-10-28 | 2016-10-28 | 2017-10-01 | [5 empty] | Filing/Order Docket No. RD16-9-000
Inactive | COM | COM-002 | COM-002-0 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable) | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | COM | COM-002 | COM-002-0 | No Parts for 1. |  |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable)
Inactive | COM | COM-002 | COM-002-0 | 2. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. The following information shall be conveyed to others in the Interconnection via an Interconnection-wide telecommunications system: |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable) | BA | [19 empty] | TOP
Inactive | COM | COM-002 | COM-002-0 | 2.1. | The Balancing Authority is unable to purchase capacity or energy to meet its demand and reserve requirements on a day-ahead or hour-by-hour basis. |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable) | BA
Inactive | COM | COM-002 | COM-002-0 | 2.2. | The Transmission Operator recognizes that potential or actual line loadings, and voltage or reactive levels are such that a single Contingency could threaten the reliability of the Interconnection. (Once a single Contingency occurs, the Transmission Operator must prepare for the next Contingency.) |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable) | [20 empty] | TOP
Inactive | COM | COM-002 | COM-002-0 | 2.3. | The Transmission Operator anticipates initiating a 3% or greater voltage reduction, public appeals for load curtailments, or firm load shedding for other than local problems. |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable) | [20 empty] | TOP
Inactive | COM | COM-002 | COM-002-0 | 3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  | Operations Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002 | COM-002-0 | No Parts for 3. |  |  | Operations Planning | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with COM-002-1 (COM-002-0 was never enforceable)
Inactive | COM | COM-002 | COM-002-1 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. |  | Operations Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-002-1 was never enforceable | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | COM | COM-002 | COM-002-1 | 1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | Operations Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-002-1 was never enforceable | BA | [19 empty] | TOP
Inactive | COM | COM-002 | COM-002-1 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  | Real-Time Operations | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-002-1 was never enforceable | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002 | COM-002-1 | No Parts for 2. |  |  | Real-Time Operations | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 COM-002-1 was never enforceable
Inactive | COM | COM-002 | COM-002-2 | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | Each Transmission Operator, Balancing Authority and Generator Operator shall have communication facilities (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators and shall have and provide as evidence, a list of communication facilities or other equivalent evidence that confirms that the communications have been provided to address a real-time emergency condition. (Requirement 1, part 1) | Real-Time Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | COM | COM-002 | COM-002-2 | 1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. | Each Transmission Operator, Balancing Authority and Generator Operator shall have communication facilities (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators and shall have and provide as evidence, a list of communication facilities or other equivalent evidence that confirms that the communications have been provided to address a real-time emergency condition. (Requirement 1, part 1) | Real-Time Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | COM | COM-002 | COM-002-2 | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. | The Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators of a condition that could threaten the reliability of its area or when firm load shedding was anticipated. (Requirement 1.1) |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002 | COM-002-2 | No Parts for 2. |  | The Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators of a condition that could threaten the reliability of its area or when firm load shedding was anticipated. (Requirement 1.1) |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2016-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | COM | COM-002 | COM-002-2a | 1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | Each Transmission Operator, Balancing Authority and Generator Operator shall have communication facilities (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators and shall have and provide as evidence, a list of communication facilities or other equivalent evidence that confirms that the communications have been provided to address a real-time emergency condition. (Requirement 1, part 1) |  | 2012-02-09 | [8 empty] | 2016-06-30 |  | BA | [5 empty] | GOP | [13 empty] | TOP
Inactive | COM | COM-002 | COM-002-2a | 1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. | Each Transmission Operator, Balancing Authority and Generator Operator shall have communication facilities (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators and shall have and provide as evidence, a list of communication facilities or other equivalent evidence that confirms that the communications have been provided to address a real-time emergency condition. (Requirement 1, part 1) |  | 2012-02-09 | [8 empty] | 2016-06-30 |  | BA | [19 empty] | TOP
Inactive | COM | COM-002 | COM-002-2a | 2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. | The Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators of a condition that could threaten the reliability of its area or when firm load shedding was anticipated. (Requirement 1.1) |  | 2012-02-09 | [8 empty] | 2016-06-30 |  | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002 | COM-002-2a | No Parts for 2. |  | The Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators of a condition that could threaten the reliability of its area or when firm load shedding was anticipated. (Requirement 1.1) |  | 2012-02-09 | [8 empty] | 2016-06-30
Inactive | COM | COM-002 | COM-002-3 | 1. | When a Reliability Coordinator, Transmission Operator, or Balancing Authority requires actions to be executed as a Reliability Directive, the Reliability Coordinator, Transmission Operator, or Balancing Authority shall identify the action as a Reliability Directive to the recipient. | When a Reliability Coordinator, Transmission Operator, or Balancing Authority required actions to be executed as a Reliability Directive, the Reliability Coordinator, Transmission Operator, or Balancing Authority shall have evidence to show that it identified the action as a Reliability Directive to the recipient. Such evidence could include, but is not limited to, dated and time-stamped voice recordings, time-stamped transcripts of voice recordings, or dated operator logs. (R1.) | Real-Time Operations | 2012-11-07 | [8 empty] | 2016-06-30 |  | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002 | COM-002-3 | No Parts for 1. |  | When a Reliability Coordinator, Transmission Operator, or Balancing Authority required actions to be executed as a Reliability Directive, the Reliability Coordinator, Transmission Operator, or Balancing Authority shall have evidence to show that it identified the action as a Reliability Directive to the recipient. Such evidence could include, but is not limited to, dated and time-stamped voice recordings, time-stamped transcripts of voice recordings, or dated operator logs. (R1.) | Real-Time Operations | 2012-11-07 | [8 empty] | 2016-06-30
Inactive | COM | COM-002 | COM-002-3 | 2. | Each Balancing Authority, Transmission Operator, Generator Operator, and Distribution Provider that is the recipient of a Reliability Directive shall repeat, restate, rephrase, or recapitulate the Reliability Directive. | Each Balancing Authority, Transmission Operator, Generator Operator, and Distribution Provider that was the recipient of a Reliability Directive shall have evidence to show that the recipient repeated, restated, rephrased, or recapitulated the Reliability Directive to the issuer of the Reliability Directive. Such evidence could include, but is not limited to, dated and time-stamped voice recordings or transcripts of voice recordings, or dated operator logs. (R2.) | Real-Time Operations | 2012-11-07 | [8 empty] | 2016-06-30 |  | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | COM | COM-002 | COM-002-3 | No Parts for 2. |  | Each Balancing Authority, Transmission Operator, Generator Operator, and Distribution Provider that was the recipient of a Reliability Directive shall have evidence to show that the recipient repeated, restated, rephrased, or recapitulated the Reliability Directive to the issuer of the Reliability Directive. Such evidence could include, but is not limited to, dated and time-stamped voice recordings or transcripts of voice recordings, or dated operator logs. (R2.) | Real-Time Operations | 2012-11-07 | [8 empty] | 2016-06-30
Inactive | COM | COM-002 | COM-002-3 | 3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issues a Reliability Directive shall either: • Confirm that the response from the recipient of the Reliability Directive (in accordance with Requirement R2) was accurate, or • Reissue the Reliability Directive to resolve a misunderstanding. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issued a Reliability Directive shall have evidence that the issuer either confirmed that the response from the recipient of the Reliability Directive was accurate or reissued the Reliability Directive to resolve a misunderstanding. Such evidence could include, but is not limited to, such as dated and time-stamped voice recordings, or dated and timestamped transcripts of voice recordings, or dated operator logs to show. (R3.) | Real-Time Operations | 2012-11-07 | [8 empty] | 2016-06-30 |  | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002 | COM-002-3 | No Parts for 3. |  | Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issued a Reliability Directive shall have evidence that the issuer either confirmed that the response from the recipient of the Reliability Directive was accurate or reissued the Reliability Directive to resolve a misunderstanding. Such evidence could include, but is not limited to, such as dated and time-stamped voice recordings, or dated and timestamped transcripts of voice recordings, or dated operator logs to show. (R3.) | Real-Time Operations | 2012-11-07 | [8 empty] | 2016-06-30
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum:[Please see the standard for more information] | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1.1. | Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1.2. | Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1.3. | Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1.4. | Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1.5. | Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 1.6. | Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | M1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 2. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | M2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its initial training records related to its documented communications protocols developed for Requirement R1 such as attendance logs, agendas, learning objectives, or course materials in fulfillment of Requirement R2. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | No Parts for 2. |  | M2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its initial training records related to its documented communications protocols developed for Requirement R1 such as attendance logs, agendas, learning objectives, or course materials in fulfillment of Requirement R2. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 3. | Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: -Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or -Request that the issuer reissue the Operating Instruction. | M3. Each Distribution Provider and Generator Operator shall provide its initial training records for its operating personnel such as attendance logs, agendas, learning objectives, or course materials in fulfillment of Requirement R3. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 |  | DP |  |  |  |  | GOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | No Parts for 3. |  | M3. Each Distribution Provider and Generator Operator shall provide its initial training records for its operating personnel such as attendance logs, agendas, learning objectives, or course materials in fulfillment of Requirement R3. | Long-Term Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 4. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months:[Please see the standard for more information] | M4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide evidence of its assessments, including spreadsheets, logs or other evidence of feedback, findings of effectiveness and any changes made to its documented communications protocols developed for Requirement R1 in fulfillment of Requirement R4. The entity shall provide, as part of its assessment, evidence of any corrective actions taken where an operating personnel’s non-adherence to the protocols developed in Requirement R1 is the sole or partial cause of an Emergency and for all other instances where the entity determined that it was appropriate to take a corrective action to address deviations from the documented protocols developed in Requirement R1. | Operations Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 4.1. | Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. | M4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide evidence of its assessments, including spreadsheets, logs or other evidence of feedback, findings of effectiveness and any changes made to its documented communications protocols developed for Requirement R1 in fulfillment of Requirement R4. The entity shall provide, as part of its assessment, evidence of any corrective actions taken where an operating personnel’s non-adherence to the protocols developed in Requirement R1 is the sole or partial cause of an Emergency and for all other instances where the entity determined that it was appropriate to take a corrective action to address deviations from the documented protocols developed in Requirement R1. | Operations Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 4.2. | Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | M4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide evidence of its assessments, including spreadsheets, logs or other evidence of feedback, findings of effectiveness and any changes made to its documented communications protocols developed for Requirement R1 in fulfillment of Requirement R4. The entity shall provide, as part of its assessment, evidence of any corrective actions taken where an operating personnel’s non-adherence to the protocols developed in Requirement R1 is the sole or partial cause of an Emergency and for all other instances where the entity determined that it was appropriate to take a corrective action to address deviations from the documented protocols developed in Requirement R1. | Operations Planning | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | 2015-06-22 |  |  |  |  | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 5. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: -Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). - Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or -Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | M5. Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issued an oral two-party, person-to-person Operating Instruction during an Emergency, excluding oral single-party to multiple-party burst Operating Instructions, shall have evidence that the issuer either: 1) confirmed that the response from the recipient of the Operating Instruction was correct; 2) reissued the Operating Instruction if the repeated information was incorrect or if requested by the receiver; or 3) took an alternative action if a response was not received or if the Operating Instruction was not understood by the receiver. Such evidence could include, but is not limited to, dated and time-stamped voice recordings, or dated and time-stamped transcripts of voice recordings, or dated operator logs in fulfillment of Requirement R5. | Real-Time Operations | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | No Parts for 5. |  | M5. Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issued an oral two-party, person-to-person Operating Instruction during an Emergency, excluding oral single-party to multiple-party burst Operating Instructions, shall have evidence that the issuer either: 1) confirmed that the response from the recipient of the Operating Instruction was correct; 2) reissued the Operating Instruction if the repeated information was incorrect or if requested by the receiver; or 3) took an alternative action if a response was not received or if the Operating Instruction was not understood by the receiver. Such evidence could include, but is not limited to, dated and time-stamped voice recordings, or dated and time-stamped transcripts of voice recordings, or dated operator logs in fulfillment of Requirement R5. | Real-Time Operations | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 6. | Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: -Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or -Request that the issuer reissue the Operating Instruction. | M6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that was the recipient of an oral two-party, person-to-person Operating Instruction during an Emergency, excluding oral single-party to multiple-party burst Operating Instructions, shall have evidence to show that the recipient either repeated, not necessarily verbatim, the Operating Instruction and received confirmation from the issuer that the response was correct, or requested that the issuer reissue the Operating Instruction in fulfillment of Requirement R6. Such evidence may include, but is not limited to, dated and time-stamped voice recordings (if the entity has such recordings), dated operator logs, an attestation from the issuer of the Operating Instruction, memos or transcripts. | Real-Time Operations | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | No Parts for 6. |  | M6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that was the recipient of an oral two-party, person-to-person Operating Instruction during an Emergency, excluding oral single-party to multiple-party burst Operating Instructions, shall have evidence to show that the recipient either repeated, not necessarily verbatim, the Operating Instruction and received confirmation from the issuer that the response was correct, or requested that the issuer reissue the Operating Instruction in fulfillment of Requirement R6. Such evidence may include, but is not limited to, dated and time-stamped voice recordings (if the entity has such recordings), dated operator logs, an attestation from the issuer of the Operating Instruction, memos or transcripts. | Real-Time Operations | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | 7. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | M7. Each Balancing Authority, Reliability Coordinator and Transmission Operator that issued a written or oral single or multiple-party burst Operating Instruction during an Emergency shall provide evidence that the Operating Instruction was received by at least one receiver. Such evidence may include, but is not limited to, dated and time-stamped voice recordings (if the entity has such recordings), dated operator logs, electronic records, memos or transcripts. | Real-Time Operations | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002 | COM-002-4 | No Parts for 7. |  | M7. Each Balancing Authority, Reliability Coordinator and Transmission Operator that issued a written or oral single or multiple-party burst Operating Instruction during an Emergency shall provide evidence that the Operating Instruction was received by at least one receiver. Such evidence may include, but is not limited to, dated and time-stamped voice recordings (if the entity has such recordings), dated operator logs, electronic records, memos or transcripts. | Real-Time Operations | 2014-05-07 | 2014-05-14 | 2015-04-16 | 2015-06-22 | 2016-07-01 | [5 empty] | Filing/Order Docket No. RM14-13-000
Inactive | EOP | EOP-001 | EOP-001-0 | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA
Inactive | EOP | EOP-001 | EOP-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000
Inactive | EOP | EOP-001 | EOP-001-0 | 2. | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | EOP | EOP-001 | EOP-001-0 | 3. | Each Transmission Operator and Balancing Authority shall: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 3.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 3.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 3.3. | Develop, maintain, and implement a set of plans for load shedding. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 3.4. | Develop, maintain, and implement a set of plans for system restoration. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 4. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 4.1. | Communications protocols to be used during emergencies. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 4.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 4.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 4.4. | Staffing levels for the emergency. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 5. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000
Inactive | EOP | EOP-001 | EOP-001-0 | 6. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000
Inactive | EOP | EOP-001 | EOP-001-0 | 7. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 7.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 7.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 7.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0 | 7.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA
Inactive | EOP | EOP-001 | EOP-001-0.1b | No Parts for 1. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-0.1b | 2. | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD11-12-000 | [20 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | No Parts for 2. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-0.1b | 3. | Each Transmission Operator and Balancing Authority shall: |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 3.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 3.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 3.3. | Develop, maintain, and implement a set of plans for load shedding. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 3.4. | Develop, maintain, and implement a set of plans for system restoration. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 4. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 4.1. | Communications protocols to be used during emergencies. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 4.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 4.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 4.4. | Staffing levels for the emergency. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 5. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | No Parts for 5. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-0.1b | 6. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | No Parts for 6. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-0.1b | 7. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 7.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 7.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 7.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0.1b | 7.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2013-06-30 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA
Inactive | EOP | EOP-001 | EOP-001-0b | No Parts for 1. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata)
Inactive | EOP | EOP-001 | EOP-001-0b | 2. | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2011-09-30 | Replaced by EOP-001-0.1b (Errata) | [20 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | No Parts for 2. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2011-09-30 | Replaced by EOP-001-0.1b (Errata)
Inactive | EOP | EOP-001 | EOP-001-0b | 3. | Each Transmission Operator and Balancing Authority shall: |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 3.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 3.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 3.3. | Develop, maintain, and implement a set of plans for load shedding. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 3.4. | Develop, maintain, and implement a set of plans for system restoration. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 4. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 4.1. | Communications protocols to be used during emergencies. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 4.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 4.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 4.4. | Staffing levels for the emergency. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 5. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | No Parts for 5. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata)
Inactive | EOP | EOP-001 | EOP-001-0b | 6. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | No Parts for 6. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata)
Inactive | EOP | EOP-001 | EOP-001-0b | 7. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 7.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 7.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 7.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-0b | 7.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | 2011-12-15 | 2011-12-15 |  |  |  | 2012-09-12 | Replaced by EOP-001-0.1b (Errata) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA
Inactive | EOP | EOP-001 | EOP-001-1 | No Parts for 1. |  |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable)
Inactive | EOP | EOP-001 | EOP-001-1 | 2. | Each Transmission Operator and Balancing Authority shall: |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 2.3. | Develop, maintain, and implement a set of plans for load shedding. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 2.4. | Develop, maintain, and implement a set of plans for system restoration. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 3.1. | Communications protocols to be used during emergencies. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 3.4. | Staffing levels for the emergency. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | No Parts for 4. |  |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable)
Inactive | EOP | EOP-001 | EOP-001-1 | 5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | No Parts for 5. |  |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable)
Inactive | EOP | EOP-001 | EOP-001-1 | 6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-1 | 6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2008-10-17 | 2009-12-31 | [7 empty] | 2011-05-23 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2 (EOP-001-1 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA
Inactive | EOP | EOP-001 | EOP-001-2 | No Parts for 1. |  |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable)
Inactive | EOP | EOP-001 | EOP-001-2 | 2. | Each Transmission Operator and Balancing Authority shall: |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 2.3. | Develop, maintain, and implement a set of plans for load shedding. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 3.1. | Communications protocols to be used during emergencies. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 3.4. | Staffing levels for the emergency. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | No Parts for 4. |  |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable)
Inactive | EOP | EOP-001 | EOP-001-2 | 5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | No Parts for 5. |  |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable)
Inactive | EOP | EOP-001 | EOP-001-2 | 6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2 | 6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-12-14 | Filing/Order Docket No. RM10-15-000, RM10-16-000 Replaced with EOP-001-2b (Interpretation of R1 and R2.2)--(EOP-001-2 was not enforceable) | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | The Transmission Operator and Balancing Authority shall have its emergency plans available for review by the Regional Reliability Organization at all times. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-001 | EOP-001-2.1b | No Parts for 1. |  | The Transmission Operator and Balancing Authority shall have its emergency plans available for review by the Regional Reliability Organization at all times. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-001 | EOP-001-2.1b | 2. | Each Transmission Operator and Balancing Authority shall: | The Transmission Operator and Balancing Authority shall have its two most recent annual selfassessments available for review by the Regional Reliability Organization at all times. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. | The Transmission Operator and Balancing Authority shall have its two most recent annual selfassessments available for review by the Regional Reliability Organization at all times. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. | The Transmission Operator and Balancing Authority shall have its two most recent annual selfassessments available for review by the Regional Reliability Organization at all times. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 2.3. | Develop, maintain, and implement a set of plans for load shedding. | The Transmission Operator and Balancing Authority shall have its two most recent annual selfassessments available for review by the Regional Reliability Organization at all times. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 3.1. | Communications protocols to be used during emergencies. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 3.4. | Staffing levels for the emergency. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | No Parts for 4. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-001 | EOP-001-2.1b | 5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | No Parts for 5. |  |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-001 | EOP-001-2.1b | 6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2013-07-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2013-07-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2.1b | 6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2013-07-01 | 2013-07-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA
Inactive | EOP | EOP-001 | EOP-001-2b | No Parts for 1. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-2b | 2. | Each Transmission Operator and Balancing Authority shall: |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 2.3. | Develop, maintain, and implement a set of plans for load shedding. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 3.1. | Communications protocols to be used during emergencies. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 3.4. | Staffing levels for the emergency. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | No Parts for 4. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-2b | 5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | No Parts for 5. |  |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000
Inactive | EOP | EOP-001 | EOP-001-2b | 6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 | [5 empty] | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-001 | EOP-001-2b | 6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  |  | 2010-11-04 | 2011-09-09 | 2011-12-15 | 2011-12-15 |  | 2011-12-15 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD11-12-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-002 | EOP-002-0 | 1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 1. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 2. | Each Balancing Authority and Reliability Coordinator shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 4. | A Reliability Coordinator that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to neighboring areas. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 4. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 5. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 5. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 6. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 6. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 7. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 7.1. | Loading all available generating capacity. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 7.2. | Deploying all available operating reserve. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 7.3. | Interrupting interruptible load and exports. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 7.4. | Requesting emergency assistance from other Balancing Authorities. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 7.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 7.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 8. | Once the Balancing Authority has exhausted the steps listed in Requirement 7, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 8.1. | Manually shed firm load without delay to return its ACE to zero; and |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA
Inactive | EOP | EOP-002 | EOP-002-0 | 8.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | 9. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | No Parts for 9. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 10. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable)
Inactive | EOP | EOP-002 | EOP-002-0 | 10.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | 10.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | 10.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-0 | 10.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with EOP-002-1 (EOP-002-0 was never enforceable) | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | 1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | No Parts for 1. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable
Inactive | EOP | EOP-002 | EOP-002-1 | 2. | Each Balancing Authority shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable
Inactive | EOP | EOP-002 | EOP-002-1 | 3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | No Parts for 3. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable
Inactive | EOP | EOP-002 | EOP-002-1 | 4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | No Parts for 4. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable
Inactive | EOP | EOP-002 | EOP-002-1 | 5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | No Parts for 5. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable
Inactive | EOP | EOP-002 | EOP-002-1 | 6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 6.1. | Loading all available generating capacity. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 6.2. | Deploying all available operating reserve. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 6.3. | Interrupting interruptible load and exports. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 6.4. | Requesting emergency assistance from other Balancing Authorities. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 7.1. | Manually shed firm load without delay to return its ACE to zero; and |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA
Inactive | EOP | EOP-002 | EOP-002-1 | 7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | 8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | No Parts for 8. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable
Inactive | EOP | EOP-002 | EOP-002-1 | 9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | [9 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002 | EOP-002-1 | 9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | 9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | 9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-1 | 9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-002-1 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2 | 1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-002 | EOP-002-2 | 2. | Each Balancing Authority shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-002 | EOP-002-2 | 3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-002 | EOP-002-2 | 4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-002 | EOP-002-2 | 5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-002 | EOP-002-2 | 6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 6.1. | Loading all available generating capacity. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 6.2. | Deploying all available operating reserve. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 6.3. | Interrupting interruptible load and exports. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 6.4. | Requesting emergency assistance from other Balancing Authorities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 7.1. | Manually shed firm load without delay to return its ACE to zero; and |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2 | 8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2 | No Parts for 8. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-002 | EOP-002-2 | 9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [9 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002 | EOP-002-2 | 9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [9 empty] | LSE
Inactive | EOP | EOP-002 | EOP-002-2 | 9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2 | 9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2 | 9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2.1 | 1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2.1 | No Parts for 1. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | EOP | EOP-002 | EOP-002-2.1 | 2. | Each Balancing Authority shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | No Parts for 2. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | EOP | EOP-002 | EOP-002-2.1 | 3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | No Parts for 3. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | EOP | EOP-002 | EOP-002-2.1 | 4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | No Parts for 4. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | EOP | EOP-002 | EOP-002-2.1 | 5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | No Parts for 5. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6.1. | Loading all available generating capacity. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6.2. | Deploying all available operating reserve. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6.3. | Interrupting interruptible load and exports. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6.4. | Requesting emergency assistance from other Balancing Authorities. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 7.1. | Manually shed firm load without delay to return its ACE to zero; and |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | BA
Inactive | EOP | EOP-002 | EOP-002-2.1 | 8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2.1 | No Parts for 8. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000
Inactive | EOP | EOP-002 | EOP-002-2.1 | 9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002 | EOP-002-2.1 | 9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | [9 empty] | LSE
Inactive | EOP | EOP-002 | EOP-002-2.1 | 9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2.1 | 9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-2.1 | 9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  | 2011-09-30 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3 | 1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3 | No Parts for 1. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000
Inactive | EOP | EOP-002 | EOP-002-3 | 2. | Each Balancing Authority shall, when required and as appropriate, take one or more actions as described in its capacity and energy emergency plan, , to reduce risks to the interconnected system. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | No Parts for 2. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000
Inactive | EOP | EOP-002 | EOP-002-3 | 3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | No Parts for 3. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000
Inactive | EOP | EOP-002 | EOP-002-3 | 4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | No Parts for 4. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000
Inactive | EOP | EOP-002 | EOP-002-3 | 5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | No Parts for 5. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000
Inactive | EOP | EOP-002 | EOP-002-3 | 6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 6.1. | Loading all available generating capacity. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 6.2. | Deploying all available operating reserve. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 6.3. | Interrupting interruptible load and exports. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 6.4. | Requesting emergency assistance from other Balancing Authorities. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 7.1. | Manually shed firm load without delay to return its ACE to zero; and |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3 | 8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3 | No Parts for 8. |  |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000
Inactive | EOP | EOP-002 | EOP-002-3 | 9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | [9 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002 | EOP-002-3 | 9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | [9 empty] | LSE
Inactive | EOP | EOP-002 | EOP-002-3 | 9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3 | 9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3 | 9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-01-10 | 2011-01-10 |  |  |  | 2012-09-12 | Filing/Order Docket No. RD10-15-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3.1 | 1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | Each Reliability Coordinator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, job descriptions, signed agreements, authority letter signed by an appropriate officer of the company, or other equivalent evidence that will be used to confirm that it meets Requirement 1. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [12 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3.1 | No Parts for 1. |  | Each Reliability Coordinator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, job descriptions, signed agreements, authority letter signed by an appropriate officer of the company, or other equivalent evidence that will be used to confirm that it meets Requirement 1. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-002 | EOP-002-3.1 | 2. | Each Balancing Authority shall, when required and as appropriate, take one or more actions as described in its capacity and energy emergency plan to reduce risks to the interconnected system. | If a Reliability Coordinator or Balancing Authority implements one or more actions described in its Capacity and Energy Emergency plan, that entity shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, computer printouts or other equivalent evidence that will be used to determine if the actions it took to relieve emergency conditions were in conformance with its Capacity and Energy Emergency Plan. (Requirement 2) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | No Parts for 2. |  | If a Reliability Coordinator or Balancing Authority implements one or more actions described in its Capacity and Energy Emergency plan, that entity shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, computer printouts or other equivalent evidence that will be used to determine if the actions it took to relieve emergency conditions were in conformance with its Capacity and Energy Emergency Plan. (Requirement 2) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-002 | EOP-002-3.1 | 3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | If a Balancing Authority experiences an operating Capacity or Energy Emergency it shall have and provide upon request evidence that could include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it met Requirement 3. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | No Parts for 3. |  | If a Balancing Authority experiences an operating Capacity or Energy Emergency it shall have and provide upon request evidence that could include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it met Requirement 3. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-002 | EOP-002-3.1 | 4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, work orders, E-Tags, or other evidence) that it took the actions described in R4 in response to anticipating a capacity or energy emergency. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | No Parts for 4. |  | The Balancing Authority shall have and provide upon request evidence (such as operator logs, work orders, E-Tags, or other evidence) that it took the actions described in R4 in response to anticipating a capacity or energy emergency. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-002 | EOP-002-3.1 | 5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it only used the assistance provided by the Interconnection frequency bias for the time needed to implement corrective actions and did not attempt to return Interconnection frequency to normal through unilateral adjustment of generation beyond that supplied through the frequency bias action and Interchange Schedule changes. (Requirement 5) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | No Parts for 5. |  | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it only used the assistance provided by the Interconnection frequency bias for the time needed to implement corrective actions and did not attempt to return Interconnection frequency to normal through unilateral adjustment of generation beyond that supplied through the frequency bias action and Interchange Schedule changes. (Requirement 5) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6.1. | Loading all available generating capacity. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6.2. | Deploying all available operating reserve. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6.3. | Interrupting interruptible load and exports. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6.4. | Requesting emergency assistance from other Balancing Authorities. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. | The Balancing Authority shall have and provide upon request evidence (such as operator logs, dispatch instructions, or other evidence) that it took actions such as those listed in R6 to comply with CPS and DCS. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | The Balancing Authority shall have and provide upon request evidence (such as operator logs, voice recordings, or other evidence) that it took the actions listed in R7 when unable to resolve an emergency condition. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 7.1. | Manually shed firm load without delay to return its ACE to zero; and | The Balancing Authority shall have and provide upon request evidence (such as operator logs, voice recordings, or other evidence) that it took the actions listed in R7 when unable to resolve an emergency condition. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” | The Balancing Authority shall have and provide upon request evidence (such as operator logs, voice recordings, or other evidence) that it took the actions listed in R7 when unable to resolve an emergency condition. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA
Inactive | EOP | EOP-002 | EOP-002-3.1 | 8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002 “Energy Emergency Alerts.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | If a Reliability Coordinator has any Balancing Authority within its Reliability Coordinator Area that has notified the Reliability Coordinator of a potential or actual Energy Emergency, the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence to determine if it initiated an Energy Emergency Alert as specified in Requirement 8 and as detailed in Attachment 1- EOP-002 “Energy Emergency Alerts.” |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3.1 | No Parts for 8. |  | If a Reliability Coordinator has any Balancing Authority within its Reliability Coordinator Area that has notified the Reliability Coordinator of a potential or actual Energy Emergency, the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence to determine if it initiated an Energy Emergency Alert as specified in Requirement 8 and as detailed in Attachment 1- EOP-002 “Energy Emergency Alerts.” |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | EOP | EOP-002 | EOP-002-3.1 | 9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff: | If a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Nondesignated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources), the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to, NERC reports, EEA reports, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if that Reliability Coordinator met Requirements 9.2, 9.3 and 9.4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [9 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002 | EOP-002-3.1 | 9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” | If a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Nondesignated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources), the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to, NERC reports, EEA reports, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if that Reliability Coordinator met Requirements 9.2, 9.3 and 9.4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [9 empty] | LSE
Inactive | EOP | EOP-002 | EOP-002-3.1 | 9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. | If a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Nondesignated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources), the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to, NERC reports, EEA reports, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if that Reliability Coordinator met Requirements 9.2, 9.3 and 9.4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3.1 | 9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. | If a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Nondesignated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources), the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to, NERC reports, EEA reports, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if that Reliability Coordinator met Requirements 9.2, 9.3 and 9.4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | EOP | EOP-002 | EOP-002-3.1 | 9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. | If a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Nondesignated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources), the Reliability Coordinator involved in the event shall have and provide upon request evidence that could include, but is not limited to, NERC reports, EEA reports, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if that Reliability Coordinator met Requirements 9.2, 9.3 and 9.4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | EOP | EOP-003 | EOP-003-0 | 1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 2. | Each Transmission Operator and Balancing Authority shall establish plans for automatic load shedding for underfrequency or undervoltage conditions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans among other interconnected Transmission Operators and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 4. | A Transmission Operator or Balancing Authority shall consider one or more of these factors in designing an automatic load shedding scheme: frequency, rate of frequency decay, voltage level, rate of voltage decay, or power flow levels. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 5. | A Transmission Operator or Balancing Authority shall implement load shedding in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 7. | The Transmission Operator and Balancing Authority shall coordinate automatic load shedding throughout their areas with underfrequency isolation of generating units, tripping of shunt capacitors, and other automatic actions that will occur under abnormal frequency, voltage, or power flow conditions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-0 | 8. | Each Transmission Operator or Balancing Authority shall have plans for operator-controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-003-0 was never enforceable
Inactive | EOP | EOP-003 | EOP-003-1 | 1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 2. | Each Transmission Operator and Balancing Authority shall establish plans for automatic load shedding for underfrequency or undervoltage conditions. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans among other interconnected Transmission Operators and Balancing Authorities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 4. | A Transmission Operator or Balancing Authority shall consider one or more of these factors in designing an automatic load shedding scheme: frequency, rate of frequency decay, voltage level, rate of voltage decay, or power flow levels. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 5. | A Transmission Operator or Balancing Authority shall implement load shedding in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 7. | The Transmission Operator and Balancing Authority shall coordinate automatic load shedding throughout their areas with underfrequency isolation of generating units, tripping of shunt capacitors, and other automatic actions that will occur under abnormal frequency, voltage, or power flow conditions. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 7. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-1 | 8. | Each Transmission Operator or Balancing Authority shall have plans for operator-controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-1 | No Parts for 8. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-003 | EOP-003-2 | 1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 1. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 2. | Each Transmission Operator shall establish plans for automatic load shedding for undervoltage conditions if the Transmission Operator or its associated Transmission Planner(s) or Planning Coordinator(s) determine that an under-voltage load shedding scheme is required. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | [20 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 2. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans, excluding automatic under-frequency load shedding plans, among other interconnected Transmission Operators and Balancing Authorities. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 3. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 4. | A Transmission Operator shall consider one or more of these factors in designing an automatic under voltage load shedding scheme: voltage level, rate of voltage decay, or power flow levels. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | [20 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 4. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 5. | A Transmission Operator or Balancing Authority shall implement load shedding, excluding automatic under-frequency load shedding, in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 5. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 6. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 7. | The Transmission Operator shall coordinate automatic undervoltage load shedding throughout their areas with tripping of shunt capacitors, and other automatic actions that will occur under abnormal voltage, or power flow conditions |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | [20 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 7. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-003 | EOP-003-2 | 8. | Each Transmission Operator or Balancing Authority shall have plans for operator controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-003 | EOP-003-2 | No Parts for 8. |  |  |  | 2010-11-04 | 2011-03-31 | 2012-05-07 | 2012-07-10 | 2012-07-10 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM11-20-000
Inactive | EOP | EOP-004 | EOP-004-1 | 1. | Each Regional Reliability Organization shall establish and maintain a Regional reporting procedure to facilitate preparation of preliminary and final disturbance reports. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [16 empty] | RRO
Inactive | EOP | EOP-004 | EOP-004-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-004 | EOP-004-1 | 2. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall promptly analyze Bulk Electric System disturbances on its system or facilities. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004 | EOP-004-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-004 | EOP-004-1 | 3. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity experiencing a reportable incident shall provide a preliminary written report to its Regional Reliability Organization and NERC. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004 | EOP-004-1 | 3.1. | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004 | EOP-004-1 | 3.2. | Applicable reporting forms are provided in Attachments 1-EOP-004 and 2-EOP-004. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004 | EOP-004-1 | 3.3. | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004 | EOP-004-1 | 3.4. | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004 | EOP-004-1 | 4. | When a Bulk Electric System disturbance occurs, the Regional Reliability Organization shall make its representatives on the NERC Operating Committee and Disturbance Analysis Working Group available to the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity immediately affected by the disturbance for the purpose of providing any needed assistance in the investigation and to assist in the preparation of a final report. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [16 empty] | RRO
Inactive | EOP | EOP-004 | EOP-004-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-004 | EOP-004-1 | 5. | The Regional Reliability Organization shall track and review the status of all final report recommendations at least twice each year to ensure they are being acted upon in a timely manner. If any recommendation has not been acted on within two years, or if Regional Reliability Organization tracking and review indicates at any time that any recommendation is not being acted on with sufficient diligence, the Regional Reliability Organization shall notify the NERC Planning Committee and Operating Committee of the status of the recommendation(s) and the steps the Regional Reliability Organization has taken to accelerate implementation. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [16 empty] | RRO
Inactive | EOP | EOP-004 | EOP-004-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-12-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-004 | EOP-004-2 | 1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Each Responsible Entity will have a dated event reporting Operating Plan that includes, but is not limited to the protocol(s) and each organization identified to receive an event report for event types specified in EOP-004-2 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2012-11-07 | 2012-12-31 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD13-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004 | EOP-004-2 | No Parts for 1. |  | Each Responsible Entity will have a dated event reporting Operating Plan that includes, but is not limited to the protocol(s) and each organization identified to receive an event report for event types specified in EOP-004-2 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2012-11-07 | 2012-12-31 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD13-3-000
Inactive | EOP | EOP-004 | EOP-004-2 | 2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | Each Responsible Entity will have as evidence of reporting an event, copy of the completed EOP-004-2 Attachment 2 form or a DOE-OE-417 form; and evidence of submittal (e.g., operator log or other operating documentation, voice recording, electronic mail message, or confirmation of facsimile) demonstrating the event report was submitted within 24 hours of recognition of meeting the threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). (R2) | Operations Assessment | 2012-11-07 | 2012-12-31 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD13-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004 | EOP-004-2 | No Parts for 2. |  | Each Responsible Entity will have as evidence of reporting an event, copy of the completed EOP-004-2 Attachment 2 form or a DOE-OE-417 form; and evidence of submittal (e.g., operator log or other operating documentation, voice recording, electronic mail message, or confirmation of facsimile) demonstrating the event report was submitted within 24 hours of recognition of meeting the threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). (R2) | Operations Assessment | 2012-11-07 | 2012-12-31 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD13-3-000
Inactive | EOP | EOP-004 | EOP-004-2 | 3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | Each Responsible Entity will have dated records to show that it validated all contact information contained in the Operating Plan each calendar year. Such evidence may include, but are not limited to, dated voice recordings and operating logs or other communication documentation. (R3) | Operations Planning | 2012-11-07 | 2012-12-31 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD13-3-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004 | EOP-004-2 | No Parts for 3. |  | Each Responsible Entity will have dated records to show that it validated all contact information contained in the Operating Plan each calendar year. Such evidence may include, but are not limited to, dated voice recordings and operating logs or other communication documentation. (R3) | Operations Planning | 2012-11-07 | 2012-12-31 | 2013-06-20 | 2013-06-20 | 2014-01-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD13-3-000
Inactive | EOP | EOP-004 | EOP-004-3 | 1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2-3 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Each Responsible Entity will have a dated event reporting Operating Plan that includes, but is not limited to the protocol(s) and each organization identified to receive an event report for event types specified in EOP-004-3 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM15-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004 | EOP-004-3 | No Parts for 1. |  | Each Responsible Entity will have a dated event reporting Operating Plan that includes, but is not limited to the protocol(s) and each organization identified to receive an event report for event types specified in EOP-004-3 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | EOP | EOP-004 | EOP-004-3 | 2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | Each Responsible Entity will have as evidence of reporting an event, copy of the completed EOP-004-3 Attachment 2 form or a DOE-OE-417 form; and evidence of submittal (e.g., operator log or other operating documentation, voice recording, electronic mail message, or confirmation of facsimile) demonstrating the event report was submitted within 24 hours of recognition of meeting the threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). (R2) | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM15-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004 | EOP-004-3 | No Parts for 2. |  | Each Responsible Entity will have as evidence of reporting an event, copy of the completed EOP-004-3 Attachment 2 form or a DOE-OE-417 form; and evidence of submittal (e.g., operator log or other operating documentation, voice recording, electronic mail message, or confirmation of facsimile) demonstrating the event report was submitted within 24 hours of recognition of meeting the threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). (R2) | Operations Assessment | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM15-13-000
Inactive | EOP | EOP-004 | EOP-004-3 | 3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | Each Responsible Entity will have dated records to show that it validated all contact information contained in the Operating Plan each calendar year. Such evidence may include, but are not limited to, dated voice recordings and operating logs or other communication documentation. (R3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM15-13-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004 | EOP-004-3 | No Parts for 3. |  | Each Responsible Entity will have dated records to show that it validated all contact information contained in the Operating Plan each calendar year. Such evidence may include, but are not limited to, dated voice recordings and operating logs or other communication documentation. (R3) | Operations Planning | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM15-13-000
Mandatory Subject to Enforcement | EOP | EOP-004 | EOP-004-4 | 1. | R1. Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | M1. Each Responsible Entity will have a dated event reporting Operating Plan that includes protocol(s) and each organization identified to receive an event report for event types specified in EOP-004-4 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | EOP | EOP-004 | EOP-004-4 | No Parts for 1. |  | M1. Each Responsible Entity will have a dated event reporting Operating Plan that includes protocol(s) and each organization identified to receive an event report for event types specified in EOP-004-4 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-004 | EOP-004-4 | 2. | R2. Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | M2. Each Responsible Entity will have as evidence of reporting an event to the entities specified per their event reporting Operating Plan either a copy of the completed EOP-004-4 Attachment 2 form or a DOE-OE-417 form; and some evidence of submittal (e.g., operator log or other operating documentation, voice recording, electronic mail message, or confirmation of facsimile) demonstrating that the event report was submitted by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Operations Assessment | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | EOP | EOP-004 | EOP-004-4 | No Parts for 2. |  | M2. Each Responsible Entity will have as evidence of reporting an event to the entities specified per their event reporting Operating Plan either a copy of the completed EOP-004-4 Attachment 2 form or a DOE-OE-417 form; and some evidence of submittal (e.g., operator log or other operating documentation, voice recording, electronic mail message, or confirmation of facsimile) demonstrating that the event report was submitted by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Operations Assessment | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Filed and Pending Regulatory Approval | EOP | EOP-004 | EOP-004-5 | 1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-5 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | M1. Each Responsible Entity will have a dated event reporting Operating Plan that includes protocol(s) and each organization identified to receive an event report for the event types specified in EOP-004-5 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2026-06-18 | 2026-06-26 | [9 empty] | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | EOP | EOP-004 | EOP-004-5 | No Parts for 1. |  | M1. Each Responsible Entity will have a dated event reporting Operating Plan that includes protocol(s) and each organization identified to receive an event report for the event types specified in EOP-004-5 Attachment 1 and in accordance with the entity responsible for reporting. | Operations Planning | 2026-06-18 | 2026-06-26
Filed and Pending Regulatory Approval | EOP | EOP-004 | EOP-004-5 | 2. | Each Responsible Entity shall report events specified in EOP-004-5 Attachment 1 to the entities specified per their event reporting Operating Plan either by 24 hours after recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day, whichever occurs later (4:00 p.m. local time will be considered the end of the business day). | M2. Each Responsible Entity will have as evidence of reporting an event to the entities specified per their event reporting Operating Plan either a copy of the completed EOP-004-5 Attachment 3 form or a DOE-417 form; and some evidence of submittal (e.g., operator log or other operating documentation, voice recording, or electronic mail message) demonstrating that the event report was submitted either by 24 hours after recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day, whichever occurs later (4:00 p.m. local time will be considered the end of the business day). | Operations Assessment | 2026-06-18 | 2026-06-26 | [9 empty] | BA | DP |  |  | GO |  | GOP | [6 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | EOP | EOP-004 | EOP-004-5 | No Parts for 2. |  | M2. Each Responsible Entity will have as evidence of reporting an event to the entities specified per their event reporting Operating Plan either a copy of the completed EOP-004-5 Attachment 3 form or a DOE-417 form; and some evidence of submittal (e.g., operator log or other operating documentation, voice recording, or electronic mail message) demonstrating that the event report was submitted either by 24 hours after recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day, whichever occurs later (4:00 p.m. local time will be considered the end of the business day). | Operations Assessment | 2026-06-18 | 2026-06-26
Inactive | EOP | EOP-005 | EOP-005-0 | 1. | Each Transmission Operator shall have a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels. Each Transmission Operator shall include the applicable elements listed in Attachment 1-EOP-005-0 in developing a restoration plan. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 2. | Each Transmission Operator shall review and update its restoration plan at least annually and whenever it makes changes in the power system network, and shall correct deficiencies found during the simulated restoration exercises. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 3. | Each Transmission Operator shall develop restoration plans with a priority of restoring the integrity of the Interconnection. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 4. | Each Transmission Operator shall coordinate its restoration plans with Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 5. | Each Transmission Operator and Balancing Authority shall periodically test its telecommunication facilities needed to implement the restoration plan. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 6. | Each Transmission Operator and Balancing Authority shall train its operating personnel in the implementation of the restoration plan. Such training shall include simulated exercises, if practicable. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 7. | Each Transmission Operator and Balancing Authority shall verify the restoration procedure by actual testing or by simulation. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 8. | Each Transmission Operator shall ensure the availability and location of black start capability within its area to meet the needs of the restoration plan. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable
Inactive | EOP | EOP-005 | EOP-005-0 | 9. | Following a disturbance in which one or more areas of the Bulk Electric System become isolated or blacked out, the affected Transmission Operators and Balancing Authorities shall begin immediately to return the Bulk Electric System to normal. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.1. | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.2. | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators online, or load shedding. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.3. | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | BA
Inactive | EOP | EOP-005 | EOP-005-0 | 9.4. | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.5. | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.5.1. | Voltage, frequency, and phase angle permit. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.5.2. | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.5.3. | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-0 | 9.5.4. | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-05-02 | Filing/Order Docket No. RM06-16-000 EOP-005-0 was never enforceable | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 1. | Each Transmission Operator shall have a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels. Each Transmission Operator shall include the applicable elements listed in Attachment 1-EOP-005 in developing a restoration plan. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 1. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 2. | Each Transmission Operator shall review and update its restoration plan at least annually and whenever it makes changes in the power system network, and shall correct deficiencies found during the simulated restoration exercises. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 3. | Each Transmission Operator shall develop restoration plans with a priority of restoring the integrity of the Interconnection. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 3. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 4. | Each Transmission Operator shall coordinate its restoration plans with the Generator Owners and Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 4. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 5. | Each Transmission Operator and Balancing Authority shall periodically test its telecommunication facilities needed to implement the restoration plan. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 5. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 6. | Each Transmission Operator and Balancing Authority shall train its operating personnel in the implementation of the restoration plan. Such training shall include simulated exercises, if practicable. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 6. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 7. | Each Transmission Operator and Balancing Authority shall verify the restoration procedure by actual testing or by simulation. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 7. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 8. | Each Transmission Operator shall verify that the number, size, availability, and location of system blackstart generating units are sufficient to meet Regional Reliability Organization restoration plan requirements for the Transmission Operator’s area. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 8. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 9. | The Transmission Operator shall document the Cranking Paths, including initial switching requirements, between each blackstart generating unit and the unit(s) to be started and shall provide this documentation for review by the Regional Reliability Organization upon request. Such documentation may include Cranking Path diagrams. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | No Parts for 9. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | EOP | EOP-005 | EOP-005-1 | 10. | The Transmission Operator shall demonstrate, through simulation or testing, that the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 10.1. | The Transmission Operator shall perform this simulation or testing at least once every five years. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11. | Following a disturbance in which one or more areas of the Bulk Electric System become isolated or blacked out, the affected Transmission Operators and Balancing Authorities shall begin immediately to return the Bulk Electric System to normal. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.1. | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.2. | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators on line, or load shedding. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.3. | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | EOP | EOP-005 | EOP-005-1 | 11.4. | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.5. | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.5.1 | Voltage, frequency, and phase angle permit. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.5.2. | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.5.3. | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-1 | 11.5.4. | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1. | Each Transmission Operator shall have a restoration plan approved by its Reliability Coordinator. The restoration plan shall allow for restoring the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shut down area to service, to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.1. | Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.2. | A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.3. | Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.4. | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.5. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.6. | Identification of acceptable operating voltage and frequency limits during restoration. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.7. | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.8. | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 1.9. | Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. | Each Transmission Operator shall have evidence such as e-mails with receipts or registered mail receipts that it provided the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan in accordance with Requirement R2. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 2. |  | Each Transmission Operator shall have evidence such as e-mails with receipts or registered mail receipts that it provided the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan in accordance with Requirement R2. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually agreed predetermined schedule. | Each Transmission Operator shall have documentation such as a dated review signature sheet, revision histories, e-mails with receipts, or registered mail receipts, that it has annually reviewed and submitted the Transmission Operator’s restoration plan to its Reliability Coordinator in accordance with Requirement R3. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 3.1. | If there are no changes to the previously submitted restoration plan, the Transmission Operator shall confirm annually on a predetermined schedule to its Reliability Coordinator that it has reviewed its restoration plan and no changes were necessary. (Retirement approved by FERC effective January 21, 2014.) | Each Transmission Operator shall have documentation such as a dated review signature sheet, revision histories, e-mails with receipts, or registered mail receipts, that it has annually reviewed and submitted the Transmission Operator’s restoration plan to its Reliability Coordinator in accordance with Requirement R3. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 4. | Each Transmission Operator shall update its restoration plan within 90 calendar days after identifying any unplanned permanent System modifications, or prior to implementing a planned BES modification, that would change the implementation of its restoration plan. | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, e-mails with receipts, or registered mail receipts, that it has updated its restoration plan and submitted it to its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 4.1. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval within the same 90 calendar day period. | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, e-mails with receipts, or registered mail receipts, that it has updated its restoration plan and submitted it to its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its implementation date. | Each Transmission Operator shall have documentation that it has made the latest Reliability Coordinator approved copy of its restoration plan available in its primary and backup control rooms and its System Operators prior to its implementation date in accordance with Requirement R5. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 5. |  | Each Transmission Operator shall have documentation that it has made the latest Reliability Coordinator approved copy of its restoration plan available in its primary and backup control rooms and its System Operators prior to its implementation date in accordance with Requirement R5. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 6. | Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: | Each Transmission Operator shall have documentation such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 6.1. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. | Each Transmission Operator shall have documentation such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 6.2. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. | Each Transmission Operator shall have documentation such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 6.3. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. | Each Transmission Operator shall have documentation such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 7. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, each affected Transmission Operator shall implement its restoration plan. If the restoration plan cannot be executed as expected the Transmission Operator shall utilize its restoration strategies to facilitate restoration. | If there has been a Disturbance in which Blackstart Resources have been utilized in restoring the shut down area of the BES to service, each Transmission Operator involved shall have evidence such as voice recordings, e-mail, dated computer printouts, or operator logs, that it implemented its restoration plan or restoration plan strategies in accordance with Requirement R7. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 7. |  | If there has been a Disturbance in which Blackstart Resources have been utilized in restoring the shut down area of the BES to service, each Transmission Operator involved shall have evidence such as voice recordings, e-mail, dated computer printouts, or operator logs, that it implemented its restoration plan or restoration plan strategies in accordance with Requirement R7. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 8. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, the Transmission Operator shall resynchronize area(s) with neighboring Transmission Operator area(s) only with the authorization of the Reliability Coordinator or in accordance with the established procedures of the Reliability Coordinator. | If there has been a Disturbance in which Blackstart Resources have been utilized in restoring the shut down area of the BES to service, each Transmission Operator involved in such an event shall have evidence, such as voice recordings, e-mail, dated computer printouts, or operator logs, that it resynchronized shut down areas in accordance with Requirement R8. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 8. |  | If there has been a Disturbance in which Blackstart Resources have been utilized in restoring the shut down area of the BES to service, each Transmission Operator involved in such an event shall have evidence, such as voice recordings, e-mail, dated computer printouts, or operator logs, that it resynchronized shut down areas in accordance with Requirement R8. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 9. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 9.1. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 9.2. | A list of required tests including: | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 9.2.1. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 9.2.2. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 9.3. | The minimum duration of each of the required tests. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 10. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall include training on the following: | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 10.1. | System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 10.2. | Restoration priorities. | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 10.3. | Building of cranking paths. | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 10.4. | Synchronizing (re-energized sections of the System). | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | 11. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall have an electronic or hard copy of the training program material provided to their field switching personnel for System restoration training and the corresponding training records including training dates and duration in accordance with Requirement R11. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 |  | DP | [17 empty] | TO | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 11. |  | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall have an electronic or hard copy of the training program material provided to their field switching personnel for System restoration training and the corresponding training records including training dates and duration in accordance with Requirement R11. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 12. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Each Transmission Operator shall have evidence, such as training records, that it participated in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested in accordance with Requirement R12. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [20 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 12. |  | Each Transmission Operator shall have evidence, such as training records, that it participated in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested in accordance with Requirement R12. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 13. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | Each Transmission Operator and Generator Operator with a Blackstart Resource shall have the dated Blackstart Resource Agreements or mutually agreed upon procedures or protocols in accordance with Requirement R13. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP | [13 empty] | TOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 13. |  | Each Transmission Operator and Generator Operator with a Blackstart Resource shall have the dated Blackstart Resource Agreements or mutually agreed upon procedures or protocols in accordance with Requirement R13. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 14. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | Each Generator Operator with a Blackstart Resource shall have dated documented procedures on file for starting each unit and energizing a bus in accordance with Requirement R14. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 14. |  | Each Generator Operator with a Blackstart Resource shall have dated documented procedures on file for starting each unit and energizing a bus in accordance with Requirement R14. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 15. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | Each Generator Operator with a Blackstart Resource shall provide evidence, such as emails with receipts or registered mail receipts, showing that it notified its Transmission Operator of any known changes to its Blackstart Resource capabilities within twenty-four hours of such changes in accordance with Requirement R15. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 15. |  | Each Generator Operator with a Blackstart Resource shall provide evidence, such as emails with receipts or registered mail receipts, showing that it notified its Transmission Operator of any known changes to its Blackstart Resource capabilities within twenty-four hours of such changes in accordance with Requirement R15. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-005 | EOP-005-2 | 16. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. | Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as emails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R16. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | 16.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. | Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as emails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R16. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | 16.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as emails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R16. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | 17. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: | Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R17. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | 17.1. | System restoration plan including coordination with the Transmission Operator. | Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R17. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | 17.2. | The procedures documented in Requirement R14. | Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R17. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | 18. | Each Generator Operator shall participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. | Each Generator Operator shall have evidence, such as dated training records, that it participated in the Reliability Coordinator’s restoration drills, exercises, or simulations if requested to do so in accordance with Requirement R18. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-005 | EOP-005-2 | No Parts for 18. |  | Each Generator Operator shall have evidence, such as dated training records, that it participated in the Reliability Coordinator’s restoration drills, exercises, or simulations if requested to do so in accordance with Requirement R18. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1. | Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.1. | Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.2. | A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.3. | Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.4. | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.5. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.6. | Identification of acceptable operating voltage and frequency limits during restoration. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.7. | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.8. | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 1.9. | Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. | M1. Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | Each Transmission Operator shall have evidence such as dated electronic receipts or registered mail receipts that it provided the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan in accordance with Requirement R2. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 2. |  | Each Transmission Operator shall have evidence such as dated electronic receipts or registered mail receipts that it provided the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan in accordance with Requirement R2. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | Each Transmission Operator shall have documentation such as a dated review signature sheet, revision histories, dated electronic receipts, or registered mail receipts, that it has annually reviewed and submitted the Transmission Operator’s restoration plan to its Reliability Coordinator in accordance with Requirement R3. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 3. |  | Each Transmission Operator shall have documentation such as a dated review signature sheet, revision histories, dated electronic receipts, or registered mail receipts, that it has annually reviewed and submitted the Transmission Operator’s restoration plan to its Reliability Coordinator in accordance with Requirement R3. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 4. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, dated electronic receipts, or registered mail receipts, that it has submitted the revised restoration plan to its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 4.1. | Within 90 calendar days after identifying any unplanned permanent BES modifications. | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, dated electronic receipts, or registered mail receipts, that it has submitted the revised restoration plan to its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 4.2. | Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, dated electronic receipts, or registered mail receipts, that it has submitted the revised restoration plan to its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | Each Transmission Operator shall have documentation that it has made the latest Reliability Coordinator approved copy of its restoration plan, in electronic or hardcopy format, in its primary and backup control rooms and available to its System Operators prior to its effective date in accordance with Requirement R5. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 5. |  | Each Transmission Operator shall have documentation that it has made the latest Reliability Coordinator approved copy of its restoration plan, in electronic or hardcopy format, in its primary and backup control rooms and available to its System Operators prior to its effective date in accordance with Requirement R5. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 6. | Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: | M6. Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning, Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 6.1. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. | M6. Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning, Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 6.2. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. | M6. Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning, Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 6.3. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. | M6. Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | Long-Term Planning, Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 7. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 7.1. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 7.2. | A list of required tests including: | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 7.2.1. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 7.2.2. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 7.3. | The minimum duration of each of the required tests. | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 8. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: | M8. Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 8.1. | System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. | M8. Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 8.2. | Restoration priorities. | M8. Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 8.3. | Building of cranking paths. | M8. Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 8.4. | Synchronizing (re-energized sections of the System). | M8. Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 8.5 . | Transition of Demand and resource balance within its area to the Balancing Authority. | M8. Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 9. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | M9. Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall have an electronic or hard copy of the training program material provided to their field switching personnel for System restoration training and the corresponding training records including training dates and duration in accordance with Requirement R9. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 |  | DP | [17 empty] | TO | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 9. |  | M9. Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall have an electronic or hard copy of the training program material provided to their field switching personnel for System restoration training and the corresponding training records including training dates and duration in accordance with Requirement R9. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 10. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | M10. Each Transmission Operator shall have evidence that it participated in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested in accordance with Requirement R10. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 10. |  | M10. Each Transmission Operator shall have evidence that it participated in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested in accordance with Requirement R10. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 11. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | M11. Each Transmission Operator and Generator Operator with a Blackstart Resource shall have the dated Blackstart Resource Agreements or mutually agreed upon procedures or protocols in accordance with Requirement R11. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP | [13 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 11. |  | M11. Each Transmission Operator and Generator Operator with a Blackstart Resource shall have the dated Blackstart Resource Agreements or mutually agreed upon procedures or protocols in accordance with Requirement R11. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 12. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | M12. Each Generator Operator with a Blackstart Resource shall have dated documented procedures on file for starting each unit and energizing a bus in accordance with Requirement R12. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 12. |  | M12. Each Generator Operator with a Blackstart Resource shall have dated documented procedures on file for starting each unit and energizing a bus in accordance with Requirement R12. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 13. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | M13. Each Generator Operator with a Blackstart Resource shall provide evidence, such as dated electronic receipts or registered mail receipts, showing that it notified its Transmission Operator of any known changes to its Blackstart Resource capabilities within 24 hours of such changes in accordance with Requirement R13. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 13. |  | M13. Each Generator Operator with a Blackstart Resource shall provide evidence, such as dated electronic receipts or registered mail receipts, showing that it notified its Transmission Operator of any known changes to its Blackstart Resource capabilities within 24 hours of such changes in accordance with Requirement R13. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 14. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. | M14. Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as e-mails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R14. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 14.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. | M14. Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as e-mails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R14. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 14.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | M14. Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as e-mails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R14. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 15. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: | M15. Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup, energizing a bus and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R15. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 15.1. | System restoration plan including coordination with the Transmission Operator | M15. Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup, energizing a bus and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R15. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 15.2. | The procedures documented in Requirement R12 | M15. Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup, energizing a bus and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R15. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | 16. | Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | M16. Each Generator Operator shall have evidence that it participated in its Reliability Coordinator’s restoration drills, exercises, or simulations if requested to do so in accordance with Requirement R16. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005 | EOP-005-3 | No Parts for 16. |  | M16. Each Generator Operator shall have evidence that it participated in its Reliability Coordinator’s restoration drills, exercises, or simulations if requested to do so in accordance with Requirement R16. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Inactive | EOP | EOP-006 | EOP-006-0 | 1. | Each Reliability Coordinator shall be aware of the restoration plan of each Transmission Operator in its Reliability Coordinator Area in accordance with NERC and regional requirements. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable
Inactive | EOP | EOP-006 | EOP-006-0 | 2. | The Reliability Coordinator shall monitor restoration progress and coordinate any needed assistance. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable
Inactive | EOP | EOP-006 | EOP-006-0 | 3. | The Reliability Coordinator shall have a Reliability Coordinator Area restoration plan that provides coordination between individual Transmission Operator restoration plans and that ensures reliability is maintained during system restoration events. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable
Inactive | EOP | EOP-006 | EOP-006-0 | 4. | The Reliability Coordinator shall serve as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators and Transmission Operators or Balancing Authorities not immediately involved in restoration. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable
Inactive | EOP | EOP-006 | EOP-006-0 | 5. | Reliability Coordinators shall approve, communicate, and coordinate the re-synchronizing of major system islands or synchronizing points so as not to cause a Burden on adjacent Transmission Operator, Balancing Authority, or Reliability Coordinator Areas. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable
Inactive | EOP | EOP-006 | EOP-006-0 | 6. | The Reliability Coordinator shall take actions to restore normal operations once an operating emergency has been mitigated in accordance with its restoration plan. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 EOP-006-0 was never enforceable
Inactive | EOP | EOP-006 | EOP-006-1 | 1. | Each Reliability Coordinator shall be aware of the restoration plan of each Transmission Operator in its Reliability Coordinator Area in accordance with NERC and regional requirements. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-006 | EOP-006-1 | 2. | The Reliability Coordinator shall monitor restoration progress and coordinate any needed assistance. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-006 | EOP-006-1 | 3. | The Reliability Coordinator shall have a Reliability Coordinator Area restoration plan that provides coordination between individual Transmission Operator restoration plans and that ensures reliability is maintained during system restoration events. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-006 | EOP-006-1 | 4. | The Reliability Coordinator shall serve as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators and Transmission Operators or Balancing Authorities not immediately involved in restoration. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-006 | EOP-006-1 | 5. | Reliability Coordinators shall approve, communicate, and coordinate the re-synchronizing of major system islands or synchronizing points so as not to cause a Burden on adjacent Transmission Operator, Balancing Authority, or Reliability Coordinator Areas. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-006 | EOP-006-1 | 6. | The Reliability Coordinator shall take actions to restore normal operations once an operating emergency has been mitigated in accordance with its restoration plan. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | EOP | EOP-006 | EOP-006-2 | 1. | Each Reliability Coordinator shall have a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shut down area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and it its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.1. | A description of the high level strategy to be employed during restoration events for restoring the Interconnection including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.2. | Operating Processes for restoring the Interconnection. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.3. | Descriptions of the elements of coordination between individual Transmission Operator restoration plans. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.4. | Descriptions of the elements of coordination of restoration plans with neighboring Reliability Coordinators. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.5. | Criteria and conditions for reestablishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.6. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.7. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.8. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 1.9. | Criteria for transferring operations and authority back to the Balancing Authority. | Each Reliability Coordinator shall have available a dated copy of its restoration plan in accordance with Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision. | Each Reliability Coordinator shall provide evidence such as e-mails with receipts, posting to a secure web site with notification to affected entities, or registered mail receipts, that its most recent restoration plan has been distributed in accordance with Requirement R2. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | No Parts for 2. |  | Each Reliability Coordinator shall provide evidence such as e-mails with receipts, posting to a secure web site with notification to affected entities, or registered mail receipts, that its most recent restoration plan has been distributed in accordance with Requirement R2. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-006 | EOP-006-2 | 3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | Each Reliability Coordinator shall provide evidence such as a review signature sheet, or revision histories, that it has reviewed its restoration plan within 13 calendar months of the last review in accordance with Requirement R3. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | No Parts for 3. |  | Each Reliability Coordinator shall provide evidence such as a review signature sheet, or revision histories, that it has reviewed its restoration plan within 13 calendar months of the last review in accordance with Requirement R3. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-006 | EOP-006-2 | 4. | Each Reliability Coordinator shall review their neighboring Reliability Coordinator’s restoration plans. | Each Reliability Coordinator shall provide evidence such as dated review signature sheets that it has reviewed its neighboring Reliability Coordinator’s restoration plans and resolved any conflicts within 30 calendar days in accordance with Requirement R4. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 4.1. | If the Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved in 30 calendar days. | Each Reliability Coordinator shall provide evidence such as dated review signature sheets that it has reviewed its neighboring Reliability Coordinator’s restoration plans and resolved any conflicts within 30 calendar days in accordance with Requirement R4. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. | Each Reliability Coordinator shall provide evidence, such as a review signature sheet or emails, that it has reviewed, approved or disapproved, and notified its Transmission Operator’s within 30 calendar days following the receipt of the restoration plan from the Transmission Operator in accordance with Requirement R5. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 5.1. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Each Reliability Coordinator shall provide evidence, such as a review signature sheet or emails, that it has reviewed, approved or disapproved, and notified its Transmission Operator’s within 30 calendar days following the receipt of the restoration plan from the Transmission Operator in accordance with Requirement R5. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the implementation date. | Each Reliability Coordinator shall have documentation such as e-mail receipts that it has made the latest copy of its restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area available in its primary and backup control rooms and to each of its System Operators prior to the implementation date in accordance with Requirement R6. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | No Parts for 6. |  | Each Reliability Coordinator shall have documentation such as e-mail receipts that it has made the latest copy of its restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area available in its primary and backup control rooms and to each of its System Operators prior to the implementation date in accordance with Requirement R6. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-006 | EOP-006-2 | 7. | Each Reliability Coordinator shall work with its affected Generator Operators, and Transmission Operators as well as neighboring Reliability Coordinators to monitor restoration progress, coordinate restoration, and take actions to restore the BES frequency within acceptable operating limits. If the restoration plan cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate System restoration. | Each Reliability Coordinator involved shall have evidence such as voice recordings, email, dated computer printouts, or operator logs, that it monitored and coordinated restoration progress in accordance with Requirement R7. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | No Parts for 7. |  | Each Reliability Coordinator involved shall have evidence such as voice recordings, email, dated computer printouts, or operator logs, that it monitored and coordinated restoration progress in accordance with Requirement R7. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-006 | EOP-006-2 | 8. | The Reliability Coordinator shall coordinate or authorize resynchronizing islanded areas that bridge boundaries between Transmission Operators or Reliability Coordinators. If the resynchronization cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate resynchronization. | If there has been a resynchronizing of an islanded area, each Reliability Coordinator involved shall have evidence such as voice recordings, e-mail, or operator logs, that it coordinated or authorized resynchronizing in accordance with Requirement R8. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | No Parts for 8. |  | If there has been a resynchronizing of an islanded area, each Reliability Coordinator involved shall have evidence such as voice recordings, e-mail, or operator logs, that it coordinated or authorized resynchronizing in accordance with Requirement R8. | Real-Time Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | EOP | EOP-006 | EOP-006-2 | 9. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall address the following: | Each Reliability Coordinator shall have an electronic or hard copy of its training records available showing that it has provided training in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 9.1. | The coordination role of the Reliability Coordinator. | Each Reliability Coordinator shall have an electronic or hard copy of its training records available showing that it has provided training in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 9.2. | Reestablishing the Interconnection. | Each Reliability Coordinator shall have an electronic or hard copy of its training records available showing that it has provided training in accordance with Requirement R9. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 10. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. | Each Reliability Coordinator shall have evidence that it conducted two System restoration drills, exercises, or simulations per calendar year and that Transmission Operators and Generator Operators included in the Reliability Coordinator’s restoration plan were invited in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | EOP | EOP-006 | EOP-006-2 | 10.1. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least every two calendar years. | Each Reliability Coordinator shall have evidence that it conducted two System restoration drills, exercises, or simulations per calendar year and that Transmission Operators and Generator Operators included in the Reliability Coordinator’s restoration plan were invited in accordance with Requirement R10. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2013-07-01 | 2011-05-23 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1. | Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1.1. | A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1.2. | Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1.3. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1.4. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1.5. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 1.6. | Criteria for transferring operations and authority back to the Balancing Authority. | M1. Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | Operations Planning, Real-Time Operations | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision | M2. Each Reliability Coordinator shall provide evidence such as electronic receipts, posting to a secure website with notification to affected entities, or registered mail receipts, that its most recent restoration plan has been distributed in accordance with Requirement R2. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | No Parts for 2. |  | M2. Each Reliability Coordinator shall provide evidence such as electronic receipts, posting to a secure website with notification to affected entities, or registered mail receipts, that its most recent restoration plan has been distributed in accordance with Requirement R2. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | M3. Each Reliability Coordinator shall provide evidence such as a review signature sheet, or revision histories, that it has reviewed its restoration plan within 13 calendar months of the last review in accordance with Requirement R3. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | No Parts for 3. |  | M3. Each Reliability Coordinator shall provide evidence such as a review signature sheet, or revision histories, that it has reviewed its restoration plan within 13 calendar months of the last review in accordance with Requirement R3. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 4. | Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. | M4. Each Reliability Coordinator shall provide evidence such as dated review signature sheets or electronic receipt that it has reviewed its neighboring Reliability Coordinator’s restoration plans and resolved any conflicts within the timing requirements of Requirement R4 and Requirement R4, Part 4.1. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 4.1. | If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | M4. Each Reliability Coordinator shall provide evidence such as dated review signature sheets or electronic receipt that it has reviewed its neighboring Reliability Coordinator’s restoration plans and resolved any conflicts within the timing requirements of Requirement R4 and Requirement R4, Part 4.1. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. | M5. Each Reliability Coordinator shall provide evidence such as a dated review signature sheet or electronic receipt that it has reviewed, approved or disapproved, and notified its Transmission Operators within 30 calendar days following the receipt of the restoration plan from the Transmission Operator in accordance with Requirement R5. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 5.1. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | M5. Each Reliability Coordinator shall provide evidence such as a dated review signature sheet or electronic receipt that it has reviewed, approved or disapproved, and notified its Transmission Operators within 30 calendar days following the receipt of the restoration plan from the Transmission Operator in accordance with Requirement R5. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. | M6. Each Reliability Coordinator shall have documentation such as electronic receipts that it has made the latest copy of its restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area available in its primary and backup control rooms and to each of its System Operators prior to the effective date in accordance with Requirement R6. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | No Parts for 6. |  | M6. Each Reliability Coordinator shall have documentation such as electronic receipts that it has made the latest copy of its restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area available in its primary and backup control rooms and to each of its System Operators prior to the effective date in accordance with Requirement R6. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 7. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: | M7. Each Reliability Coordinator shall have an electronic copy or hard copy of its training records available showing that it has provided training in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 7.1. | The coordination role of the Reliability Coordinator; and | M7. Each Reliability Coordinator shall have an electronic copy or hard copy of its training records available showing that it has provided training in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 7.2. | Re-establishing the Interconnection. | M7. Each Reliability Coordinator shall have an electronic copy or hard copy of its training records available showing that it has provided training in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 8. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. | M8. Each Reliability Coordinator shall have evidence, such as dated electronic documents, that it conducted two System restoration drills, exercises, or simulations per calendar year in accordance with Requirement R8. And each Reliability Coordinator shall have evidence that the Reliability Coordinator requested each applicable Transmission Operator and Generator Operator to participate per Requirement R8 and Requirement R8, Part 8.1. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006 | EOP-006-3 | 8.1. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | M8. Each Reliability Coordinator shall have evidence, such as dated electronic documents, that it conducted two System restoration drills, exercises, or simulations per calendar year in accordance with Requirement R8. And each Reliability Coordinator shall have evidence that the Reliability Coordinator requested each applicable Transmission Operator and Generator Operator to participate per Requirement R8 and Requirement R8, Part 8.1. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Inactive | EOP | EOP-007 | EOP-007-0 | 1. | Each Regional Reliability Organization shall establish and maintain a system BCP, as part of an overall coordinated Regional SRP. The Regional SRP shall include requirements for verification through analysis how system blackstart generating units shall perform their intended functions and shall be sufficient to meet SRP expectations. The Regional Reliability Organization shall coordinate with and among other Regional Reliability Organizations as appropriate in the development of its BCP. The BCP shall include: |  |  | 2005-02-08 | 2006-04-04 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-23 | Filing/Order Docket No. RM06-16-000 FERC approved withdrawal of standard | [16 empty] | RRO
Inactive | EOP | EOP-007 | EOP-007-0 | 1.1. | A requirement to have a database that contains all blackstart generators1 designated for use in an SRP within the respective areas. This database shall be updated on an annual basis. The database shall include the name, location, megawatt capacity, type of unit, latest date of test, and starting method. |  |  | 2005-02-08 | 2006-04-04 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-23 | Filing/Order Docket No. RM06-16-000 FERC approved withdrawal of standard | [16 empty] | RRO
Inactive | EOP | EOP-007 | EOP-007-0 | 1.2. | A requirement to demonstrate that blackstart units perform their intended functions as required in the Regional SRP. This requirement can be met through either simulation or testing. The BCP must consider the availability of designated BCP units and initial transmission switching requirements. |  |  | 2005-02-08 | 2006-04-04 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-23 | Filing/Order Docket No. RM06-16-000 FERC approved withdrawal of standard | [16 empty] | RRO
Inactive | EOP | EOP-007 | EOP-007-0 | 1.4. | A requirement to review and update the Regional BCP at least every five years. |  |  | 2005-02-08 | 2006-04-04 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-23 | Filing/Order Docket No. RM06-16-000 FERC approved withdrawal of standard | [16 empty] | RRO
Inactive | EOP | EOP-007 | EOP-007-0 | 2. | The Regional Reliability Organization shall provide documentation of its system BCPs to NERC within 30 calendar days of a request. |  |  | 2005-02-08 | 2006-04-04 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-23 | Filing/Order Docket No. RM06-16-000 FERC approved withdrawal of standard | [16 empty] | RRO
Inactive | EOP | EOP-007 | EOP-007-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-23 | Filing/Order Docket No. RM06-16-000 FERC approved withdrawal of standard
Inactive | EOP | EOP-008 | EOP-008-0 | 1. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have a plan to continue reliability operations in the event its control center becomes inoperable. The contingency plan must meet the following requirements: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.1. | The contingency plan shall not rely on data or voice communication from the primary control facility to be viable. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.2. | The plan shall include procedures and responsibilities for providing basic tie line control and procedures and for maintaining the status of all inter-area schedules, such that there is an hourly accounting of all schedules. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.3. | The contingency plan must address monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events. The plan shall list the critical facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.4. | The plan shall include procedures and responsibilities for maintaining basic voice communication capabilities with other areas. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.5. | The plan shall include procedures and responsibilities for conducting periodic tests, at least annually, to ensure viability of the plan. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.6. | The plan shall include procedures and responsibilities for providing annual training to ensure that operating personnel are able to implement the contingency plans. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.7. | The plan shall be reviewed and updated annually. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-0 | 1.8. | Interim provisions must be included if it is expected to take more than one hour to implement the contingency plan for loss of primary control facility. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include the following, at a minimum: [See Standard pdf for what the Operating Plan for backup functionality shall include] | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.1. | The location and method of implementation for providing backup functionality for the time it takes to restore the primary control center functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.2. | A summary description of the elements required to support the backup functionality. These elements shall include, at a minimum: | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.2.1. | Tools and applications to ensure that System Operators have situational awareness of the BES. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.2.2. | Data communications. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.2.3. | Voice communications. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.2.4. | Power source(s). | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.2.5. | Physical and cyber security. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2013-07-01 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.3. | An Operating Process for keeping the backup functionality consistent with the primary control center. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.4. | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.5. | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.6. | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include at a minimum: | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.6.1. | A list of all entities to notify when there is a change in operating locations. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.6.2. | Actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of the primary or backup functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 1.6.3. | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force copy of its Operating Plan for backup functionality in accordance with Requirement R2, in electronic or hardcopy format, available at its primary control center and at the location providing backup functionality. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | No Parts for 2. |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, in force copy of its Operating Plan for backup functionality in accordance with Requirement R2, in electronic or hardcopy format, available at its primary control center and at the location providing backup functionality. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000
Inactive | EOP | EOP-008 | EOP-008-1 | 3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: · Planned outages of the primary or backup facilities of two weeks or less · Unplanned outages of the primary or backup facilities | Each Reliability Coordinator shall provide dated evidence that it has a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality in accordance with Requirement R3. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | [13 empty] | RC
Inactive | EOP | EOP-008 | EOP-008-1 | No Parts for 3. |  | Each Reliability Coordinator shall provide dated evidence that it has a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality in accordance with Requirement R3. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000
Inactive | EOP | EOP-008 | EOP-008-1 | 4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority and Transmission Operator’s primary control center functionality respectively. To avoid requiring tertiary functionality, backup functionality is not required during: - Planned outages of the primary or backup functionality of two weeks or less - Unplanned outages of the primary or backup functionality | Each Balancing Authority and Transmission Operator shall provide dated evidence that its backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority or Transmission Operator’s primary control center functionality respectively in accordance with Requirement R4. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | No Parts for 4. |  | Each Balancing Authority and Transmission Operator shall provide dated evidence that its backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority or Transmission Operator’s primary control center functionality respectively in accordance with Requirement R4. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000
Inactive | EOP | EOP-008 | EOP-008-1 | 5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall have evidence that its dated, current, in force Operating Plan for backup functionality, in electronic or hardcopy format, has been reviewed and approved annually and that it has been updated within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1 in accordance with Requirement R5. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 5.1. | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall have evidence that its dated, current, in force Operating Plan for backup functionality, in electronic or hardcopy format, has been reviewed and approved annually and that it has been updated within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1 in accordance with Requirement R5. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have dated evidence that its primary and backup functionality do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards in accordance with Requirement R6. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | No Parts for 6. |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have dated evidence that its primary and backup functionality do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards in accordance with Requirement R6. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000
Inactive | EOP | EOP-008 | EOP-008-1 | 7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 7.1. | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 7.2. | The backup functionality for a minimum of two continuous hours. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 | 2011-06-27 |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | 8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of their primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide evidence that a plan has been submitted to its Regional Entity within six calendar months of the date when the functionality is lost showing how it will re-establish primary or backup functionality in accordance with Requirement R8. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008 | EOP-008-1 | No Parts for 8. |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of their primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide evidence that a plan has been submitted to its Regional Entity within six calendar months of the date when the functionality is lost showing how it will re-establish primary or backup functionality in accordance with Requirement R8. | Operations Planning | 2010-08-05 | 2011-02-11 | 2011-04-21 | 2011-06-27 | 2011-06-27 |  |  |  |  | 2019-03-31 | Filing/Order Docket No. RM11-4-000
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.1. | The location and method of implementation for providing backup functionality. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.2. | A summary description of the elements required to support the backup functionality. These elements shall include: | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.2.1. | Tools and applications to ensure that System Operators have situational awareness of the BES. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.2.2. | Data exchange capabilities. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.2.3. | Interpersonal Communications. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.2.4. | Power source(s). | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.2.5. | Physical and cyber security. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.3. | An Operating Process for keeping the backup functionality consistent with the primary control center. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.4. | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.5. | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.6. | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.6.1. | A list of all entities to notify when there is a change in operating locations. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.6.2. | Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 1.6.3. | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | M1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | M2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect copy of its Operating Plan for backup functionality in accordance with Requirement R2, in electronic or hardcopy format, available at its primary control center and at the location providing backup functionality. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | No Parts for 2. |  | M2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect copy of its Operating Plan for backup functionality in accordance with Requirement R2, in electronic or hardcopy format, available at its primary control center and at the location providing backup functionality. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | M3. Each Reliability Coordinator shall provide dated evidence that it has a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that are applicable to the primary control center functionality in accordance with Requirement R3. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | No Parts for 3. |  | M3. Each Reliability Coordinator shall provide dated evidence that it has a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that are applicable to the primary control center functionality in accordance with Requirement R3. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | M4. Each Balancing Authority and Transmission Operator shall provide dated evidence that its backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s or Transmission Operator’s primary control center functionality in accordance with Requirement R4. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | No Parts for 4. |  | M4. Each Balancing Authority and Transmission Operator shall provide dated evidence that its backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s or Transmission Operator’s primary control center functionality in accordance with Requirement R4. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. | M5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have evidence that its dated, current, and in effect Operating Plan for backup functionality, in electronic or hardcopy format, has been reviewed and approved annually and that it has been updated within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1 in accordance with Requirement R5. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 5.1. | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | M5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have evidence that its dated, current, and in effect Operating Plan for backup functionality, in electronic or hardcopy format, has been reviewed and approved annually and that it has been updated within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1 in accordance with Requirement R5. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | M6. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have dated evidence that its primary and backup functionality do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards in accordance with Requirement R6. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | No Parts for 6. |  | M6. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have dated evidence that its primary and backup functionality do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards in accordance with Requirement R6. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: | M7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 7.1 . | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. | M7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2019-04-01 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 7.2. | The backup functionality for a minimum of two continuous hours. | M7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | 2018-03-26 |  |  |  |  | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | 8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | M8. Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of their primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide evidence that a plan has been submitted to its Regional Entity within six calendar months of the date when the functionality is lost showing how it will re-establish primary or backup functionality in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000 | BA | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008 | EOP-008-2 | No Parts for 8. |  | M8. Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of their primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide evidence that a plan has been submitted to its Regional Entity within six calendar months of the date when the functionality is lost showing how it will re-establish primary or backup functionality in accordance with Requirement R8. | Operations Planning | 2017-02-09 | 2017-03-27 | 2018-01-18 | 2018-03-26 | 2019-04-01 | [5 empty] | Filing/Order Docket No. RM17-12-000
Inactive | EOP | EOP-009 | EOP-009-0 | 1. | The Generator Operator of each blackstart generating unit shall test the startup and operation of each system blackstart generating unit identified in the BCP as required in the Regional BCP (Reliability Standard EOP-007-0_R1). Testing records shall include the dates of the tests, the duration of the tests, and an indication of whether the tests met Regional BCP requirements. |  | Long-Term Planning, Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 | [6 empty] | GOP
Inactive | EOP | EOP-009 | EOP-009-0 | No Parts for 1. |  |  | Long-Term Planning, Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | EOP | EOP-009 | EOP-009-0 | 2. | The Generator Owner or Generator Operator shall provide documentation of the test results of the startup and operation of each blackstart generating unit to the Regional Reliability Organizations and upon request to NERC. |  | Long-Term Planning, Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO |  | GOP
Inactive | EOP | EOP-009 | EOP-009-0 | No Parts for 2. |  |  | Long-Term Planning, Operations Planning, Real-Time Operations | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-06-30 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 1. | Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: [Please see the standard for more information] | M1. Each Reliability Coordinator shall have a current GMD Operating Plan meeting all the provisions of Requirement R1; evidence such as a review or revision history to indicate that the GMD Operating Plan has been maintained; and evidence to show that the plan was implemented as called for in its GMD Operating Plan, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 |  | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 1.1. | A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. | M1. Each Reliability Coordinator shall have a current GMD Operating Plan meeting all the provisions of Requirement R1; evidence such as a review or revision history to indicate that the GMD Operating Plan has been maintained; and evidence to show that the plan was implemented as called for in its GMD Operating Plan, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 | 2015-04-01 | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 1.2. | A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. | M1. Each Reliability Coordinator shall have a current GMD Operating Plan meeting all the provisions of Requirement R1; evidence such as a review or revision history to indicate that the GMD Operating Plan has been maintained; and evidence to show that the plan was implemented as called for in its GMD Operating Plan, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 | 2015-04-01 | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 2. | Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | M2. Each Reliability Coordinator shall have evidence such as dated operator logs, voice recordings, transcripts, or electronic communications to indicate that forecasted and current space weather information was disseminated as stated in its GMD Operating Plan. | Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 |  | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have evidence such as dated operator logs, voice recordings, transcripts, or electronic communications to indicate that forecasted and current space weather information was disseminated as stated in its GMD Operating Plan. | Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 |  | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 3. | Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: [Please see the standard for more information] | M3. Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 |  | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 3.1. | Steps or tasks to receive space weather information. | M3. Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 | 2015-04-01 | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 3.2. | System Operator actions to be initiated based on predetermined conditions. | M3. Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 | 2015-04-01 | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-010 | EOP-010-1 | 3.3. | The conditions for terminating the Operating Procedure or Operating Process. | M3. Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | Long-Term Planning, Operations Planning, Real-Time Operations, Same-Day Operations | 2013-11-07 | 2013-11-14 | 2014-06-19 | 2014-08-25 | 2015-04-01 | 2015-04-01 | X |  |  |  | Filing/Order Docket No. RM14-1-000 A FERC order was issued on June 19, 2014, approving EOP-010-1. Requirement 2 of Reliability Standard EOP-010-1 will not become effective until the first day following retirement of Reliabili | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable:[See Standard for additional information.] | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.1. | Roles and responsibilities for activating the Operating Plan(s); | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2. | Processes to prepare for and mitigate Emergencies including: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2.2. | Cancellation or recall of Transmission and generation outages; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2.3. | Transmission system reconfiguration; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2.4. | Redispatch of generation request; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 1.2.6. | Reliability impacts of extreme weather conditions. | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | 2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [See Standard for additional information.] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.1. | Roles and responsibilities for activating the Operating Plan(s); | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2. | Processes to prepare for and mitigate Emergencies including: | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.3. | Managing generating resources in its Balancing Authority Area to address: | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.3.1. | capability and availability; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.3.2. | fuel supply and inventory concerns; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.3.3. | fuel switching capabilities; and | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.3.4. | environmental constraints. | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.4. | Public appeals for voluntary Load reductions; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.6. | Reduction of internal utility energy use; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 2.2.9. | Reliability impacts of extreme weather conditions. | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | BA
Inactive | EOP | EOP-011 | EOP-011-1 | 3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | 3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | 3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | 3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | 3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | 4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-1 | No Parts for 4. |  | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000
Inactive | EOP | EOP-011 | EOP-011-1 | 5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators . | Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | No Parts for 5. |  | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators . | Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000
Inactive | EOP | EOP-011 | EOP-011-1 | 6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-1 | No Parts for 6. |  | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2014-11-13 | 2014-12-29 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2023-03-31 | RM15-7-000
Inactive | EOP | EOP-011 | EOP-011-2 | 1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.1. | Roles and responsibilities for activating the Operating Plan(s); | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2. | Processes to prepare for and mitigate Emergencies including: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.2. | Cancellation or recall of Transmission and generation outages; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.3. | Transmission system reconfiguration; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.4. | Redispatch of generation request; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.6. | Provisions to determine reliability impacts of: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.6.1 | cold weather conditions; and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 1.2.6.2 | extreme weather conditions. | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | 2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.1. | Roles and responsibilities for activating the Operating Plan(s); | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2. | Processes to prepare for and mitigate Emergencies including: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.3. | Managing generating resources in its Balancing Authority Area to address: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.3.1. | capability and availability; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.3.2. | fuel supply and inventory concerns; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.3.3. | fuel switching capabilities; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.3.4. | environmental constraints. | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.4. | Public appeals for voluntary Load reductions; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.6. | Reduction of internal utility energy use; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.9. | Provisions to determine reliability impacts of: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.9.1 | cold weather conditions; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 2.2.9.2 | extreme weather conditions. | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA
Inactive | EOP | EOP-011 | EOP-011-2 | 3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | 3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | 3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | 3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | 3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | M3. The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | 4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-2 | No Parts for 4. |  | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000
Inactive | EOP | EOP-011 | EOP-011-2 | 5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators . | Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | No Parts for 5. |  | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators . | Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000
Inactive | EOP | EOP-011 | EOP-011-2 | 6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-2 | No Parts for 6. |  | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000
Inactive | EOP | EOP-011 | EOP-011-2 | 7. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.1. | Generating unit(s) freeze protection measures based on geographical location and plant configuration; | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.2. | Annual inspection and maintenance of generating unit(s) freeze protection measures; | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3. | Generating unit(s) cold weather data, to include: | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.1. | Generating unit(s) operating limitations in cold weather to include: | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.1.1. | capability and availability; | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.1.2. | fuel supply and inventory concerns; | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.1.3. | fuel switching capabilities; and | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.1.4. | environmental constraints. | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.2. | Generating unit(s) minimum: | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.2.1. | design temperature; or | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.2.2. | historical operating temperature; or | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 7.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | M7. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R7. | Operations Planning, Real-Time Operations | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 | 2023-04-01 |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-011 | EOP-011-2 | 8. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide the training to its maintenance or operations personnel responsible for implementing cold weather preparedness plan(s) developed pursuant to Requirement R7. | M8. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R8. | Long-Term Planning, Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000 |  |  |  |  | GO |  | GOP
Inactive | EOP | EOP-011 | EOP-011-2 | No Parts for 8. |  | M8. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R8. | Long-Term Planning, Operations Planning | 2021-06-11 | 2021-06-17 | 2021-08-24 | 2023-04-01 | 2023-04-01 |  |  |  |  | 2024-09-30 | Filing/Order Docket No. RD21-5-000
Inactive | EOP | EOP-011 | EOP-011-3 | 1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.1. | Roles and responsibilities for activating the Operating Plan(s); | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2. | Processes to prepare for and mitigate Emergencies including: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.2. | Cancellation or recall of Transmission and generation outages; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.3. | Transmission system reconfiguration; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.4. | Redispatch of generation request; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.5. | Operator-controlled manual Load shedding during an Emergency that accounts for each of the following: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.5.1. | Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.5.2. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that serve designated critical loads; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.5.3. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for underfrequency load shed (UFLS) or undervoltage load shed (UVLS); and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.5.4. | Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions. | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.6. | Provisions to determine reliability impacts of: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.6.1. | cold weather conditions; and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 1.2.6.2. | extreme weather conditions. | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [20 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | 2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.1. | Roles and responsibilities for activating the Operating Plan(s); | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2. | Processes to prepare for and mitigate Emergencies including: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.3. | Managing generating resources in its Balancing Authority Area to address: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.3.1. | capability and availability; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.3.2. | fuel supply and inventory concerns; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.3.3. | fuel switching capabilities; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.3.4. | environmental constraints. | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.4. | Public appeals for voluntary Load reductions; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.6. | Reduction of internal utility energy use; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.8. | Provisions for Transmission Operators to implement operator-controlled manual Load shed in accordance with Requirement R1 Part 1.2.5; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.9. | Provisions to determine reliability impacts of: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.9.1. | cold weather conditions; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 2.2.9.2. | extreme weather conditions. | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA
Inactive | EOP | EOP-011 | EOP-011-3 | 3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | 3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | 3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | 3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | 3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | 4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | BA | [19 empty] | TOP
Inactive | EOP | EOP-011 | EOP-011-3 | No Parts for 4. |  | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000
Inactive | EOP | EOP-011 | EOP-011-3 | 5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | No Parts for 5. |  | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000
Inactive | EOP | EOP-011 | EOP-011-3 | 6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000 | [13 empty] | RC
Inactive | EOP | EOP-011 | EOP-011-3 | No Parts for 6. |  | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  |  | Filing/Order Docket No. RD23-1-000
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.1. | Roles and responsibilities for activating the Operating Plan(s); | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2. | Processes to prepare for and mitigate Emergencies including: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.2. | Cancellation or recall of Transmission and generation outages; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.3. | Transmission system reconfiguration; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.4. | Redispatch of generation request; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.5. | Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2027-04-01 | X |  | Manual load shed - 10/1/2024 effective date UVLS and UFLS - 4/1/2027 effective date |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.5.1. | Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.5.2. | Provisions to minimize the overlap of circuits that are designated for manual Load shed, UVLS, or UFLS and circuits that serve designated critical loads which are essential to the reliability of the BES; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  | Manual load shed - 10/1/2024 effective date UVLS and UFLS - 4/1/2027 effective date |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.5.3. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for UFLS or UVLS; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.5.4. | Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions; | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.5.5. | Provisions for the identification and prioritization of designated critical natural gas infrastructure loads which are essential to the reliability of the BES as defined by the Applicable Entity; and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2027-04-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.6. | Provisions to determine reliability impacts of: | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.6.1. | Cold weather conditions; and | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 1.2.6.2. | Extreme weather conditions. | M1. Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.1. | Roles and responsibilities for activating the Operating Plan(s); | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2. | Processes to prepare for and mitigate Emergencies including: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.1. | Notification to its Reliability Coordinator to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.10. | Provisions to determine reliability impacts of: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.10.1. | Cold weather conditions; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.10.2. | Extreme weather conditions. | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.3. | Managing generating resources in its Balancing Authority Area to address: | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.3.1. | Capability and availability; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.3.2. | Fuel supply and inventory concerns; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.3.3. | Fuel switching capabilities; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.3.4. | Environmental constraints. | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.4. | Public appeals for voluntary Load reductions; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.6. | Reduction of internal utility energy use; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.7. | Use of Interruptible Load, curtailable Load, and demand response; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.8. | Provisions for excluding critical natural gas infrastructure loads which are essential to the reliability of the BES, as defined by the Applicable Entity, as Interruptible Load, curtailable Load, and demand response during extreme cold weather periods within each Balancing Authority Area; | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2027-04-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 2.2.9. | Provisions for Transmission Operators to implement operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding in accordance with Requirement R1 Part 1.2.5; and | M2. Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2027-04-01 | X |  | Manual load shed - 10/1/2024 effective date UVLS and UFLS - 4/1/2027 effective date |  | Filing/Order Docket No. RD24-1-000 | BA
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | M3. The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 | 2024-10-01 | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000 | BA | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | No Parts for 4. |  | M4. The Transmission Operator and Balancing Authority will have documentation, such as dated emails or other correspondence, with an Operating Plan(s) version history showing that it responded and updated the Operating Plan(s) within the timeframe identified by its Reliability Coordinator in accordance with Requirement R4. | Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | No Parts for 5. |  | M5. Each Reliability Coordinator that receives an Emergency notification from a Balancing Authority or Transmission Operator within its Reliability Coordinator Area will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that will be used to determine if the Reliability Coordinator communicated, in accordance with Requirement R5, with other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000 | [13 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | No Parts for 6. |  | M6. Each Reliability Coordinator, with a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area, will have, and provide upon request, evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence that it declared an Energy Emergency Alert, as detailed in Attachment 1, in accordance with Requirement R6. | Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X |  |  |  | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 7. | Each Transmission Operator shall annually identify and notify Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding. | M7. Each Transmission Operator will have documentation, such as dated emails or other correspondences that it identified and notified Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners annually in accordance with Requirement R7. | Long-Term Planning, Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | No Parts for 7. |  | M7. Each Transmission Operator will have documentation, such as dated emails or other correspondences that it identified and notified Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners annually in accordance with Requirement R7. | Long-Term Planning, Operations Planning | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2024-10-01 |  | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8. | Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 |  | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.1. | Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.1.1. | Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.1.2. | Provisions to minimize the overlap of circuits that are designated for manual, undervoltage, or underfrequency Load shed and circuits that serve designated critical loads which are essential to the reliability of the BES; | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.1.3. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for UFLS or UVLS; | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.1.4. | Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions; and | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.1.5. | Provisions for the identification and prioritization of designated critical natural gas infrastructure loads which are essential to the reliability of the BES as defined by the Applicable Entity. | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Mandatory Subject to Enforcement | EOP | EOP-011 | EOP-011-4 | 8.2. | Provisions to provide the Load shedding plan to the Transmission Operator for review. | M8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area will have a dated Load shedding plan(s) developed in accordance with Requirement R8 and evidence that the Load shedding plan(s) was provided to its Transmission Operator; evidence such as a review or revision history to indicate that the Load shedding plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Load shedding plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R8. | Long-Term Planning, Operations Planning, Real-Time Operations | 2023-10-23 | 2023-10-30 | 2024-02-15 | 2024-02-15 | 2027-04-01 | 2027-04-01 | X | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  |  | Filing/Order Docket No. RD24-1-000 |  | DP | DP-UFLS | [16 empty] | TO
Inactive | EOP | EOP-012 | EOP-012-1 | 1. | For each generating unit(s) with a commercial operation date subsequent to [Effective Date of this requirement], the Generator Owner shall: • Implement freeze protection measures that provide capability to operate for a period of not less than twelve (12) continuous hours at the Extreme Cold Weather Temperature for the unit(s), assuming a concurrent twenty (20) mph wind speed on any exposed Generator Cold Weather Critical Components; or • Explain in a declaration any technical, commercial, or operational constraints, as defined by the Generator Owner, that preclude the ability to implement appropriate freeze protection measures to provide capability of operating for twelve (12) hours at the documented Extreme Cold Weather Temperature. | M1. Each Generator Owner will have dated evidence that demonstrates it has the capability to operate in accordance with Requirement R1. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Documentation of cold weather preparedness plan, documentation of design features, any declaration that contains dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning, Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X | April 1, 2028 Compliance Date for EOP-012-1 - Requirement R1 and R2 Entities shall not be required to comply with Requirement R1 and R2 until 42 months after the effective date of Reliability Standard EOP-012-1. |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | No Parts for 1. |  | M1. Each Generator Owner will have dated evidence that demonstrates it has the capability to operate in accordance with Requirement R1. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Documentation of cold weather preparedness plan, documentation of design features, any declaration that contains dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning, Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X | April 1, 2028 Compliance Date for EOP-012-1 - Requirement R1 and R2 Entities shall not be required to comply with Requirement R1 and R2 until 42 months after the effective date of Reliability Standard EOP-012-1. |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000
Inactive | EOP | EOP-012 | EOP-012-1 | 2. | For each generating unit(s) in commercial operation prior to [Effective Date of this requirement], the Generator Owner shall ensure its generating unit(s) add new or modify existing freeze protection measures as needed to provide the capability to operate for a period of not less than one (1) hour at the unit(s) Extreme Cold Weather Temperature. Generating unit(s) that are not capable of operating for one (1) hour at its Extreme Cold Weather Temperature shall develop a Corrective Action Plan (CAP) for the identified issues, including identification of any needed modifications to the cold weather preparedness plan required under Requirement R3. | M2. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R2, or it has developed a CAP for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating units minimum temperature per Part 3.5.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, cold weather preparedness plan, and CAP(s). | Long-Term Planning, Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | No Parts for 2. |  | M2. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R2, or it has developed a CAP for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating units minimum temperature per Part 3.5.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, cold weather preparedness plan, and CAP(s). | Long-Term Planning, Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000
Inactive | EOP | EOP-012 | EOP-012-1 | 3. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.1 | The Extreme Cold Weather Temperature for their unit(s) including the calculation date and source of temperature data; | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.2 | Documentation identifying the Generator Cold Weather Critical Components; | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.3 | Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which may include measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.4 | Annual inspection and maintenance of generating unit(s) freeze protection measures; and | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5 | Generating unit(s) cold weather data, to include: | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5.1 | Generating unit(s) operating limitations in cold weather to include: | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5.1.1 | Capability and availability; | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5.1.2 | Fuel supply and inventory concerns; | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5.1.3 | Fuel switching capabilities; and | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5.1.4 | Environmental constraints. | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 3.5.2 | Generating unit(s) minimum: - Design temperature; - Historical operating temperature; or - Current cold weather performance temperature determined by an engineering analysis. | M3. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 4. | Once every five calendar years, each Generator Owner shall for each generating unit: | M4. Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 4.1. | Calculate the Extreme Cold Weather Temperature, and update the cold weather preparedness plan if this temperature is now lower than the previous lowest calculation; | M4. Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 4.2 | Review its documented generating unit(s) minimum temperature contained within its cold weather preparedness plan(s), pursuant to Part 3.5.2; and | M4. Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 4.3 | Review whether its generating units have the freeze protection measures required to operate at the Extreme Cold Weather Temperature pursuant to R1 or R2 as applicable, and if not develop a CAP for the identified issues, including identification of any needed modifications to the cold weather preparedness plan required under Requirement R3. | M4. Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | Operations Planning, Real-Time Operations | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 5. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R3. | M5. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5. | Long-Term Planning, Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO |  | GOP
Inactive | EOP | EOP-012 | EOP-012-1 | No Parts for 5. |  | M5. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5. | Long-Term Planning, Operations Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000
Inactive | EOP | EOP-012 | EOP-012-1 | 6. | Each Generator Owner that owns a generating unit that experiences a Generator Cold Weather Reliability Event shall develop a CAP, within 150 days or by July 1, whichever is earlier, that contains at a minimum: | M6. Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 6.1 | A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data; | M6. Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 6.2 | A review of applicability to similar equipment at other generating units owned by the Generator Owner; | M6. Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 6.3 | An identification of any temporary operating limitations or impacts to the cold weather preparedness plan, that would apply until execution of the corrective action(s) identified in the CAP. | M6. Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 7. | Each Generator Owner shall: | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R7. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 7.1 | Implement each CAP developed pursuant to Requirements R2, R4, or R6, or explain in a declaration why corrective actions are not being implemented due to any technical, commercial, or operational constraints as defined by the Generator Owner. | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R7. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-1 | 7.2 | Update each CAP if actions or timetables change, until completed. | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R7. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2022-02-16 | 2022-12-16 | 2023-02-16 |  |  |  | X |  |  | 2024-09-30 | Filing/Order Docket No. RD23-1-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1. | At least once every five calendar years, each Generator Owner shall, for each of its applicable generating unit(s): | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.1. | Calculate the Extreme Cold Weather Temperature for each of its applicable unit(s) and identify the calculation date and source of temperature data; and | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.1.1. | If the re-calculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) months of the recalculation. If new corrective actions are needed to provide the required operational capability under Requirement R2 or R3, the entity shall develop a Corrective Action Plan within 6 months of the recalculation. | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2. | Identify generating unit(s) cold weather data, to include: | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.1. | Generating unit(s) operating limitations in cold weather to include: | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.1.1. | Capability and availability; | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.1.2. | Fuel supply and inventory concerns; | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.1.3. | Start-up issues; | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.1.4. | Fuel switching capabilities; and | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.1.5. | Environmental constraints. | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 1.2.2. | Generating unit(s) minimum: • Design temperature, and if available, the concurrent wind speed and precipitation; • Historical operating temperature at least one hour in duration, and if available, the concurrent wind speed and precipitation; or • Current cold weather performance temperature determined by an engineering analysis, which includes the concurrent wind speed and precipitation. | M1.Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 2. | Applicable to generating units with a commercial operation date on or after October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), [1] shall: • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or • Develop a Corrective Action Plan(s) to add new or modify existing or previously planned freeze protection measures to provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with a sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours. [1] Generating unit(s) that do not self-commit or are not required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), but may be called upon to operate in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), are exempt from this requirement. | M2. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R2, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s). | Long-Term Planning, Operations Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | No Parts for 2. |  | M2. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R2, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s). | Long-Term Planning, Operations Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000
Inactive | EOP | EOP-012 | EOP-012-2 | 4. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained. | Operations Planning, Real-Time Operations | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 4.1. | The lowest calculated Extreme Cold Weather Temperature for each unit, as determined in Requirement R1;3 | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained. | Operations Planning, Real-Time Operations | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 4.2. | The generating unit cold weather data, as determined in Requirement R1.2; | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained. | Operations Planning, Real-Time Operations | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 4.3. | Documentation identifying Generator Cold Weather Critical Components; | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained. | Operations Planning, Real-Time Operations | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 4.4. | Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); and | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained. | Operations Planning, Real-Time Operations | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 4.5. | Annual inspection and maintenance of generating unit(s) freeze protection measures. | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained. | Operations Planning, Real-Time Operations | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 5. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4. | M5. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5. | Long-Term Planning, Operations Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO |  | GOP
Inactive | EOP | EOP-012 | EOP-012-2 | No Parts for 5. |  | M5. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5. | Long-Term Planning, Operations Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000
Inactive | EOP | EOP-012 | EOP-012-2 | 6. | Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),4 develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: | M6. Each Generator Owner will have documented evidence that it developed a Corrective Action Plan following a Cold Weather Reliability Event at an applicable unit in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s) and updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 6.1. | A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data; | M6. Each Generator Owner will have documented evidence that it developed a Corrective Action Plan following a Cold Weather Reliability Event at an applicable unit in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s) and updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 6.2. | A review of applicability to similar equipment at generating units owned by the Generator Owner; and | M6. Each Generator Owner will have documented evidence that it developed a Corrective Action Plan following a Cold Weather Reliability Event at an applicable unit in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s) and updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 6.3. | An identification of operating limitations or impacts to the cold weather preparedness plan that would apply until execution of the corrective action(s) identified in the Corrective Action Plan. | M6. Each Generator Owner will have documented evidence that it developed a Corrective Action Plan following a Cold Weather Reliability Event at an applicable unit in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s) and updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7. | Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.1. | Include a timetable for implementing the selected corrective action(s) that shall: | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.1.1. | List the action(s) which address(es) existing equipment or freeze protection measures, if any, to be completed within 24 calendar months of completing development of the Corrective Action Plan; | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.1.2. | List the action(s) which require(s) new equipment or freeze protection measures, if any, to be completed within 48 calendar months of completing development of the Corrective Action Plan; and | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.1.3. | List the updates to the cold weather preparedness plan required under Requirement R4 to identify the updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures; | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.2. | Implement the Corrective Action Plan in accordance with the specified timetables in Requirement R7 Part 7.1; | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.3. | Update the Corrective Action Plan action(s) and timetable(s), with justification, if corrective action(s) change or timetable(s) exceed the timelines in Requirement R7 Part 7.1; and | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 7.4. | Document in a declaration, with justification, any Generator Cold Weather Constraint that precludes the Generator Owner from implementing selected action(s) contained within the Corrective Action Plan. | M7. Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 8. | Each Generator Owner that creates a Generator Cold Weather Constraint declaration shall: | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the review and updated operating limitations as needed. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the performance of the review and update to the operating limitations, as needed. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 8.1. | Review the Generator Cold Weather Constraint declaration at least every five calendar years or as needed when a change of status to the Generator Cold Weather Constraint occurs; and | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the review and updated operating limitations as needed. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the performance of the review and update to the operating limitations, as needed. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 8.2. | Update the operating limitations associated with capability and availability under Requirement R1 Part R1.2 if applicable. | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the review and updated operating limitations as needed. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the performance of the review and update to the operating limitations, as needed. | Long-Term Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2024-10-01 | 2024-10-01 | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | 3. | Applicable to generating unit(s) in commercial operation prior to October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), [2] shall: • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature; or • Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature. [2] Generating unit(s) that do not self-commit or are not required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), but may be called upon to operate in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), are exempt from this requirement. | M3. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R3, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature per Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s). | Long-Term Planning, Operations Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2025-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000 |  |  |  |  | GO
Inactive | EOP | EOP-012 | EOP-012-2 | No Parts for 3. |  | M3. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R3, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature per Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s). | Long-Term Planning, Operations Planning | 2024-02-15 | 2024-02-16 | 2024-06-27 | 2024-06-27 | 2025-10-01 |  | X |  |  | 2025-09-30 | Filing/Order Docket No. RD24-5-000
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1. | At least once every five (5) calendar years, each Generator Owner shall, for each of its applicable generating unit(s): | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.1. | Calculate the Extreme Cold Weather Temperature for each of its applicable generating unit(s) and identify the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, if necessary; and | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.1.1. | If the recalculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) calendar months of the recalculation, and if new corrective actions are needed to provide the required operational capability described in Requirement R2 or R3, the entity shall develop a Corrective Action Plan within six (6) calendar months of the recalculation. | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2. | Identify generating unit(s) cold weather data, to include: | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.1. | Generating unit(s) operating limitations in cold weather to include: | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.1.1. | Capability and availability; | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.1.2. | Fuel supply and inventory concerns; | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.1.3. | Start-up issues; | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.1.4. | Fuel switching capabilities; and | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.1.5. | Environmental constraints. | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 1.2.2. | Generating unit(s) minimum: • Design temperature, and if available, the concurrent wind speed and precipitation; • Historical operating temperature at least one hour in duration, and if available, the concurrent wind speed and precipitation; or • Current cold weather performance temperature determined by an engineering analysis, which includes the concurrent wind speed and precipitation. | M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, and design information, operating data, or engineering analysis that supports its generating unit minimum temperature. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 2. | Applicable to generating units that begin commercial operation [1] on or after October 1, 2027 [2]: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), [3] shall: • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the generating unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph (32 km/h) wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or • Document in a declaration, with justification, if applicable, a Generator Cold Weather Constraint in accordance with Requirement R8. [1] Commercial operation means achievement of this designation indicating that the facility has received all approvals necessary for operation after completion of initial start-up testing. [2] In non-U.S. jurisdictions, this will be the date established by the Applicable Governmental Authority. [3] Generating unit(s) that do not self-commit or are not required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), but may be called upon to operate in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), are exempt from this requirement. | M2. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its generating unit(s) in accordance with R2, or it has declared a Generator Cold Weather Constraint for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the generating unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Generator Cold Weather Constraints (if applicable). | Long-Term Planning, Operations Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 |  |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | No Parts for 2. |  | M2. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its generating unit(s) in accordance with R2, or it has declared a Generator Cold Weather Constraint for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the generating unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Generator Cold Weather Constraints (if applicable). | Long-Term Planning, Operations Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 |  |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 3. | Applicable to generating unit(s) in commercial operation prior to October 1, 2027: [4] Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), [5] shall: • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the generating unit(s)' Extreme Cold Weather Temperature; or • Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the generating unit(s)' Extreme Cold Weather Temperature. [4] In non-U.S. jurisdictions, this will be the date established by the Applicable Governmental Authority. [5] Generating unit(s) that do not self-commit or are not required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), but may be called upon to operate in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), are exempt from this requirement. | M3. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its generating unit(s) in accordance with R3, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature per Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s). | Long-Term Planning, Operations Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | No Parts for 3. |  | M3. Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its generating unit(s) in accordance with R3, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature per Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s). | Long-Term Planning, Operations Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 4. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation, to demonstrate inspections and maintenance have been completed, may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components. | Operations Planning, Real-Time Operations | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 4.1. | The lowest calculated Extreme Cold Weather Temperature for each generating unit, as determined in Requirement R1; [6] [6] Generator Owners shall include the lowest calculated Extreme Cold Weather Temperature for the unit, even where subsequent periodic re-calculations under Requirement R1 Part 1.1 cause an increase in the Extreme Cold Weather Temperature. | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation, to demonstrate inspections and maintenance have been completed, may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components. | Operations Planning, Real-Time Operations | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 4.2. | The generating unit cold weather data, as determined in Requirement R1, Part 1.2; | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation, to demonstrate inspections and maintenance have been completed, may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components. | Operations Planning, Real-Time Operations | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 4.3. | Documentation identifying Generator Cold Weather Critical Components; | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation, to demonstrate inspections and maintenance have been completed, may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components. | Operations Planning, Real-Time Operations | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 4.4. | Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components that includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation, to demonstrate inspections and maintenance have been completed, may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components. | Operations Planning, Real-Time Operations | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 4.5. | Annual inspection and maintenance of generating unit(s) freeze protection measures implemented on Generator Cold Weather Critical Components. | M4. Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation, to demonstrate inspections and maintenance have been completed, may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components. | Operations Planning, Real-Time Operations | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 5. | Each Generator Owner, in conjunction with its Generator Operator, shall identify the entity responsible for providing generating unit-specific training, and that identified entity shall provide annual training to the maintenance and operations personnel, as applicable, responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4. | M5. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5. | Long-Term Planning, Operations Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO |  | GOP
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | No Parts for 5. |  | M5. Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5. | Long-Term Planning, Operations Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6. | Each Generator Owner shall, after experiencing a Generator Cold Weather Reliability Event at a generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), [7] develop and implement [8] a Corrective Action Plan(s) to address identified freezing issues as follows: [7] Generating unit(s) that do not self-commit or are not required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), but may be called upon to operate in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), are exempt from this requirement. [8] If a Generator Owner has previously experienced a Generator Cold Weather Reliability Event and developed a Corrective Action Plan for the generating unit or units under Requirement R6 Parts 6.1 or 6.2, the Generator Owner may review and update its existing plan(s) in lieu of developing a new plan. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.1. | The Generator Owner shall develop a Corrective Action Plan for the generating unit that experienced a Generator Cold Weather Reliability Event no later than prior to the first day of the first December following the Generator Cold Weather Reliability Event. [9] [9] For events that occur in September, October, or November, the timetable shall specify completion prior to December 1 of the following calendar year. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.2. | The Generator Owner shall conduct a review of other generating unit(s) in its fleet with the same or similar equipment as the affected generating unit to determine if any of those generating unit(s) are susceptible to the identified freezing issues. If corrective actions are needed, the Generator Owner shall develop or update a Corrective Action Plan to address the other generating unit(s). This review and, if applicable, the development or update of any Corrective Action Plan(s), shall be completed no later than 12 calendar months following the Generator Cold Weather Reliability Event. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3. | For each Corrective Action Plan, the Generator Owner shall include at a minimum: | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.1. | A summary of the identified cause(s) of the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data; | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.2. | A list of actions to add new freeze protection measures or remedy issues with existing freeze protection measures; | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.3. | An identification of operating limitations on the generating unit(s), or impacts to the cold weather preparedness plan, if any, that would apply until implementation of the corrective action(s) identified in the Corrective Action Plan is completed; | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.4. | A description of the updates to the cold weather preparedness plan required under Requirement R4 to identify updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures, if required; and | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.5. | A timetable specifying that implementation of the Corrective Action Plan(s) shall be completed as follows: | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.5.1. | For the generating unit experiencing the Generator Cold Weather Reliability Event, prior to the first day of the first December following the Generator Cold Weather Reliability Event. [10] [10] For events that occur in September, October or November, the timetable shall specify completion prior to December 1 of the following calendar year. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.3.5.2. | For other generating unit(s) owned by the Generator Owner, within 24 calendar months of completing the review required in Part 6.2, or no later than 36 calendar months following the Generator Cold Weather Reliability Event. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.4. | If a Generator Owner determines it will be unable to complete one or more of the actions in a Corrective Action Plan in accordance with the timetables specified in Requirement R6 Part 6.3.5 due to circumstances beyond its control, the Generator Owner shall submit a Corrective Action Plan extension request to the Compliance Enforcement Authority (CEA) for approval. The submitted Corrective Action Plan extension request shall include the following: | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.4.1. | An explanation of the circumstances causing the delay and why those circumstances are beyond the control of the Generator Owner; | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.4.2. | Revisions to the selected actions in Part 6.3.2, if any, including utilization of operating procedures, if applicable; and | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.4.3. | Updated timetable for implementing the selected actions in Part 6.3.2. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 6.5. | The Generator Owner shall document in a declaration, with justification, if applicable, any Generator Cold Weather Constraint in accordance with Requirement R8, as applicable. | M6. Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7. | Each Generator Owner that is required to develop a Corrective Action Plan under Requirements R1, R3, or R9 shall develop and implement the Corrective Action Plan in accordance with the following: | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.1. | For each Corrective Action Plan, the Generator Owner shall include at a minimum the following: | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.1.1. | A list of any actions that require new freeze protection measures, with a timetable specifying completion of such measures within 48 calendar months of completing development of the Corrective Action Plan; | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.1.2. | A list of any actions that remedy issues with existing freeze protection measures with a timetable specifying completion of such measures within 24 calendar months of completing development of the Corrective Action Plan (regardless of any longer timelines in the Corrective Action Plan associated with new freeze protection measures); | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.1.3. | A description of updates to the cold weather preparedness plan required under Requirement R4 to identify the updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures; and | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.1.4. | An identification of operating limitations on the generating unit(s), or impacts to the cold weather preparedness plan, if any, that would apply until implementation of the corrective action(s) identified in the Corrective Action Plan is completed. | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.2. | If a Generator Owner determines it will be unable to complete one or more of the actions in a Corrective Action Plan in accordance with the timetables specified in Requirement R7 Part 7.1 due to circumstances beyond its control, the Generator Owner shall submit a Corrective Action Plan extension request to the CEA for approval. The submitted Corrective Action Plan extension request shall include the following: | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.2.1. | An explanation of the circumstances causing the delay and how those circumstances are beyond the control of the Generator Owner; | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.2.2. | Revisions to the selected actions in Parts 7.1, if any, including utilization of operating procedures, if applicable; and | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.2.3. | Updated timetable for implementing the selected actions in Part 7.1. | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 7.3. | The Generator Owner shall document in a declaration, with justification, if applicable, any Generator Cold Weather Constraint in accordance with Requirement R8. | M7. Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 8. | Each Generator Owner that declares a Generator Cold Weather Constraint in accordance with Attachment 1 shall: | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the actions in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): a copy of the Generator Cold Weather Constraint declaration, evidence the declaration was provided to the CEA in accordance with the specified timeframe, records that document update(s) to the operating limitations, as needed, updates to the Corrective Action Plan(s), if applicable, and documentation and notice to the CEA of subsequent Generator Cold Weather Reliability Events, if applicable. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 |  |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 8.1. | Submit its Generator Cold Weather Constraint declaration(s) to the CEA as follows: • For Generator Cold Weather Constraints determined in accordance with Requirement R2 for generating unit(s) upon beginning commercial operation, submit within 15 calendar days after commercial operation; or • For all other Generator Cold Weather Constraints, submit within 45 calendar days of determining that the Generator Cold Weather Constraint is applicable. | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the actions in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): a copy of the Generator Cold Weather Constraint declaration, evidence the declaration was provided to the CEA in accordance with the specified timeframe, records that document update(s) to the operating limitations, as needed, updates to the Corrective Action Plan(s), if applicable, and documentation and notice to the CEA of subsequent Generator Cold Weather Reliability Events, if applicable. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 8.2. | Update the operating limitations under Requirement R1 Part R1.2 if applicable; | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the actions in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): a copy of the Generator Cold Weather Constraint declaration, evidence the declaration was provided to the CEA in accordance with the specified timeframe, records that document update(s) to the operating limitations, as needed, updates to the Corrective Action Plan(s), if applicable, and documentation and notice to the CEA of subsequent Generator Cold Weather Reliability Events, if applicable. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 8.3. | If the CEA determines the declared Generator Cold Weather Constraint is invalid, update its Corrective Action Plan(s) to require corrective actions be completed in accordance with Requirement R6 or Requirement R7, as applicable, subject to any extensions approved by the CEA, or implement freeze protection measures to provide the necessary capability in accordance with Requirement R2; | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the actions in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): a copy of the Generator Cold Weather Constraint declaration, evidence the declaration was provided to the CEA in accordance with the specified timeframe, records that document update(s) to the operating limitations, as needed, updates to the Corrective Action Plan(s), if applicable, and documentation and notice to the CEA of subsequent Generator Cold Weather Reliability Events, if applicable. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 8.4. | Document and provide notice to the CEA, when a generating unit experiences a Generator Cold Weather Reliability Event with the same cause of a previous Generator Cold Weather Reliability Event at the same or a similar unit, and one or more corrective actions to address the cause is addressed by an existing validated Generator Cold Weather Constraint for the same or a similar unit. | M8. Each Generator Owner shall have dated evidence that demonstrates it performed the actions in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): a copy of the Generator Cold Weather Constraint declaration, evidence the declaration was provided to the CEA in accordance with the specified timeframe, records that document update(s) to the operating limitations, as needed, updates to the Corrective Action Plan(s), if applicable, and documentation and notice to the CEA of subsequent Generator Cold Weather Reliability Events, if applicable. | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  | Phased-in highlights EOP-012-3 Requirement R2 – New Generating Units entering commercial operation on/after October 1, 2027 Entities shall become compliant with Requirement R2 no later than the commercial operations date for the applicable unit, except as provided below. Any Generator Cold Weather Constraint shall be submitted in accordance with the timeline provided in Requirement R8. For generating units for which the GO first contractually committed to design criteria relevant to this Requirement before June 29, 2023, and which enter commercial operation between October 1, 2027 and March 31, 2028, the GO shall comply with Requirement R2 relating to implementing required capability by no later than April 1, 2028. Requirement R8 Previously-declared Generator Cold Weather Constraints to be submitted for CEA review by November 15, 2025 Newly declared Generator Cold Weather Constraints shall be submitted in accordance with the timelines specified in Requirement R8. |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 9. | The Generator Owner shall review each Generator Cold Weather Constraint declaration validated by the CEA at least once every 36 calendar months to determine if it remains valid in accordance with Attachment 1. | M9. Each Generator Owner shall have dated evidence that demonstrates it reviewed Generator Cold Weather Constraints in accordance with Requirement R9. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the performance of the review within the required timeframe, records that demonstrate that a Corrective Action Plan was developed or updated within the required timeframe (if applicable). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | [5 empty] | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | EOP | EOP-012 | EOP-012-3 | 9.1. | If a Generator Cold Weather Constraint is determined to be no longer valid, then within six (6) calendar months of such determination, the Generator Owner shall develop or update a Corrective Action Plan pursuant to Requirement R7. | M9. Each Generator Owner shall have dated evidence that demonstrates it reviewed Generator Cold Weather Constraints in accordance with Requirement R9. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the performance of the review within the required timeframe, records that demonstrate that a Corrective Action Plan was developed or updated within the required timeframe (if applicable). | Long-Term Planning | 2025-04-04 | 2025-04-10 | 2025-09-18 | 2025-09-18 | 2025-10-01 | 2025-10-01 |  |  |  |  | Filing/Order Docket No. RD25-7-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-0 | 1. | The Transmission Owner shall document, maintain, and publish facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Reliability Organization, subregional, Power Pool, and individual Transmission Owner planning criteria and facility connection requirements. The Transmission Owner’s facility connection requirements shall address connection requirements for: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 1.1. | Generation facilities, |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 1.2. | Transmission facilities, and |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 1.3. | End-user facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2. | The Transmission Owner’s facility connection requirements shall address, but are not limited to, the following items: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.1. | Procedures for coordinated joint studies of new facilities and their impacts on the interconnected transmission systems. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.10. | Power quality impacts. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.11. | Equipment Ratings. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.12. | Synchronizing of facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.13. | Maintenance coordination. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.14. | Operational issues (abnormal frequency and voltages). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.15. | Inspection requirements for existing or new facilities. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.16. | Communications and procedures during normal and emergency operating conditions. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.2. | Procedures for notification of new or modified facilities to others (those responsible for the reliability of the interconnected transmission systems) as soon as feasible. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.3. | Voltage level and MW and MVAR capacity or demand at point of connection. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.4. | Breaker duty and surge protection. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.5. | System protection and coordination. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.6. | Metering and telecommunications. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.7. | Grounding and safety issues. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.8. | Insulation and insulation coordination. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 2.1.9. | Voltage, Reactive Power, and power factor control. |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | 3. | The Transmission Owner shall maintain and update its facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Reliability Organization, and NERC on request (five business days). |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-0 | No Parts for 3. |  |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-11-24 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-001 | FAC-001-1 | 1. | The Transmission Owner shall document, maintain, and publish Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. The Transmission Owner’s Facility connection requirements shall address connection requirements for: 1.1. Generation Facilities, 1.2. Transmission Facilities, and 1.3. End-user Facilities | M1. The Transmission Owner shall make available (to its Compliance Enforcement Authority) evidence that it met all the requirements stated in Requirement R1. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 1.1. | Generation Facilities, | M1. The Transmission Owner shall make available (to its Compliance Enforcement Authority) evidence that it met all the requirements stated in Requirement R1. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 1.2. | Transmission Facilities, and | M1. The Transmission Owner shall make available (to its Compliance Enforcement Authority) evidence that it met all the requirements stated in Requirement R1. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 1.3. | End-user Facilities | M1. The Transmission Owner shall make available (to its Compliance Enforcement Authority) evidence that it met all the requirements stated in Requirement R1. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 2. | Each applicable Generator Owner shall, within 45 days of having an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems (under FAC-002-1), document and publish its Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. | M2. Each Generator Owner that has an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R2. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-1 | No Parts for 2. |  | M2. Each Generator Owner that has an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R2. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-001 | FAC-001-1 | 3. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall address the following items in its Facility connection requirements: 3.1. Provide a written summary of its plans to achieve the required system performance as described in Requirements R1 or R2 throughout the planning horizon: 3.1.1. Procedures for coordinated joint studies of new Facilities and their impacts on the interconnected Transmission systems. 3.1.2. Procedures for notification of new or modified Facilities to others (those responsible for the reliability of the interconnected Transmission systems) as soon as feasible. 3.1.3. Voltage level and MW and MVAR capacity or demand at point of connection. 3.1.4. Breaker duty and surge protection. 3.1.5. System protection and coordination. 3.1.6. Metering and telecommunications. 3.1.7. Grounding and safety issues. 3.1.8. Insulation and insulation coordination. 3.1.9. Voltage, Reactive Power, and power factor control. 3.1.10. Power quality impacts. 3.1.11. Equipment Ratings. 3.1.12. Synchronizing of Facilities. 3.1.13. Maintenance coordination. 3.1.14. Operational issues (abnormal frequency and voltages). 3.1.15. Inspection requirements for existing or new Facilities. 3.1.16. Communications and procedures during normal and emergency operating conditions. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1. | Provide a written summary of its plans to achieve the required system performance as described in Requirements R1 or R2 throughout the planning horizon: | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.1. | Procedures for coordinated joint studies of new Facilities and their impacts on the interconnected Transmission systems. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.10. | Power quality impacts. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.11. | Equipment Ratings. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.12. | Synchronizing of Facilities. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.13. | Maintenance coordination. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.14. | Operational issues (abnormal frequency and voltages). | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.15. | Inspection requirements for existing or new Facilities. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.16. | Communications and procedures during normal and emergency operating conditions. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.2. | Procedures for notification of new or modified Facilities to others (those responsible for the reliability of the interconnected Transmission systems) as soon as feasible. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.3. | Voltage level and MW and MVAR capacity or demand at point of connection. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.4. | Breaker duty and surge protection. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.5. | System protection and coordination. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.6. | Metering and telecommunications. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.7. | Grounding and safety issues. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.8. | Insulation and insulation coordination. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 3.1.9. | Voltage, Reactive Power, and power factor control. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall make available (to its Compliance Enforcement Authority) evidence that it met all requirements stated in Requirement R3. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 | 2013-11-25 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | 4. | The Transmission Owner shall maintain and update its Facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Entity, and ERO on request (five business days). | M4. The Transmission Owner shall make available (to its Compliance Enforcement Authority) evidence that it met all the requirements stated in Requirement R4. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-1 | No Parts for 4. |  | M4. The Transmission Owner shall make available (to its Compliance Enforcement Authority) evidence that it met all the requirements stated in Requirement R4. | Long-Term Planning | 2012-02-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2013-11-25 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-001 | FAC-001-2 | 1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 1.1. | generation Facilities; | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 1.2. | transmission Facilities; and | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2016-01-01 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 1.3. | end-user Facilities. | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | M2. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R2. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-2 | No Parts for 2. |  | M2. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R2. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000
Inactive | FAC | FAC-001 | FAC-001-2 | 3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-2 | 4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-2 | 4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-2 | 4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2018-12-31 | Filing/Order Docket No. RD14-12-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-3 | 1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 1.1. | generation Facilities; | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 1.2. | transmission Facilities; and | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 1.3. | end-user Facilities | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | M2. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R2. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-3 | No Parts for 2. |  | M2. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R2. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000
Inactive | FAC | FAC-001 | FAC-001-3 | 3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 3.3. | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified transmission Facilities are within a Balancing Authority Area’s metered boundaries. | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 | [19 empty] | TO
Inactive | FAC | FAC-001 | FAC-001-3 | 4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-3 | 4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-3 | 4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 |  |  |  |  | GO
Inactive | FAC | FAC-001 | FAC-001-3 | 4.3. | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified generation Facilities are within a Balancing Authority Area’s metered boundaries. | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2016-02-11 | 2016-04-20 | 2017-09-20 | 2017-11-27 | 2019-01-01 | 2019-01-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RM16-13-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | 1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R1.1. | generation Facilities; | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R1.2. | transmission Facilities; and | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R1.3. | end-user Facilities. | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | 2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | M2. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R2. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | No Parts for 2. |  | M2. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R2. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | 3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R3.1. | Procedures for coordinated studies for new interconnections or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator and their impacts on affected systems. | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections or existing interconnections seeking to make a qualified change. | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R3.3. | Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change are within a Balancing Authority Area. | M3. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | 4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-001 | FAC-001-4 | R4.3. | Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change as defined by the Planning Coordinator are within a Balancing Authority Area. | M4. Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Inactive | FAC | FAC-002 | FAC-002-0 | 1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-0 | 1.1. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-0 | 1.2. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-0 | 1.3. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-0 | 1.4. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance in accordance with Reliability Standard TPL-001-0. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-0 | 1.5. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | Long-Term Planning | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-0 | 2. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) Regional Reliability Organization(s) and NERC on request (within 30 calendar days). |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 |  | DP |  |  | GO |  |  |  |  | LSE | PA | PC | [7 empty] | TO |  | TP
Inactive | FAC | FAC-002 | FAC-002-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-002 | FAC-002-1 | 1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | M1. The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load- Serving Entity, and Distribution Provider’s documentation of its assessment of the reliability impacts of new facilities shall address all items in Reliability Standard FAC-002-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-1 | 1.1. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. | M1. The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load- Serving Entity, and Distribution Provider’s documentation of its assessment of the reliability impacts of new facilities shall address all items in Reliability Standard FAC-002-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-1 | 1.2. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. | M1. The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load- Serving Entity, and Distribution Provider’s documentation of its assessment of the reliability impacts of new facilities shall address all items in Reliability Standard FAC-002-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-1 | 1.3. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. | M1. The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load- Serving Entity, and Distribution Provider’s documentation of its assessment of the reliability impacts of new facilities shall address all items in Reliability Standard FAC-002-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-1 | 1.4. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under both normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | M1. The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load- Serving Entity, and Distribution Provider’s documentation of its assessment of the reliability impacts of new facilities shall address all items in Reliability Standard FAC-002-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-1 | 1.5. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. | M1. The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load- Serving Entity, and Distribution Provider’s documentation of its assessment of the reliability impacts of new facilities shall address all items in Reliability Standard FAC-002-0_R1. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 | 2011-01-10 |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-1 | 2. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) and NERC on request (within 30 calendar days). | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, LoadServing Entity, and Distribution Provider shall each have evidence of its assessment of the reliability impacts of new facilities and their connections on the interconnected transmission systems is retained and provided to other entities in accordance with Reliability Standard FAC-002-0_R2. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014 |  | DP |  |  | GO |  |  |  |  | LSE | PA | PC | [7 empty] | TO |  | TP
Inactive | FAC | FAC-002 | FAC-002-1 | No Parts for 2. |  | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, LoadServing Entity, and Distribution Provider shall each have evidence of its assessment of the reliability impacts of new facilities and their connections on the interconnected transmission systems is retained and provided to other entities in accordance with Reliability Standard FAC-002-0_R2. |  | 2010-08-05 | 2010-09-09 | 2011-01-10 | 2011-01-10 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM06-22-014
Inactive | FAC | FAC-002 | FAC-002-2 | 1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-2 | 1.1. | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-2 | 1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-2 | 1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-2 | 1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 | 2014-11-06 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-2 | 2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M2. Each Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R2. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 |  |  |  |  | GO
Inactive | FAC | FAC-002 | FAC-002-2 | No Parts for 2. |  | M2. Each Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R2. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000
Inactive | FAC | FAC-002 | FAC-002-2 | 3. | Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M3. Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R3. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 |  | DP | [7 empty] | LSE | [9 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-2 | No Parts for 3. |  | M3. Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R3. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000
Inactive | FAC | FAC-002 | FAC-002-2 | 4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M4. Each Transmission Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R4. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 | [19 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-2 | No Parts for 4. |  | M4. Each Transmission Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R4. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000
Inactive | FAC | FAC-002 | FAC-002-2 | 5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M5. Each applicable Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R5. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000 |  |  |  |  | GO
Inactive | FAC | FAC-002 | FAC-002-2 | No Parts for 5. |  | M5. Each applicable Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R5. | Long-Term Planning | 2014-08-14 | 2014-08-22 | 2014-11-06 | 2014-11-06 | 2016-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-12-000
Inactive | FAC | FAC-002 | FAC-002-3 | 1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-3 | 1.1. | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-3 | 1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-3 | 1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-3 | 1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 | 2021-04-01 |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 | [10 empty] | PA | PC | [9 empty] | TP
Inactive | FAC | FAC-002 | FAC-002-3 | 2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Each Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 |  |  |  |  | GO
Inactive | FAC | FAC-002 | FAC-002-3 | No Parts for 2. |  | Each Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R2. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000
Inactive | FAC | FAC-002 | FAC-002-3 | 3. | Each Transmission Owner and each Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Each Transmission Owner and each Distribution Provider shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 |  | DP | [17 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-3 | No Parts for 3. |  | Each Transmission Owner and each Distribution Provider shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R3. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000
Inactive | FAC | FAC-002 | FAC-002-3 | 4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Each Transmission Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 | [19 empty] | TO
Inactive | FAC | FAC-002 | FAC-002-3 | No Parts for 4. |  | Each Transmission Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R4. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000
Inactive | FAC | FAC-002 | FAC-002-3 | 5. | R5. Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Each applicable Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R5. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000 |  |  |  |  | GO
Inactive | FAC | FAC-002 | FAC-002-3 | No Parts for 5. |  | Each applicable Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R5. | Long-Term Planning | 2020-02-06 | 2020-02-21 | 2020-10-30 | 2020-10-30 | 2021-04-01 |  |  |  |  | 2023-12-31 | Filing/Order Docket No. RD20-4-000
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 1.1. | The reliability impact of the new interconnection, or existing interconnection seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, on affected system(s); | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 | 2024-01-01 | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 2. | Each Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M2. Each Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R2. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | No Parts for 2. |  | M2. Each Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R2. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 3. | Each Transmission Owner and each Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M3. Each Transmission Owner and each Distribution Provider shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R3. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  | DP | [17 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | No Parts for 3. |  | M3. Each Transmission Owner and each Distribution Provider shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R3. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | M4. Each Transmission Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R4. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | No Parts for 4. |  | M4. Each Transmission Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R4. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4 | M5. Each applicable Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R5. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | No Parts for 5. |  | M5. Each applicable Generator Owner shall have evidence (such as documents containing the data provided in response to the requests of the Transmission Planner or Planning Coordinator) that it met all requirements in Requirement R5. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | 6. | Each Planning Coordinator shall maintain a publicly available definition of qualified change for the purposes of facility interconnection. | M6. Each Planning Coordinator shall have evidence that it has maintained a publicly available definition of qualified change. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information | [10 empty] | PA | PC
Mandatory Subject to Enforcement | FAC | FAC-002 | FAC-002-4 | No Parts for 6. |  | M6. Each Planning Coordinator shall have evidence that it has maintained a publicly available definition of qualified change. | Long-Term Planning | 2022-05-12 | 2022-06-14 | 2022-11-17 | 2022-11-17 | 2024-01-01 |  | X |  |  |  | Filing/Order Docket No. RD22-5-000 See Implementation Plan for additional compliance information
Inactive | FAC | FAC-003 | FAC-003-0 | 1. | Each Transmission Owner shall have a vegetation management program to prevent transmission line contact with vegetation. The vegetation management program shall include the following three elements: |  |  | 2005-02-08 | [8 empty] | 2006-04-07 | Replaced with FAC-003-1 (FAC-003-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-0 | 1.1. | Inspection requirements. |  |  | 2005-02-08 | [8 empty] | 2006-04-07 | Replaced with FAC-003-1 (FAC-003-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-0 | 1.2. | Trimming clearances. |  |  | 2005-02-08 | [8 empty] | 2006-04-07 | Replaced with FAC-003-1 (FAC-003-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-0 | 1.3. | Annual work plan. |  |  | 2005-02-08 | [8 empty] | 2006-04-07 | Replaced with FAC-003-1 (FAC-003-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-0 | 2. | Each Transmission Owner shall report to its Regional Reliability Organization all vegetationrelated outages on transmission circuits 200 kV and higher and any other lower voltage lines designated by the Regional Reliability Organization to be critical to the reliability of the electric system. |  |  | 2005-02-08 | [8 empty] | 2006-04-07 | Replaced with FAC-003-1 (FAC-003-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-04-07 | Replaced with FAC-003-1 (FAC-003-0 was never enforceable)
Inactive | FAC | FAC-003 | FAC-003-1 | 1. | The Transmission owner shall prepare, and keep current, a formal transmission vegetation management (TVMP). The TVMP shall include the Transmission Owner's objectives, practices, approved procedures, and work specifications. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.1. | The TVMP shall define a schedule for and the type (aerial, ground) of ROW vegetation inspections. This schedule should be flexible enough to adjust for changing conditions. The inspection schedule shall be based on the anticipated growth of vegetation and any other environmental or operational factors that could impact the relationship of vegetation to the Transmission Owner’s transmission lines. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.2. | The Transmission Owner, in the TVMP, shall identify and document clearances between vegetation and any overhead, ungrounded supply conductors, taking into consideration transmission line voltage, the effects of ambient temperature on conductor sag under maximum design loading, and the effects of wind velocities on conductor sway. Specifically, the Transmission Owner shall establish clearances to be achieved at the time of vegetation management work identified herein as Clearance 1, and shall also establish and maintain a set of clearances identified herein as Clearance 2 to prevent flashover between vegetation and overhead ungrounded supply conductors. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.2.1. | Clearance 1 — The Transmission Owner shall determine and document appropriate clearance distances to be achieved at the time of transmission vegetation management work based upon local conditions and the expected time frame in which the Transmission Owner plans to return for future vegetation management work. Local conditions may include, but are not limited to: operating voltage, appropriate vegetation management techniques, fire risk, reasonably anticipated tree and conductor movement, species types and growth rates, species failure characteristics, local climate and rainfall patterns, line terrain and elevation, location of the vegetation within the span, and worker approach distance requirements. Clearance 1 distances shall be greater than those defined by Clearance 2 below. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.2.2. | Clearance 2 — The Transmission Owner shall determine and document specific radial clearances to be maintained between vegetation and conductors under all rated electrical operating conditions. These minimum clearance distances are necessary to prevent flashover between vegetation and conductors and will vary due to such factors as altitude and operating voltage. These Transmission Owner-specific minimum clearance distances shall be no less than those set forth in the Institute of Electrical and Electronics Engineers (IEEE) Standard 516-2003 (Guide for Maintenance Methods on Energized Power Lines) and as specified in its Section 4.2.2.3, Minimum Air Insulation Distances without Tools in the Air Gap. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.2.2.1. | Where transmission system transient overvoltage factors are not known, clearances shall be derived from Table 5, IEEE 516-2003, phase-to-ground distances, with appropriate altitude correction factors applied. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.2.2.2. | Where transmission system transient overvoltage factors are known, clearances shall be derived from Table 7, IEEE 516-2003, phase-to-phase voltages, with appropriate altitude correction factors applied. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.3. | All personnel directly involved in the design and implementation of the TVMP shall hold appropriate qualifications and training, as defined by the Transmission Owner, to perform their duties. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.4. | Each Transmission Owner shall develop mitigation measures to achieve sufficient clearances for the protection of the transmission facilities when it identifies locations on the ROW where the Transmission Owner is restricted from attaining the clearances specified in Requirement 1.2.1. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 1.5. | Each Transmission Owner shall establish and document a process for the immediate communication of vegetation conditions that present an imminent threat of a transmission line outage. This is so that action (temporary reduction in line rating, switching line out of service, etc.) may be taken until the threat is relieved. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 2. | The Transmission Owner shall create and implement an annual plan for vegetation management work to ensure the reliability of the system. The plan shall describe the methods used, such as manual clearing, mechanical clearing, herbicide treatment, or other actions. The plan should be flexible enough to adjust to changing conditions, taking into consideration anticipated growth of vegetation and all other environmental factors that may have an impact on the reliability of the transmission systems. Adjustments to the plan shall be documented as they occur. The plan should take into consideration the time required to obtain permissions or permits from landowners or regulatory authorities. Each Transmission Owner shall have systems and procedures for documenting and tracking the planned vegetation management work and ensuring that the vegetation management work was completed according to work specifications. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-003 | FAC-003-1 | 3. | The Transmission Owner shall report quarterly to its RRO, or the RRO’s designee, sustained transmission line outages determined by the Transmission Owner to have been caused by vegetation. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.1. | Multiple sustained outages on an individual line, if caused by the same vegetation, shall be reported as one outage regardless of the actual number of outages within a 24-hour period. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.2. | The Transmission Owner is not required to report to the RRO, or the RRO’s designee, certain sustained transmission line outages caused by vegetation: (1) Vegetationrelated outages that result from vegetation falling into lines from outside the ROW that result from natural disasters shall not be considered reportable (examples of disasters that could create non-reportable outages include, but are not limited to, earthquakes, fires, tornados, hurricanes, landslides, wind shear, major storms as defined either by the Transmission Owner or an applicable regulatory body, ice storms, and floods), and (2) Vegetation-related outages due to human or animal activity shall not be considered reportable (examples of human or animal activity that could cause a non-reportable outage include, but are not limited to, logging, animal severing tree, vehicle contact with tree, arboricultural activities or horticultural or agricultural activities, or removal or digging of vegetation). |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.3. | The outage information provided by the Transmission Owner to the RRO, or the RRO’s designee, shall include at a minimum: the name of the circuit(s) outaged, the date, time and duration of the outage; a description of the cause of the outage; other pertinent comments; and any countermeasures taken by the Transmission Owner. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.4. | An outage shall be categorized as one of the following: |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.4.1. | Category 1 — Grow-ins: Outages caused by vegetation growing into lines from vegetation inside and/or outside of the ROW; |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.4.2. | Category 2 — Fall-ins: Outages caused by vegetation falling into lines from inside the ROW; |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 3.4.3. | Category 3 — Fall-ins: Outages caused by vegetation falling into lines from outside the ROW. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-1 | 4. | The RRO shall report the outage information provided to it by Transmission Owner’s, as required by Requirement 3, quarterly to NERC, as well as any actions taken by the RRO as a result of any of the reported outages. |  | Real-Time Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000 | [16 empty] | RRO
Inactive | FAC | FAC-003 | FAC-003-1 | No Parts for 4. |  |  | Real-Time Operations | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-003 | FAC-003-2 | 1. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Realtime, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetationrelated Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | No Parts for 1. |  |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000
Inactive | FAC | FAC-003 | FAC-003-2 | 2. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | No Parts for 2. |  |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000
Inactive | FAC | FAC-003 | FAC-003-2 | 3. | Each Transmission Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | 3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | 3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | 4. | Each Transmission Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the Transmission Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | No Parts for 4. |  |  | Real-Time Operations | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000
Inactive | FAC | FAC-003 | FAC-003-2 | 5. | When a Transmission Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the Transmission Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. |  | Long-Term Planning | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | No Parts for 5. |  |  | Long-Term Planning | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000
Inactive | FAC | FAC-003 | FAC-003-2 | 6. | Each Transmission Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. |  | Long-Term Planning | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | No Parts for 6. |  |  | Long-Term Planning | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000
Inactive | FAC | FAC-003 | FAC-003-2 | 7. | Each Transmission Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include: Change in expected growth rate/environmental factors; Circumstances that are beyond the control of a Transmission Owner; Rescheduling work between growing seasons; Crew or contractor availability/Mutual assistance agreements; Identified unanticipated high priority work; Weather conditions/Accessibility; Permitting delays; Land ownership changes/Change in land use by the landowner; Emerging technologies |  | Long-Term Planning | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000 | [19 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-2 | No Parts for 7. |  |  | Long-Term Planning | 2011-11-03 | 2011-12-21 | 2013-03-21 | 2013-05-28 | [5 empty] | 2013-11-25 | Filing/Order Docket No. RM12-4-000
Inactive | FAC | FAC-003 | FAC-003-3 | 1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | No Parts for 1. |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-003 | FAC-003-3 | 2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R2) | Real-Time Operations | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | No Parts for 2. |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R2) | Real-Time Operations | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-003 | FAC-003-3 | 3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: [See Standard pdf for further information] |  | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | 3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 | 2013-11-25 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | 3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | Long-Term Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 | 2013-11-25 |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | 4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | M4. Each applicable Transmission Owner and applicable Generator Owner that has a confirmed vegetation condition likely to cause a Fault at any moment will have evidence that it notified the control center holding switching authority for the associated transmission line without any intentional time delay. Examples of evidence may include control center logs, voice recordings, switching orders, clearance orders and subsequent work orders. | Real-Time Operations | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | No Parts for 4. |  | M4. Each applicable Transmission Owner and applicable Generator Owner that has a confirmed vegetation condition likely to cause a Fault at any moment will have evidence that it notified the control center holding switching authority for the associated transmission line without any intentional time delay. Examples of evidence may include control center logs, voice recordings, switching orders, clearance orders and subsequent work orders. | Real-Time Operations | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-003 | FAC-003-3 | 5. | When a applicable Transmission Owner and applicable Generator Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | M5. Each applicable Transmission Owner and applicable Generator Owner has evidence of the corrective action taken for each constraint where an applicable transmission line was put at potential risk. Examples of acceptable forms of evidence may include initially-planned work orders, documentation of constraints from landowners, court orders, inspection records of increased monitoring, documentation of the de-rating of lines, revised work orders, invoices, or evidence that the line was de-energized. | Operations Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | No Parts for 5. |  | M5. Each applicable Transmission Owner and applicable Generator Owner has evidence of the corrective action taken for each constraint where an applicable transmission line was put at potential risk. Examples of acceptable forms of evidence may include initially-planned work orders, documentation of constraints from landowners, court orders, inspection records of increased monitoring, documentation of the de-rating of lines, revised work orders, invoices, or evidence that the line was de-energized. | Operations Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-003 | FAC-003-3 | 6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | M6. Each applicable Transmission Owner and applicable Generator Owner has evidence that it conducted Vegetation Inspections of the transmission line ROW for all applicable lines at least once per calendar year but with no more than 18 calendar months between inspections on the same ROW. Examples of acceptable forms of evidence may include completed and dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | No Parts for 6. |  | M6. Each applicable Transmission Owner and applicable Generator Owner has evidence that it conducted Vegetation Inspections of the transmission line ROW for all applicable lines at least once per calendar year but with no more than 18 calendar months between inspections on the same ROW. Examples of acceptable forms of evidence may include completed and dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-003 | FAC-003-3 | 7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include: • Change in expected growth rate/ environmental factors • Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner • Rescheduling work between growing seasons • Crew or contractor availability/ Mutual assistance agreements • Identified unanticipated high priority work • Weather conditions/Accessibility • Permitting delays • Land ownership changes/Change in land use by the landowner • Emerging technologies | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-3 | No Parts for 7. |  | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2012-05-09 | 2012-07-30 | 2013-09-19 | 2013-11-25 | 2014-07-01 |  |  |  |  | 2016-09-30 | Filing/Order Docket No. RM12-16-000
Inactive | FAC | FAC-003 | FAC-003-4 | 1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: (Footnote: This requirement does not apply to circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner subject to this reliability standard, including natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, wind shear, fresh gale, major storms as defined either by the applicable Transmission Owner or applicable Generator Owner or an applicable regulatory body, ice storms, and floods; human or animal activity such as logging, animal severing tree, vehicle contact with tree, or installation, removal, or digging of vegetation. Nothing in this footnote should be construed to limit the Transmission Owner’s or applicable Generator Owner’s right to exercise its full legal rights on the ROW.) | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 1.1. | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, (Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real-time observation.) | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 1.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, (Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period.) | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: Footnote: This requirement does not apply to circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner subject to this reliability standard, including natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, wind shear, fresh gale, major storms as defined either by the applicable Transmission Owner or applicable Generator Owner or an applicable regulatory body, ice storms, and floods; human or animal activity such as logging, animal severing tree, vehicle contact with tree, or installation, removal, or digging of vegetation. Nothing in this footnote should be construed to limit the Transmission Owner’s or applicable Generator Owner’s right to exercise its full legal rights on the ROW. | M2. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 2.1. | An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real-time observation. | M2. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 2.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. | M2. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 2.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. | M2. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 2.4. | An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. | M2. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | M3. The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. | Long-Term Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | M3. The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. | Long-Term Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | M3. The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. | Long-Term Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | M4. Each applicable Transmission Owner and applicable Generator Owner that has a confirmed vegetation condition likely to cause a Fault at any moment will have evidence that it notified the control center holding switching authority for the associated transmission line without any intentional time delay. Examples of evidence may include control center logs, voice recordings, switching orders, clearance orders and subsequent work orders. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | No Parts for 4. |  | M4. Each applicable Transmission Owner and applicable Generator Owner that has a confirmed vegetation condition likely to cause a Fault at any moment will have evidence that it notified the control center holding switching authority for the associated transmission line without any intentional time delay. Examples of evidence may include control center logs, voice recordings, switching orders, clearance orders and subsequent work orders. | Real-Time Operations | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000
Inactive | FAC | FAC-003 | FAC-003-4 | 5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | M5. Each applicable Transmission Owner and applicable Generator Owner has evidence of the corrective action taken for each constraint where an applicable transmission line was put at potential risk. Examples of acceptable forms of evidence may include initially-planned work orders, documentation of constraints from landowners, court orders, inspection records of increased monitoring, documentation of the de-rating of lines, revised work orders, invoices, or evidence that the line was de-energized. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | No Parts for 5. |  | M5. Each applicable Transmission Owner and applicable Generator Owner has evidence of the corrective action taken for each constraint where an applicable transmission line was put at potential risk. Examples of acceptable forms of evidence may include initially-planned work orders, documentation of constraints from landowners, court orders, inspection records of increased monitoring, documentation of the de-rating of lines, revised work orders, invoices, or evidence that the line was de-energized. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000
Inactive | FAC | FAC-003 | FAC-003-4 | 6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW (Footnote: When the applicable Transmission Owner or applicable Generator Owner is prevented from performing a Vegetation Inspection within the timeframe in R6 due to a natural disaster, the TO or GO is granted a time extension that is equivalent to the duration of the time the TO or GO was prevented from performing the Vegetation Inspection.) | M6. Each applicable Transmission Owner and applicable Generator Owner has evidence that it conducted Vegetation Inspections of the transmission line ROW for all applicable lines at least once per calendar year but with no more than 18 calendar months between inspections on the same ROW. Examples of acceptable forms of evidence may include completed and dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | No Parts for 6. |  | M6. Each applicable Transmission Owner and applicable Generator Owner has evidence that it conducted Vegetation Inspections of the transmission line ROW for all applicable lines at least once per calendar year but with no more than 18 calendar months between inspections on the same ROW. Examples of acceptable forms of evidence may include completed and dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000
Inactive | FAC | FAC-003 | FAC-003-4 | 7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.1. | Change in expected growth rate/environmental factors | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-10-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner Footnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.3. | Rescheduling work between growing seasons | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.4. | Crew or contractor availability/Mutual assistance agreements | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.5. | Identified unanticipated high priority work | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.6. | Weather conditions/Accessibility | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.7. | Permitting delays | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.8. | Land ownership changes/Change in land use by the landowner | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-003 | FAC-003-4 | 7.9. | Emerging technologies | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | Operations Planning | 2016-02-11 | 2016-03-14 | 2016-04-26 | 2016-04-26 | 2016-10-01 | 2016-04-26 |  |  |  | 2024-03-31 | Filing/Order Docket No. RD16-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s), operating within their Rating and all Rated Electrical Operating Conditions of the types shown below. Footnote: This requirement does not apply to circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner subject to this Reliability Standard, including natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, wind shear, fresh gale, major storms as defined either by the applicable Transmission Owner or applicable Generator Owner or an applicable regulatory body, ice storms, and floods; human or animal activity such as logging, animal severing tree, vehicle contact with tree, or installation, removal, or digging of vegetation. Nothing in this footnote should be construed to limit the Transmission Owner’s or applicable Generator Owner’s right to exercise its full legal rights on the ROW. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 1.1. | An encroachment into the MVCD as shown in FAC‐003‐Table 2, observed in Real‐ time, absent a Sustained Outage, Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real‐time observation. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 1.2. | An encroachment due to a fall‐in from inside the ROW that caused a vegetation‐ related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation‐related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation‐related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. | M1. Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 2. | Reserved for future use. | Reserved for future use. |  | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | No Parts for 2. |  | Reserved for future use. |  | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | M3. The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | M3. The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 3.2. | Inter‐relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | M3. The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | M4. Each applicable Transmission Owner and applicable Generator Owner that has a confirmed vegetation condition likely to cause a Fault at any moment will have evidence that it notified the control center holding switching authority for the associated transmission line without any intentional time delay. Examples of evidence may include control center logs, voice recordings, switching orders, clearance orders and subsequent work orders. (R4) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | No Parts for 4. |  | M4. Each applicable Transmission Owner and applicable Generator Owner that has a confirmed vegetation condition likely to cause a Fault at any moment will have evidence that it notified the control center holding switching authority for the associated transmission line without any intentional time delay. Examples of evidence may include control center logs, voice recordings, switching orders, clearance orders and subsequent work orders. (R4) | Real-Time Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | M5. Each applicable Transmission Owner and applicable Generator Owner has evidence of the corrective action taken for each constraint where an applicable transmission line was put at potential risk. Examples of acceptable forms of evidence may include initially‐planned work orders, documentation of constraints from landowners, court orders, inspection records of increased monitoring, documentation of the de‐rating of lines, revised work orders, invoices, or evidence that the line was de‐energized. (R5) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | No Parts for 5. |  | M5. Each applicable Transmission Owner and applicable Generator Owner has evidence of the corrective action taken for each constraint where an applicable transmission line was put at potential risk. Examples of acceptable forms of evidence may include initially‐planned work orders, documentation of constraints from landowners, court orders, inspection records of increased monitoring, documentation of the de‐rating of lines, revised work orders, invoices, or evidence that the line was de‐energized. (R5) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. Footnote: When the applicable Transmission Owner or applicable Generator Owner is prevented from performing a Vegetation Inspection within the timeframe in R6 due to a natural disaster, the TO or GO is granted a time extension that is equivalent to the duration of the time the TO or GO was prevented from performing the Vegetation Inspection. | M6. Each applicable Transmission Owner and applicable Generator Owner has evidence that it conducted Vegetation Inspections of the transmission line ROW for all applicable lines at least once per calendar year but with no more than 18 calendar months between inspections on the same ROW. Examples of acceptable forms of evidence may include completed and dated work orders, dated invoices, or dated inspection records. (R6) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | No Parts for 6. |  | M6. Each applicable Transmission Owner and applicable Generator Owner has evidence that it conducted Vegetation Inspections of the transmission line ROW for all applicable lines at least once per calendar year but with no more than 18 calendar months between inspections on the same ROW. Examples of acceptable forms of evidence may include completed and dated work orders, dated invoices, or dated inspection records. (R6) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include: | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.1. | Change in expected growth rate/environmental factors | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner Footnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.3. | Rescheduling work between growing seasons | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.4. | Crew or contractor availability/Mutual assistance agreements | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.5. | Identified unanticipated high priority work | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.6. | Weather conditions/Accessibility | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.7. | Permitting delays | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.8. | Land ownership changes/Change in land use by the landowner | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003 | FAC-003-5 | 7.9. | Emerging technologies | M7. Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1. | The Transmission Owner and Generator Owner shall each document the methodology(ies) used to determine its electrical equipment and Facility Ratings. Further, the methodology(ies) shall comply with applicable Regional Reliability Organization requirements. The documentation shall address and include |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1. | The methodology(ies) used to determine equipment and Facility Rating of the items listed for both normal and emergency conditions: |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.1. | Transmission circuits. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.2. | Transformers. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.3. | Series and shunt reactive elements |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.4. | Terminal equipment (e.g., switches, breakers, current transformers, etc) |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.5. | VAR compensators. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.6. | High voltage direct current converters. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.1.7. | Any other device listed as a Limiting Element |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.2. | The Rating of a facility shall not exceed the Rating(s) of the most Limiting Element(s) in the circuit, including terminal connections and associated equipment. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.3. | In cases where protection systems and control settings constitute a loading limit on a facility, this limit shall become the Rating for that facility. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.4. | Ratings of jointly-owned and jointly-operated facilities shall be coordinated among the joint owners and joint operators resulting in a single set of Ratings. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 1.5. | The documentation shall identify the assumptions used to determine each of the equipment and Facility Ratings, including references to industry Rating practices and standards (e.g., ANSI, IEEE, etc.). Seasonal Ratings and variations in assumptions shall be included. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | 2. | The Transmission Owner and Generator Owner shall provide documentation of the methodology(ies) used to determine its transmission equipment and Facility Ratings to the Regional Reliability Organization(s) and NERC on request (30 calendar days). |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-004 | FAC-004-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with FAC-008-1 and FAC-009-1 (FAC-004-0 was never enforceable)
Inactive | FAC | FAC-005 | FAC-005-0 | 1. | The transmission Owner, and Generator Owner shall each have on file or be able to readily provide, a document or database identifying the Normal and Emergency Ratings of all of its transmission facilities (e.g., lines, transformers, terminal equipment, and storage devices) that are part of the interconnected transmission systems. Seasonal variations in Ratings shall be included as appropriate. |  |  | 2005-02-08 | [8 empty] | 2006-10-07 | Replaced with FAC-008-1 and FAC-009-1 (FAC-005-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-005 | FAC-005-0 | 1.1. | The Ratings shall be consistent with the entity’s methodology(ies) for determining Facility Ratings and shall be updated as facility changes occur. |  |  | 2005-02-08 | [8 empty] | 2006-10-07 | Replaced with FAC-008-1 and FAC-009-1 (FAC-005-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-005 | FAC-005-0 | 2. | The Transmission Owner and Generator Owner shall provide the Normal and Emergency Facility Ratings of all its transmission facilities to the Regional Reliability Organization(s) and NERC on request (30 calendar days). |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-10-07 | Replaced with FAC-008-1 and FAC-009-1 (FAC-005-0 was never enforceable) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-005 | FAC-005-0 | No Parts for 2. |  |  | Long-Term Planning | 2005-02-08 | [8 empty] | 2006-10-07 | Replaced with FAC-008-1 and FAC-009-1 (FAC-005-0 was never enforceable)
Inactive | FAC | FAC-008 | FAC-008-1 | 1. | The Transmission Owner and Generator Owner shall each document its current methodology used for developing Facility Ratings (Facility Ratings Methodology) of its solely and jointly owned Facilities. The methodology shall include all of the following: |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.1. | A statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.2. | The method by which the Rating (of major BES equipment that comprises a Facility) is determined. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.2.1. | The scope of equipment addressed shall include, but not be limited to, generators, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.2.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.3. | Consideration of the following: |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.3.1. | Ratings provided by equipment manufacturers. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.3.2. | Design criteria (e.g., including applicable references to industry Rating practices such as manufacturer’s warranty, IEEE, ANSI or other standards). |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.3.3. | Ambient conditions. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.3.4. | Operating limitations. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 1.3.5. | Other assumptions. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | 2. | The Transmission Owner and Generator Owner shall each make its Facility Ratings Methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners, and Planning Authorities that have responsibility for the area in which the associated Facilities are located, within 15 business days of receipt of a request. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | No Parts for 2. |  |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-008 | FAC-008-1 | 3. | If a Reliability Coordinator, Transmission Operator, Transmission Planner, or Planning Authority provides written comments on its technical review of a Transmission Owner’s or Generator Owner’s Facility Ratings Methodology, the Transmission Owner or Generator Owner shall provide a written response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings Methodology and, if no change will be made to that Facility Ratings Methodology, the reason why. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-1 | No Parts for 3. |  |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-008 | FAC-008-2 | 1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [See standard for methodology requirements] |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.2.4. | Operating limitations. Note: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-2 | 3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [See standard for methodology requirements] |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.2.4. | Operating limitations. Note: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | 4. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | No Parts for 4. |  |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction)
Inactive | FAC | FAC-008 | FAC-008-2 | 5. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | No Parts for 5. |  |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction)
Inactive | FAC | FAC-008 | FAC-008-2 | 6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | No Parts for 6. |  |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction)
Inactive | FAC | FAC-008 | FAC-008-2 | 7. | Each Transmission Owner and Generator Owner shall provide Facility Ratings for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction) |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-2 | No Parts for 7. |  |  | Long-Term Planning | 2010-05-12 | [8 empty] | 2011-05-24 | Replaced by FAC-008-3 (FAC-008-2 was not enforceable in any jurisdiction)
Inactive | FAC | FAC-008 | FAC-008-3 | 1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] | M1. Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | M1. Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M1. Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [See standard for methodology requirements] | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.2.1. | Equipment Rating standard(s) used in development of this methodology. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.2.4. | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | 3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [See standard for methodology requirements] | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.2.1. | Equipment Rating standard(s) used in development of this methodology. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.2.4. | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.4.1. DO NOT USE | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 4. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. | M4. Each Transmission Owner shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it made its Facility Ratings methodology available for inspection within 21 calendar days of a request in accordance with Requirement 4. The Generator Owner shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it made its documentation for determining its Facility Ratings or its Facility Ratings methodology available for inspection within 21 calendar days of a request in accordance with Requirement R4. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | No Parts for 4. |  | M4. Each Transmission Owner shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it made its Facility Ratings methodology available for inspection within 21 calendar days of a request in accordance with Requirement 4. The Generator Owner shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it made its documentation for determining its Facility Ratings or its Facility Ratings methodology available for inspection within 21 calendar days of a request in accordance with Requirement R4. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000
Inactive | FAC | FAC-008 | FAC-008-3 | 5. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. | M5. If the Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s or Generator Owner’s Facility Ratings methodology or a Generator Owner’s documentation for determining its Facility Ratings, the Transmission Owner or Generator Owner shall have evidence, (such as a copy of a dated electronic or hard copy note, or other comparable evidence from the Transmission Owner or Generator Owner addressed to the commenter that includes the response to the comment,) that it provided a response to that commenting entity in accordance with Requirement R5. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | No Parts for 5. |  | M5. If the Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s or Generator Owner’s Facility Ratings methodology or a Generator Owner’s documentation for determining its Facility Ratings, the Transmission Owner or Generator Owner shall have evidence, (such as a copy of a dated electronic or hard copy note, or other comparable evidence from the Transmission Owner or Generator Owner addressed to the commenter that includes the response to the comment,) that it provided a response to that commenting entity in accordance with Requirement R5. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000
Inactive | FAC | FAC-008 | FAC-008-3 | 6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | M6. Each Transmission Owner and Generator Owner shall have evidence to show that its Facility Ratings are consistent with the documentation for determining its Facility Ratings as specified in Requirement R1 or consistent with its Facility Ratings methodology as specified in Requirements R2 and R3 (Requirement R6). | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | No Parts for 6. |  | M6. Each Transmission Owner and Generator Owner shall have evidence to show that its Facility Ratings are consistent with the documentation for determining its Facility Ratings as specified in Requirement R1 or consistent with its Facility Ratings methodology as specified in Requirements R2 and R3 (Requirement R6). | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000
Inactive | FAC | FAC-008 | FAC-008-3 | 7. | Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | M7. Each Generator Owner shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R7. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-3 | No Parts for 7. |  | M7. Each Generator Owner shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R7. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000
Inactive | FAC | FAC-008 | FAC-008-3 | 8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [See standard for requirements of providing requested information] | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 |  |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 8.1. | As scheduled by the requesting entities: | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 8.1.1. | Facility Ratings | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 8.1.2. | Identity of the most limiting equipment of the Facilities | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2011-11-17 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 8.2.1. | Identity of the existing next most limiting equipment of the Facility | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-3 | 8.2.2. | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2011-05-24 | 2011-06-15 | 2011-11-17 | 2011-11-17 | 2013-01-01 | 2013-01-01 |  |  |  | 2021-09-30 | Filing/Order Docket No. RM11-28-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | M1. Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | M1. Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M1. Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.2.1. | Equipment Rating standard(s) used in development of this methodology. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.2.4. | Operating limitations. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO
Inactive | FAC | FAC-008 | FAC-008-4 | 3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.2.1. | Equipment Rating standard(s) used in development of this methodology. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.2.4. | Operating limitations. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 | [19 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | 4. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | No Parts for 4. |  | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | 5. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | No Parts for 5. |  | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | 6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | M6. Each Transmission Owner and Generator Owner shall have evidence to show that its Facility Ratings are consistent with the documentation for determining its Facility Ratings as specified in Requirement R1 or consistent with its Facility Ratings methodology as specified in Requirements R2 and R3 (Requirement R6). | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-008 | FAC-008-4 | No Parts for 6. |  | M6. Each Transmission Owner and Generator Owner shall have evidence to show that its Facility Ratings are consistent with the documentation for determining its Facility Ratings as specified in Requirement R1 or consistent with its Facility Ratings methodology as specified in Requirements R2 and R3 (Requirement R6). | Operations Planning | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | 7. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | No Parts for 7. |  | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | 8. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Inactive | FAC | FAC-008 | FAC-008-4 | No Parts for 8. |  | Reserved |  | 2019-05-09 | 2019-06-07 | [7 empty] | 2021-02-04 | Filing/Order Docket No. RM19-17-000 Withdrawn 2/4/2021 Replaced by FAC-008-5
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | M1.Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 1.1 | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | M1.Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 1.2 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M1.Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.2.1 | Equipment Rating standard(s) used in development of this methodology. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.2.2 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.2.3 | Ambient conditions (for particular or average conditions or as they vary in real-time). | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.2.4 | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.4.1 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 2.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | M2. Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.2.1. | Equipment Rating standard(s) used in development of this methodology. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | M3. Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | Long-Term Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 4. | Reserved. | Reserved. |  | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | No Parts for 4. |  | Reserved. |  | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 5. | Reserved. | Reserved. |  | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | No Parts for 5. |  | Reserved. |  | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | M6. Each Transmission Owner and Generator Owner shall have evidence to show that its Facility Ratings are consistent with the documentation for determining its Facility Ratings as specified in Requirement R1 or consistent with its Facility Ratings methodology as specified in Requirements R2 and R3 (Requirement R6). | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | No Parts for 6. |  | M6. Each Transmission Owner and Generator Owner shall have evidence to show that its Facility Ratings are consistent with the documentation for determining its Facility Ratings as specified in Requirement R1 or consistent with its Facility Ratings methodology as specified in Requirements R2 and R3 (Requirement R6). | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 7. | Reserved. | Reserved. |  | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | No Parts for 7. |  | Reserved. |  | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | [5 empty] | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8.1. | As scheduled by the requesting entities: | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8.1.1. | Facility Ratings | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8.1.2. | Identity of the most limiting equipment of the Facilities | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8.2.1. | Identity of the existing next most limiting equipment of the Facility | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008 | FAC-008-5 | 8.2.2. | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | M8. Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | Operations Planning | 2021-02-04 | 2021-02-19 | 2021-04-07 | 2021-04-07 | 2021-10-01 | 2021-10-01 |  |  |  |  | Filing/Order Docket No. RD21-4-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-009 | FAC-009-1 | 1. | The Transmission Owner and Generator Owner shall each establish Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-009 | FAC-009-1 | No Parts for 1. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-009 | FAC-009-1 | 2. | The Transmission Owner and Generator Owner shall each provide Facility Ratings for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities to its associated Reliability Coordinator(s), Planning Authority(ies), Transmission Planner(s), and Transmission Operator(s) as scheduled by such requesting entities. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000 |  |  |  |  | GO | [14 empty] | TO
Inactive | FAC | FAC-009 | FAC-009-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2012-12-31 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-010 | FAC-010-1 | 1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 1.1. | Be applicable for developing SOLs used in the planning horizon. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.2. | Following the single Contingencies (see footnote in standard) identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.3.2. | System reconfiguration through manual or automatic control or protection actions. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.3.3. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.4. | Starting with all facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.5. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 2.5.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-07-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3.2. | Selection of applicable Contingencies. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3.3. | Level of detail of system models used to determine SOLs. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | 5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-07-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | FAC | FAC-010 | FAC-010-2 | 1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 1.1. | Be applicable for developing SOLs used in the planning horizon. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.3.2. | System reconfiguration through manual or automatic control or protection actions. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3.2. | Selection of applicable Contingencies. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3.3. | Level of detail of system models used to determine SOLs. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | 5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2 | No Parts for 5. |  |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2010-04-18 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-010 | FAC-010-2.1 | 1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | M1. The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 1.1. | Be applicable for developing SOLs used in the planning horizon. | M1. The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. | M1. The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | M1. The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.3.2. | System reconfiguration through manual or automatic control or protection actions. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. | M2. The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3.2. | Selection of applicable Contingencies. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3.3. | Level of detail of system models used to determine SOLs. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | 5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-2.1 | No Parts for 5. |  |  |  | 2009-11-05 | 2009-11-20 | 2010-04-19 | 2010-04-19 | 2010-04-19 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD10-9-000
Inactive | FAC | FAC-010 | FAC-010-3 | 1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 1.1. | Be applicable for developing SOLs used in the planning horizon. | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.2. | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.3.2. | System reconfiguration through manual or automatic control or protection actions. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. | The Planning Authority shall have evidence it issued its SOL Methodology and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Planning Authority that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2017-04-01 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3.2. | Selection of applicable Contingencies |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3.3. | Level of detail of system models used to determine SOLs. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3.4. | Allowed uses of Remedial Action Schemes. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 |  | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-010 | FAC-010-3 | 4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2016-01-25 | 2016-01-25 | X |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-011 | FAC-011-1 | 1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 1.1. | Be applicable for developing SOLs used in the operations horizon. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.3.2. | Interruption of other network customers, only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or, if the real-time operating conditions are more adverse than anticipated in the corresponding studies, e.g., load greater than studied. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.3.3. | System reconfiguration through manual or automatic control or protection actions. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.2. | Selection of applicable Contingencies. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-10-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.4. | Level of detail of system models used to determine SOLs. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.5. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.6. | Anticipated transmission system configuration, generation dispatch and Load level. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | 5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Reliability Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2008-10-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | FAC | FAC-011 | FAC-011-2 | 1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 1.1. | Be applicable for developing SOLs used in the operations horizon. | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.3.2. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.3.3. | System reconfiguration through manual or automatic control or protection actions. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.2. | Selection of applicable Contingencies | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.4. | Level of detail of system models used to determine SOLs. | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.5. | Allowed uses of Special Protection Systems or Remedial Action Plans. | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.6. | Anticipated transmission system configuration, generation dispatch and Load level | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | M3. If the recipient of the SOL Methodology provides documented comments on its technical review of that SOL methodology, the Reliability Coordinator that distributed that SOL Methodology shall have evidence that it provided a written response to that commenter within 45 calendar days of receipt of those comments in accordance with Requirement 5. (Retirement approved by FERC effective January 21, 2014.) |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | 5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Reliability Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-2 | No Parts for 5. |  |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-011 | FAC-011-3 | 1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 1.1. | Be applicable for developing SOLs used in the operations horizon. | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 1.2. | State that SOLs shall not exceed associated Facility Ratings. | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs | M1. The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.2. | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.3.2. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.3.3. | System reconfiguration through manual or automatic control or protection actions. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | M2. The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.2. | Selection of applicable Contingencies |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.4. | Level of detail of system models used to determine SOLs. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.5. | Allowed uses of Remedial Action Schemes. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.6. | Anticipated transmission system configuration, generation dispatch and Load level |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2017-04-01 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Inactive | FAC | FAC-011 | FAC-011-3 | 4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  |  | 2014-11-13 | 2015-02-03 | 2015-11-19 | 2016-01-25 | 2017-04-01 | 2016-01-25 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-13-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 1. | Each Reliability Coordinator shall have a documented methodology for establishing SOLs (i.e., SOL methodology) within its Reliability Coordinator Area. | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | No Parts for 1. |  | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 2. | Each Reliability Coordinator shall include in its SOL methodology the method for Transmission Operators to determine which owner-provided Facility Ratings are to be used in operations such that the Transmission Operator and its Reliability Coordinator use common Facility Ratings. | M2. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology, that addresses the items listed in Requirement R2. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | No Parts for 2. |  | M2. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology, that addresses the items listed in Requirement R2. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 3. | Each Reliability Coordinator shall include in its SOL methodology the method for Transmission Operators to determine the System Voltage Limits to be used in operations. The method shall: | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 3.1. | Require that each BES bus/station have an associated System Voltage Limits, unless its SOL methodology specifically allows the exclusion of BES buses/stations from the requirement to have an associated System Voltage Limit; | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 3.2. | Require that System Voltage Limits respect voltage-based Facility Ratings; | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 3.3. | Require that System Voltage Limits are greater than or equal to in-service BES relay settings for undervoltage load shedding systems and Undervoltage Load Shedding Programs; | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 3.4. | Identify the minimum allowable System Voltage Limit; | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 3.5. | Define the method for determining common System Voltage Limits between the Reliability Coordinator and its Transmission Operators, between adjacent Transmission Operators, and between adjacent Reliability Coordinators within an Interconnection. | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4. | Each Reliability Coordinator shall include in its SOL methodology the method for determining the stability limits to be used in operations. The method shall: | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.1. | Specify stability performance criteria, including any margins applied. The criteria shall, at a minimum, include the following: | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.1.1. | steady-state voltage stability; | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.1.2. | transient voltage response; | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.1.3. | angular stability; and | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.1.4. | System damping. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.2. | Require that stability limits are established to meet the criteria specified in Part 4.1 for the Contingencies identified in Requirement R5 applicable to the establishment of stability limits that are expected to produce more severe System impacts on its portion of the BES. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.3. | Describe how the Reliability Coordinator establishes stability limits when there is an impact to more than one Transmission Operator in its Reliability Coordinator Area or other Reliability Coordinator Areas. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.4. | Describe how stability limits are determined, considering levels of transfers, Load and generation dispatch, and System conditions including any changes to System topology such as Facility outages. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.5. | Describe the level of detail that is required for the study model(s), including the portion modeled of the Reliability Coordinator Area, and the critical modeling details from other Reliability Coordinator Areas, necessary to determine different types of stability limits. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.6. | Describe the allowed uses of Remedial Action Schemes and other automatic post-Contingency mitigation actions in establishing stability limits used in operations. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 4.7. | State that the use of underfrequency load shedding (UFLS) programs and Undervoltage Load Shedding (UVLS) Programs are not allowed in the establishment of stability limits. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 5. | Each Reliability Coordinator shall identify in its SOL methodology the set of Contingency events for use in determining stability limits and the set of Contingency events for use in performing Operational Planning Analysis (OPAs) and Real-time Assessments (RTAs). The SOL methodology for each set shall: | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 5.1. | Specify the following single Contingency events | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 5.1.1. | Loss of any of the following either by single phase to ground or three phase Fault (whichever is more severe) with Normal Clearing, or without a Fault: • generator; • transmission circuit; • transformer; • shunt device; or • single pole block in a monopolar or bipolar high voltage direct current system | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 5.2. | Specify additional single or multiple Contingency events or types of Contingency events, if any. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 5.3. | Describe the method(s) for identifying which, if any, of the Contingency events provided by the Planning Coordinator or Transmission Planner in accordance with FAC-014-3, Requirement R7, to use in determining stability limits. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6. | Each Reliability Coordinator shall include the following performance framework in its SOL methodology to determine SOL exceedances when performing Real-time monitoring, Real-time Assessments, and Operational Planning Analyses: | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.1. | System performance for no Contingencies demonstrates the following: | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.1.1. | Steady state flow through Facilities are within Normal Ratings; however, Emergency Ratings may be used when System adjustments to return the flow within its Normal Rating could be executed and completed within the specified time duration of those Emergency Ratings. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.1.2. | Steady state voltages are within normal System Voltage Limits; however, emergency System Voltage Limits may be used when System adjustments to return the voltage within its normal System Voltage Limits could be executed and completed within the specified time duration of those emergency System Voltage Limits. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.1.3. | Predetermined stability limits are not exceeded. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.1.4. | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.2. | System performance for the single Contingencies listed in Part 5.1 demonstrates the following: | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.2.1. | Steady state post-Contingency flow through Facilities within applicable Emergency Ratings. Steady state post-Contingency flow through a Facility must not be above the Facility’s highest Emergency Rating. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.2.2. | Steady state post-Contingency voltages are within emergency System Voltage Limits. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.2.3. | The stability performance criteria defined in the Reliability Coordinator’s SOL methodology are met. Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.2.4. | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.3. | System performance for applicable Contingencies identified in Part 5.2 demonstrates that: instability, Cascading, or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 6.4. | In determining the System’s response to any Contingency identified in Requirement R5, planned manual load shedding is acceptable only after all other available System adjustments have been made. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7. | Each Reliability Coordinator shall include in its SOL methodology a risk-based approach for determining how SOL exceedances identified as part of Real-time monitoring and Real-time Assessments must be communicated and if so, the timeframe that communication must occur. The approach shall include: | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.1. | A requirement that the following SOL exceedances will always be communicated, within a timeframe identified by the Reliability Coordinator. | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.1.1. | IROL exceedances; | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.1.2. | SOL exceedances of stability limits; | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.1.3. | Post Contingency SOL exceedances that are identified to have a validated risk of instability, Cascading, and uncontrolled separation; | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.1.4. | Pre-Contingency SOL exceedances of Facility Ratings; and | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.1.5. | Pre-Contingency SOL exceedances of normal minimum System Voltage Limits. | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.2. | A requirement that the following SOL exceedances must be communicated, if not resolved within 30 minutes, within a timeframe identified by the Reliability Coordinator. | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.2.1. | Post-Contingency SOL exceedances of Facility Ratings and emergency System Voltage Limits, and | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 7.2.2. | Pre-Contingency SOL exceedances of normal maximum System Voltage Limits. | M7. Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 8. | Each Reliability Coordinator shall include in its SOL methodology: | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R8. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 8.1. | A description of how to identify the subset of SOLs that qualify as Interconnection Reliability Operating Limits (IROLs). | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R8. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 8.2. | Criteria for determining when exceeding a SOL qualifies as exceeding an IROL and criteria for developing any associated IROL Tv. | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R8. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9. | Each Reliability Coordinator shall provide its SOL methodology to: | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9.1. | Each Reliability Coordinator that requests and indicates it has a reliability-related need within 30 days of a request. | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9.2. | Each of the following entities prior to the effective date of the SOL methodology: | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9.2.1. | Each adjacent Reliability Coordinator within the same; Interconnection; | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9.2.2. | Each Planning Coordinator and Transmission Planner that is responsible for planning any portion of the Reliability Coordinator Area; | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9.2.3. | Each Transmission Operator within its Reliability Coordinator Area; and | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | FAC | FAC-011 | FAC-011-4 | 9.2.4. | Each Reliability Coordinator that has requested to receive updates and indicated it had a reliability-related need. | M9. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1. | The Reliability Coordinator and Planning Authority shall each document its current methodology used for developing its inter-regional and intra-regional Transfer Capabilities (Transfer Capability Methodology). The Transfer Capability Methodology shall include all of the following: |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.1. | A statement that Transfer Capabilities shall respect all applicable System Operating Limits (SOLs). |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.2. | A definition stating whether the methodology is applicable to the planning horizon or the operating horizon. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.3. | A description of how each of the following is addressed, including any reliability margins applied to reflect uncertainty with projected BES conditions: |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.3.1. | Transmission system topology |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.3.2. | System demand |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.3.3. | Generation dispatch |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 1.3.4. | Current and projected transmission uses |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 2. | The Reliability Coordinator shall issue its Transfer Capability Methodology, and any changes to that methodology, prior to the effectiveness of such changes, to all of the following: |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 2.1. | Each Adjacent Reliability Coordinator and each Reliability Coordinator that indicated a reliability-related need for the methodology. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 2.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 2.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | FAC | FAC-012 | FAC-012-1 | 3. | The Planning Authority shall issue its Transfer Capability Methodology, and any changes to that methodology, prior to the effectiveness of such changes, to all of the following: | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-012 | FAC-012-1 | 3.1. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-012 | FAC-012-1 | 3.2. | Each Adjacent Planning Authority and each Planning Authority that indicated a reliability-related need for the methodology. | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-012 | FAC-012-1 | 3.3. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-012 | FAC-012-1 | 4. | If a recipient of the Transfer Capability Methodology provides documented technical comments on the methodology, the Reliability Coordinator or Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability Methodology and, if no change will be made to that Transfer Capability Methodology, the reason why. |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-012 | FAC-012-1 | No Parts for 4. |  |  | Long-Term Planning | 2006-02-07 | 2006-04-04 | [7 empty] | 2013-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-013 | FAC-013-1 | 1. | The Reliability Coordinator and Planning Authority shall each establish a set of inter-regional and intra-regional Transfer Capabilities that is consistent with its current Transfer Capability Methodology. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-013 | FAC-013-1 | No Parts for 1. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | FAC | FAC-013 | FAC-013-1 | 2. | The Reliability Coordinator and Planning Authority shall each provide its inter-regional and intra-regional Transfer Capabilities to those entities that have a reliability-related need for such Transfer Capabilities and make a written request that includes a schedule for delivery of such Transfer Capabilities as follows: | M3. Each Planning Coordinator shall have evidence such as dated assessment results, that it conducted and documented a Transfer Capability assessment in accordance with Requirement R4. | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC |  | RC
Inactive | FAC | FAC-013 | FAC-013-1 | 2.1. | The Reliability Coordinator shall provide its Transfer Capabilities to its associated Regional Reliability Organization(s), to its adjacent Reliability Coordinators, and to the Transmission Operators, Transmission Service Providers and Planning Authorities that work in its Reliability Coordinator Area. | M3. Each Planning Coordinator shall have evidence such as dated assessment results, that it conducted and documented a Transfer Capability assessment in accordance with Requirement R4. | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | FAC | FAC-013 | FAC-013-1 | 2.2. | The Planning Authority shall provide its Transfer Capabilities to its associated Reliability Coordinator(s) and Regional Reliability Organization(s), and to the Transmission Planners and Transmission Service Provider(s) that work in its Planning Authority Area. | M3. Each Planning Coordinator shall have evidence such as dated assessment results, that it conducted and documented a Transfer Capability assessment in accordance with Requirement R4. | Long-Term Planning | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2013-03-31 | Filing/Order Docket No. RM06-16-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1. | Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.1. | Criteria for the selection of the transfers to be assessed. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.2. | A statement that the assessment shall respect known System Operating Limits (SOLs). | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.3. | A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4. | A description of how each of the following assumptions and criteria used in performing the assessment are addressed: | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.1. | Generation dispatch, including but not limited to long term planned outages, additions and retirements. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.2. | Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.3. | System demand. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.4. | Current approved and projected Transmission uses. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.5. | Parallel path (loop flow) adjustments. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.6. | Contingencies | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.4.7. | Monitored Facilities. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 1.5. | A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | M1. Each Planning Coordinator shall have a Transfer Capability methodology that includes the information specified in Requirement R1. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 2. | Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 2.1. | Distribute to the following prior to the effectiveness of such revisions: | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 2.1.1. | Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 2.1.2. | Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2013-04-01 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 2.2. | Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | M2. Each Planning Coordinator shall have evidence such as dated e-mail or dated transmittal letters that it provided the new or revised Transfer Capability methodology in accordance with Requirement R2 Each Planning Coordinator shall have evidence, such as dated e-mail or dated transmittal letters, that the Planning Coordinator provided a written response to that commenter in accordance with Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 | 2012-01-23 | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | 3. | If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Each Planning Coordinator shall have evidence such as dated assessment results, that it conducted and documented a Transfer Capability assessment in accordance with Requirement R4. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | No Parts for 3. |  | Each Planning Coordinator shall have evidence such as dated assessment results, that it conducted and documented a Transfer Capability assessment in accordance with Requirement R4. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000
Inactive | FAC | FAC-013 | FAC-013-2 | 4. | During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | M4. Each Planning Coordinator shall have evidence, such as dated copies of e-mails or transmittal letters, that it made its documented Transfer Capability assessment available to the entities in accordance with Requirement R5. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | No Parts for 4. |  | M4. Each Planning Coordinator shall have evidence, such as dated copies of e-mails or transmittal letters, that it made its documented Transfer Capability assessment available to the entities in accordance with Requirement R5. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000
Inactive | FAC | FAC-013 | FAC-013-2 | 5. | Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | M5. Each Planning Coordinator shall have evidence, such as dated copies of e-mails or transmittal letters, that it made its documented Transfer Capability assessment data available in accordance with Requirement R6. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | No Parts for 5. |  | M5. Each Planning Coordinator shall have evidence, such as dated copies of e-mails or transmittal letters, that it made its documented Transfer Capability assessment data available in accordance with Requirement R6. | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000
Inactive | FAC | FAC-013 | FAC-013-2 | 6. | If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. |  | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-013 | FAC-013-2 | No Parts for 6. |  |  | Long-Term Planning | 2011-01-24 | 2011-01-28 | 2011-11-17 | 2012-01-23 | 2013-04-01 |  | X |  |  | 2020-12-14 | Filing/Order Docket No. RM08-19-000, RD11-3-000
Inactive | FAC | FAC-014 | FAC-014-1 | 1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | FAC | FAC-014 | FAC-014-1 | 2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | FAC | FAC-014 | FAC-014-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | FAC | FAC-014 | FAC-014-1 | 3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | FAC | FAC-014 | FAC-014-1 | 4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [21 empty] | TP
Inactive | FAC | FAC-014 | FAC-014-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | FAC | FAC-014 | FAC-014-1 | 5. | The Reliability Coordinator, Planning Authority and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC |  | RC | [7 empty] | TP
Inactive | FAC | FAC-014 | FAC-014-1 | 5.1. | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2008-05-29 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-1 | 5.1.1. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2009-01-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-1 | 5.1.2. | The value of the IROL and its associated Tv. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2009-01-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-1 | 5.1.3. | The associated Contingency(ies). |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2009-01-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-1 | 5.1.4. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2009-01-01 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-1 | 5.2. | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [20 empty] | TOP
Inactive | FAC | FAC-014 | FAC-014-1 | 5.3. | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-1 | 5.4. | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [21 empty] | TP
Inactive | FAC | FAC-014 | FAC-014-1 | 6. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 |  |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-1 | 6.1. | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-1 | 6.2. | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  |  | 2006-11-01 | 2006-11-15 | 2007-12-27 | 2008-02-08 | 2009-01-01 | 2008-02-08 |  |  |  | 2009-04-28 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-2 | 1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | The Reliability Coordinator, Planning Authority, Transmission Operator, and Transmission Planner shall each be able to demonstrate that it developed its SOLs (including the subset of SOLs that are IROLs) consistent with the applicable SOL Methodology in accordance with Requirements 1 through 4. | Operations Assessment | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-2 | No Parts for 1. |  | The Reliability Coordinator, Planning Authority, Transmission Operator, and Transmission Planner shall each be able to demonstrate that it developed its SOLs (including the subset of SOLs that are IROLs) consistent with the applicable SOL Methodology in accordance with Requirements 1 through 4. | Operations Assessment | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-014 | FAC-014-2 | 2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | M2. The Reliability Coordinator, Planning Authority, Transmission Operator, and Transmission Planner shall each have evidence that its SOLs (including the subset of SOLs that are IROLs) were supplied in accordance with schedules supplied by the requestors of such SOLs as specified in Requirement 5. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [20 empty] | TOP
Inactive | FAC | FAC-014 | FAC-014-2 | No Parts for 2. |  | M2. The Reliability Coordinator, Planning Authority, Transmission Operator, and Transmission Planner shall each have evidence that its SOLs (including the subset of SOLs that are IROLs) were supplied in accordance with schedules supplied by the requestors of such SOLs as specified in Requirement 5. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-014 | FAC-014-2 | 3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | M3. The Planning Authority shall have evidence it identified a list of multiple contingencies (if any) and their associated stability limits and provided the list and the limits to its Reliability Coordinators in accordance with Requirement 6. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-2 | No Parts for 3. |  | M3. The Planning Authority shall have evidence it identified a list of multiple contingencies (if any) and their associated stability limits and provided the list and the limits to its Reliability Coordinators in accordance with Requirement 6. |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-014 | FAC-014-2 | 4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [21 empty] | TP
Inactive | FAC | FAC-014 | FAC-014-2 | No Parts for 4. |  |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-014 | FAC-014-2 | 5. | The Reliability Coordinator, Planning Authority, and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC |  | RC | [7 empty] | TP
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1. | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1.1. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1.2. | The value of the IROL and its associated Tv. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1.2.2. (DO NOT USE) | (DO NOT USE) |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1.2.4. (DO NOT USE) | (DO NOT USE) |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1.3. | The associated Contingency(ies). |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-2 | 5.1.4. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [13 empty] | RC
Inactive | FAC | FAC-014 | FAC-014-2 | 5.2. | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [20 empty] | TOP
Inactive | FAC | FAC-014 | FAC-014-2 | 5.3. | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-2 | 5.4. | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [21 empty] | TP
Inactive | FAC | FAC-014 | FAC-014-2 | 6. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-2 | 6.1. | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Inactive | FAC | FAC-014 | FAC-014-2 | 6.2. | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  |  | 2008-06-24 | 2008-06-30 | 2009-03-20 | 2009-04-29 | 2009-04-29 | 2009-04-29 |  |  |  | 2024-03-31 | Filing/Order Docket No. RM08-11-000 | [10 empty] | PA | PC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 1. | Each Reliability Coordinator shall establish Interconnection Reliability Operating Limits (IROLs) for its Reliability Coordinator Area in accordance with its System Operating Limit methodology (SOL methodology). | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Reliability Coordinator established IROLs in accordance with it SOL methodology. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | No Parts for 1. |  | M1. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Reliability Coordinator established IROLs in accordance with it SOL methodology. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 2. | Each Transmission Operator shall establish System Operating Limits (SOLs) for its portion of the Reliability Coordinator Area in accordance with its Reliability Coordinator’s SOL methodology. | M2. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Transmission Operator established SOLs in accordance with its Reliability Coordinator’s SOL methodology. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | No Parts for 2. |  | M2. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Transmission Operator established SOLs in accordance with its Reliability Coordinator’s SOL methodology. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 3. | Each Transmission Operator shall provide its SOLs to its Reliability Coordinator. | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Transmission Operator provided its SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [20 empty] | TOP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | No Parts for 3. |  | M3. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Transmission Operator provided its SOLs. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 4. | Each Reliability Coordinator shall establish stability limits when an identified instability impacts adjacent Reliability Coordinator Areas or more than one Transmission Operator in its Reliability Coordinator Area in accordance with its SOL methodology. | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Reliability Coordinator established stability limits in accordance with Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | No Parts for 4. |  | M4. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation that demonstrates the Reliability Coordinator established stability limits in accordance with Requirement R4. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5. | Each Reliability Coordinator shall provide: | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.1. | Each Planning Coordinator and each Transmission Planner within its Reliability Coordinator Area, the SOLs for its Reliability Coordinator Area (including the subset of SOLs that are IROLs) at least once every twelve calendar months. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2. | Each impacted Planning Coordinator and each impacted Transmission Planner within its Reliability Coordinator Area, the following information for each established stability limit and each established IROL at least once every twelve calendar months: | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2.1. | The value of the stability limit or IROL; | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2.2. | Identification of the Facilities that are critical to the derivation of the stability limit or the IROL; | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2.3. | The associated IROL Tv for any IROL; | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2.4. | The associated critical Contingency(ies); | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2.5. | A description of system conditions associated with the stability limit or IROL; and | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.2.6. | The type of limitation represented by the stability limit or IROL (e.g., voltage collapse, angular stability). | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.3. | Each impacted Transmission Operator within its Reliability Coordinator Area, the value of the stability limits established pursuant to Requirement R4 and each IROL established pursuant to Requirement R1, in an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.4. | Each impacted Transmission Operator within its Reliability Coordinator Area, the information identified in Requirement R5 Parts 5.2.2 – 5.2.6 for each established stability limit and each established IROL, and any updates to that information within an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.5. | Each requesting Transmission Operator within its Reliability Coordinator Area, requested SOL information for its Reliability Coordinator Area, on a mutually agreed upon schedule. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 5.6. | Each impacted Generator Owner or Transmission Owner, within its Reliability Coordinator Area, with a list of their Facilities that have been identified as critical to the derivation of an IROL and its associated critical contingencies at least once every twelve calendar months. | M5. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 6. | Each Planning Coordinator and each Transmission Planner shall implement a documented process to use Facility Ratings, System steady-state voltage limits and stability criteria in its Planning Assessment of Near-Term Transmission Planning Horizon that are equally limiting or more limiting than the criteria for Facility Ratings, System Voltage Limits and stability described in its respective Reliability Coordinator’s SOL methodology. • The Planning Coordinator may use less limiting Facility Ratings, System steady-state voltage limits and stability criteria if it provides a technical rationale to each affected Transmission Planner, Transmission Operator and Reliability Coordinator. • The Transmission Planner may use less limiting Facility Ratings, System steady-state voltage limits and stability criteria if it provides a technical rationale to each affected Planning Coordinator, Transmission Operator and Reliability Coordinator. | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner implemented its documented process in accordance with Requirement R6. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | No Parts for 6. |  | M6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner implemented its documented process in accordance with Requirement R6. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 7. | Each Planning Coordinator and each Transmission Planner shall annually communicate the following information for Corrective Action Plans developed to address any instability identified in its Planning Assessment of the Near-Term Transmission Planning Horizon to each impacted Transmission Operator and Reliability Coordinator. This communication shall include: | M7. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 7.1. | The Corrective Action Plan developed to mitigate the identified instability, including any automatic control or operator-assisted actions (such as Remedial Action Schemes, under voltage load shedding, or any Operating Procedures); | M7. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 7.2. | The type of instability addressed by the Corrective Action Plan (e.g. steady-state and/or transient voltage instability, angular instability including generating unit loss of synchronism and/or unacceptable damping); | M7. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 7.3. | The associated stability criteria violation requiring the Corrective Action Plan (e.g. violation of transient voltage response criteria or damping rate criteria); | M7. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 7.4. | The planning event Contingency(ies) associated with the identified instability requiring the Corrective Action Plan; | M7. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 7.5. | The System conditions and Facilities associated with the identified instability requiring the Corrective Action Plan. | M7. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | 2024-04-01 |  |  |  |  | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | 8. | Each Planning Coordinator and each Transmission Planner shall annually communicate to each impacted Transmission Owner and Generation Owner a list of their Facilities that comprise the planning event Contingency(ies) that would cause instability, Cascading or uncontrolled separation that adversely impacts the reliability of the BES as identified in its Planning Assessment of the Near‐Term Transmission Planning Horizon. | M8. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R8. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [10 empty] | PA | PC | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-014 | FAC-014-3 | No Parts for 8. |  | M8. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R8. | Long-Term Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Inactive | FAC | FAC-501 | FAC-501-WECC-1 | 1. | Transmission Owners shall have a TMIP detailing their inspection and maintenance requirements that apply to all transmission facilities necessary for System Operating Limits associated with each of the transmission paths identified in table titled “Major WECC Transfer Paths in the Bulk Electric System." R1.1. Transmission Owners shall annually review their TMIP and update as required. | M1. Transmission Owners shall have a documented TMIP per R.1. | Long-Term Planning | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM09-9-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-1 | 1.1. | Transmission Owners shall annually review their TMIP and update as required. | M1. Transmission Owners shall have a documented TMIP per R.1. | Long-Term Planning | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 | 2011-07-01 |  |  |  | 2018-06-30 | Filing/Order Docket No. RM09-9-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-1 | 2. | Transmission Owners shall include the maintenance categories in Attachment 1-FAC-501-WECC-1 when developing their TMIP. | M2. Transmission Owners shall have evidence that their TMIP addresses the required maintenance details of R.2. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM09-9-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-1 | No Parts for 2. |  | M2. Transmission Owners shall have evidence that their TMIP addresses the required maintenance details of R.2. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM09-9-000
Inactive | FAC | FAC-501 | FAC-501-WECC-1 | 3. | Transmission Owners shall implement and follow their TMIP. | M3. Transmission Owners shall have records that they implemented and followed their TMIP as required in R.3. The records shall include: 1. The person or crew responsible for performing the work or inspection, 2. The date(s) the work or inspection was performed, 3. The transmission facility on which the work was performed, and 4. A description of the inspection or maintenance performed. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM09-9-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-1 | No Parts for 3. |  | M3. Transmission Owners shall have records that they implemented and followed their TMIP as required in R.3. The records shall include: 1. The person or crew responsible for performing the work or inspection, 2. The date(s) the work or inspection was performed, 3. The transmission facility on which the work was performed, and 4. A description of the inspection or maintenance performed. | Operations Assessment | 2008-10-29 | 2009-02-09 | 2011-04-21 | 2011-06-27 | 2011-07-01 |  |  |  |  | 2018-06-30 | Filing/Order Docket No. RM09-9-000
Inactive | FAC | FAC-501 | FAC-501-WECC-2 | 1. | Each Transmission Owner shall have a TMIP that includes, at a minimum, each of the items listed in Attachment A, Transmission Maintenance and Inspection Plan Content. | M1. Each Transmission Owner will have evidence that it has a TMIP detailing each of the items listed in Attachment A, as required in Requirement R1. | Long-Term Planning | 2018-02-08 | 2018-03-16 | 2018-05-30 | 2018-05-30 | 2018-07-01 |  |  |  |  | 2024-12-31 | Filing/Order Docket No. RD18-5-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-2 | No Parts for 1. |  | M1. Each Transmission Owner will have evidence that it has a TMIP detailing each of the items listed in Attachment A, as required in Requirement R1. | Long-Term Planning | 2018-02-08 | 2018-03-16 | 2018-05-30 | 2018-05-30 | 2018-07-01 |  |  |  |  | 2024-12-31 | Filing/Order Docket No. RD18-5-000
Inactive | FAC | FAC-501 | FAC-501-WECC-2 | 2. | Each Transmission Owner shall annually update its TMIP to reflect all changes to its TMIP. | M2. Each Transmission Owner will have evidence that it annually updated its TMIP, as required in Requirement R2. When an annual update shows that no changes are required to the TMIP, evidence may include but is not limited to, attestation that the update was performed but showed that no changes were required. | Long-Term Planning | 2018-02-08 | 2018-03-16 | 2018-05-30 | 2018-05-30 | 2018-07-01 |  |  |  |  | 2024-12-31 | Filing/Order Docket No. RD18-5-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-2 | No Parts for 2. |  | M2. Each Transmission Owner will have evidence that it annually updated its TMIP, as required in Requirement R2. When an annual update shows that no changes are required to the TMIP, evidence may include but is not limited to, attestation that the update was performed but showed that no changes were required. | Long-Term Planning | 2018-02-08 | 2018-03-16 | 2018-05-30 | 2018-05-30 | 2018-07-01 |  |  |  |  | 2024-12-31 | Filing/Order Docket No. RD18-5-000
Inactive | FAC | FAC-501 | FAC-501-WECC-2 | 3. | Each Transmission Owner shall adhere to its TMIP. | M3. Each Transmission Owner will have evidence that it adhered to its TMIP, as required in Requirement R3. Evidence may include, but is not limited to: 1.1 The date(s) the patrol, inspection or maintenance was performed; 1.2 The transmission Facility or Element on which the maintenance was performed; 1.3 A description of the inspection results or maintenance performed. | Operations Assessment | 2018-02-08 | 2018-03-16 | 2018-05-30 | 2018-05-30 | 2018-07-01 |  |  |  |  | 2024-12-31 | Filing/Order Docket No. RD18-5-000 | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-2 | No Parts for 3. |  | M3. Each Transmission Owner will have evidence that it adhered to its TMIP, as required in Requirement R3. Evidence may include, but is not limited to: 1.1 The date(s) the patrol, inspection or maintenance was performed; 1.2 The transmission Facility or Element on which the maintenance was performed; 1.3 A description of the inspection results or maintenance performed. | Operations Assessment | 2018-02-08 | 2018-03-16 | 2018-05-30 | 2018-05-30 | 2018-07-01 |  |  |  |  | 2024-12-31 | Filing/Order Docket No. RD18-5-000
Inactive | FAC | FAC-501 | FAC-501-WECC-3 | 1. | Each Transmission Owner shall have a TMIP that includes, at a minimum, each of the items listed in Attachment A, Transmission Maintenance and Inspection Plan (TMIP) Content. | M1.Each Transmission Owner will have evidence that it has a TMIP detailing each of the items listed in Attachment A, as required in Requirement R1. | Long-Term Planning | [9 empty] | 2024-09-26 | This version will never become effective | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-3 | No Parts for 1. |  | M1.Each Transmission Owner will have evidence that it has a TMIP detailing each of the items listed in Attachment A, as required in Requirement R1. | Long-Term Planning | [9 empty] | 2024-09-26 | This version will never become effective
Inactive | FAC | FAC-501 | FAC-501-WECC-3 | 2. | Each Transmission Owner shall annually update its TMIP to reflect all changes to its TMIP. | M2.Each Transmission Owner will have evidence that it annually updated its TMIP, as required in Requirement R2. When an annual update shows no changes are required to the TMIP, evidence may include but is not limited to, attestation that the update was performed but showed no changes were required. | Long-Term Planning | [9 empty] | 2024-09-26 | This version will never become effective | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-3 | No Parts for 2. |  | M2.Each Transmission Owner will have evidence that it annually updated its TMIP, as required in Requirement R2. When an annual update shows no changes are required to the TMIP, evidence may include but is not limited to, attestation that the update was performed but showed no changes were required. | Long-Term Planning | [9 empty] | 2024-09-26 | This version will never become effective
Inactive | FAC | FAC-501 | FAC-501-WECC-3 | 3. | Each Transmission Owner shall adhere to its TMIP. | M3.Each Transmission Owner will have evidence that it adhered to its TMIP, as required in Requirement R3. Evidence may include, but is not limited to: 1.1 The date(s) the patrol, inspection or maintenance was performed; 1.2 The equipment on which the maintenance was performed; 1.3 A description of the inspection results or maintenance performed. | Operations Assessment | [9 empty] | 2024-09-26 | This version will never become effective | [19 empty] | TO
Inactive | FAC | FAC-501 | FAC-501-WECC-3 | No Parts for 3. |  | M3.Each Transmission Owner will have evidence that it adhered to its TMIP, as required in Requirement R3. Evidence may include, but is not limited to: 1.1 The date(s) the patrol, inspection or maintenance was performed; 1.2 The equipment on which the maintenance was performed; 1.3 A description of the inspection results or maintenance performed. | Operations Assessment | [9 empty] | 2024-09-26 | This version will never become effective
Mandatory Subject to Enforcement | FAC | FAC-501 | FAC-501-WECC-4 | 1. | Each Transmission Owner shall have a TMIP that includes, at a minimum, each of the items listed in Attachment A, Transmission Maintenance and Inspection Plan (TMIP) Content. |  | Long-Term Planning | 2024-05-09 | 2024-05-17 | 2024-09-26 | 2024-09-26 | 2025-01-01 | [5 empty] | Filing/Order Docket No. RD24-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-501 | FAC-501-WECC-4 | No Parts for 1. |  |  | Long-Term Planning | 2024-05-09 | 2024-05-17 | 2024-09-26 | 2024-09-26 | 2025-01-01 | [5 empty] | Filing/Order Docket No. RD24-7-000
Mandatory Subject to Enforcement | FAC | FAC-501 | FAC-501-WECC-4 | 2. | Each Transmission Owner shall annually update its TMIP to reflect all changes to its TMIP. | Each Transmission Owner will have evidence that it annually updated its TMIP, as required in Requirement R2. When an annual update shows no changes are required to the TMIP, evidence may include but is not limited to, attestation that the update was performed but showed no changes were required. | Long-Term Planning | 2024-05-09 | 2024-05-17 | 2024-09-26 | 2024-09-26 | 2025-01-01 | [5 empty] | Filing/Order Docket No. RD24-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-501 | FAC-501-WECC-4 | No Parts for 2. |  | Each Transmission Owner will have evidence that it annually updated its TMIP, as required in Requirement R2. When an annual update shows no changes are required to the TMIP, evidence may include but is not limited to, attestation that the update was performed but showed no changes were required. | Long-Term Planning | 2024-05-09 | 2024-05-17 | 2024-09-26 | 2024-09-26 | 2025-01-01 | [5 empty] | Filing/Order Docket No. RD24-7-000
Mandatory Subject to Enforcement | FAC | FAC-501 | FAC-501-WECC-4 | 3. | Each Transmission Owner shall adhere to its TMIP. | Each Transmission Owner will have evidence that it adhered to its TMIP, as required in Requirement R3. Evidence may include, but is not limited to: 1.1 The date(s) the patrol, inspection or maintenance was performed; 1.2 The equipment on which the maintenance was performed; 1.3 A description of the inspection results or maintenance performed. | Operations Assessment | 2024-05-09 | 2024-05-17 | 2024-09-26 | 2024-09-26 | 2025-01-01 | [5 empty] | Filing/Order Docket No. RD24-7-000 | [19 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-501 | FAC-501-WECC-4 | No Parts for 3. |  | Each Transmission Owner will have evidence that it adhered to its TMIP, as required in Requirement R3. Evidence may include, but is not limited to: 1.1 The date(s) the patrol, inspection or maintenance was performed; 1.2 The equipment on which the maintenance was performed; 1.3 A description of the inspection results or maintenance performed. | Operations Assessment | 2024-05-09 | 2024-05-17 | 2024-09-26 | 2024-09-26 | 2025-01-01 | [5 empty] | Filing/Order Docket No. RD24-7-000
Inactive | INT | INT-001 | INT-001-0 | 1. | The Load-serving Purchasing-Selling Entity shall be responsible for ensuring Tags are submitted for: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | 1.1. | All Interchange Transactions that are between Balancing Authority Areas |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA | [11 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | 1.2. | All transfers that are entirely within a Balancing Authority Area using Point-to-Point Transmission Service (including all grandfathered and “non-Order 888” Point-to-Point Transmission Service). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA | [11 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | 1.3. | All Dynamic Schedules at the expected average MW profile for each hour. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA | [11 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | 2. | The Sink Balancing Authority shall be responsible for ensuring a Tag is provided: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA
Inactive | INT | INT-001 | INT-001-0 | 2.1. | If a Purchasing-Selling Entity is not involved in the Transaction, such as delivery from a jointly owned generator. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA
Inactive | INT | INT-001 | INT-001-0 | 2.2. | To replace unexpected generation loss, such as through prearranged reserve sharing agreements or other arrangements. If the duration of the Emergency Transaction to replace the generation loss is less than 60 minutes, then the Transaction shall be exempt from Tagging. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA
Inactive | INT | INT-001 | INT-001-0 | 2.3. | All bilateral inadvertent interchange payback. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA
Inactive | INT | INT-001 | INT-001-0 | 3. | The Purchasing Selling Entity responsible for submitting the Tag shall submit all Tags to the Sink Balancing Authority according to timing tables in Attachment 1-INT-001-0. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA | [11 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable
Inactive | INT | INT-001 | INT-001-0 | 4. | The Balancing Authority or Purchasing-Selling Entity responsible for submitting the Tag shall include the reliability data listed in Attachment 2-INT-001-0 in the Tag. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | BA | [11 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable
Inactive | INT | INT-001 | INT-001-0 | 5. | Each Purchasing-Selling Entity with title to an Interchange Transaction shall have, or shall arrange to have, personnel directly and immediately available for notification of Interchange Transaction changes. These personnel shall be available from the time that the title to the Interchange Transaction is acquired until the Interchange Transaction has been completed. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-001-0 was never enforceable
Inactive | INT | INT-001 | INT-001-1 | 1. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: |  |  | 2006-05-02 | [8 empty] | 2006-11-01 | Replaced with INT-001-2 (INT-001-1 was never enforceable) | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-1 | 1.1. | All Dynamic Schedules at the expected average MW profile for each hour. |  |  | 2006-05-02 | [8 empty] | 2006-11-01 | Replaced with INT-001-2 (INT-001-1 was never enforceable) | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-1 | 2. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: |  |  | 2006-05-02 | [8 empty] | 2006-11-01 | Replaced with INT-001-2 (INT-001-1 was never enforceable) | BA
Inactive | INT | INT-001 | INT-001-1 | 2.1. | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  |  | 2006-05-02 | [8 empty] | 2006-11-01 | Replaced with INT-001-2 (INT-001-1 was never enforceable) | BA | [11 empty] | PSE
Inactive | INT | INT-001 | INT-001-1 | 2.2. | For each bilateral Inadvertent Interchange payback. |  |  | 2006-05-02 | [8 empty] | 2006-11-01 | Replaced with INT-001-2 (INT-001-1 was never enforceable) | BA
Inactive | INT | INT-001 | INT-001-2 | 1. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-2 | 1.1. | All Dynamic Schedules at the expected average MW profile for each hour. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-2 | 2. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-001 | INT-001-2 | 2.1. | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-001 | INT-001-2 | 2.2. | For each bilateral Inadvertent Interchange payback. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-001 | INT-001-3 | 1. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-3 | 1.1. | All Dynamic Schedules at the expected average MW profile for each hour. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | [12 empty] | PSE
Inactive | INT | INT-001 | INT-001-3 | 2. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-001 | INT-001-3 | 2.1. | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-001 | INT-001-3 | 2.2. | For each bilateral Inadvertent Interchange payback. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-002 | INT-002-0 | 1. | The Sink Balancing Authority shall ensure that all Tags and any modifications to Tags are provided via a secure network to the following entities on the Scheduling Path: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 1.1. | Sink and Source Balancing Authority for the Transaction. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 1.2. | Intermediate Balancing Authorities on the Schedule Path. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 1.3. | Transmission Service Provider(s) on the Schedule Path |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA | [21 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 1.4. | Reliability analysis services (IDC or other regional reliability tools). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 1.5. | Transmission Operators and Reliability Coordinators who may receive the information through Reliability analysis services. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 2. | Transmission Service Providers on the Scheduling Path shall be responsible for assessing and approving or denying the Interchange Transaction based on established reliability criteria and adequacy of Interconnected Operating Services and transmission rights as well as the reasonableness of the Interchange Transaction Tag. The Transmission Service Provider shall verify and assess: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 2.1. | Valid OASIS reservation number or transmission contract identifier. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 2.2. | Transmission priority matches reservation |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 2.3. | Energy profile fits within OASIS reservation. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 2.4. | OASIS reservation accommodates all Interchange Transactions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 2.5. | Connectivity of adjacent Transmission Service Providers. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 2.6. | Loss accounting. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | [22 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | 3. | Balancing Authorities on the Scheduling Path shall be responsible for assessing and approving or denying the Interchange Transaction. The Balancing Authority shall verify and assess: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 3.1. | Transaction start and end time. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 3.2. | Energy profile (ability to support the magnitude of the transaction). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 3.3. | Ramp (ability of generation maneuverability to accommodate). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 3.4. | Scheduling path (proper connectivity of adjacent Balancing Authorities). |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | 4. | Each Balancing Authority and Transmission Service Provider on the Scheduling Path shall communicate their approval or denial of the Interchange Transaction to the Sink Balancing Authority. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA | [21 empty] | TSP
Inactive | INT | INT-002 | INT-002-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable
Inactive | INT | INT-002 | INT-002-0 | 5. | Upon receipt of approvals or denials from all of the individual Balancing Authorities and Transmission Service Providers, the Sink Balancing Authority shall communicate the composite approval status of the Interchange Transaction to the Purchasing-Selling Entity and all other Balancing Authorities and Transmission Service Providers on the Scheduling Path and through the Reliability analysis service to affected Transmission Operators and Reliability Coordinators. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable | BA
Inactive | INT | INT-002 | INT-002-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 This standard was never enforceable
Inactive | INT | INT-003 | INT-003-0 | 1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 1.1.1. | Interchange Schedule start and end time. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 1.1.2. | Energy profile. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 1.1.3. | Ramp start time and duration (Balancing Authorities shall use the Ramp duration established for their Interconnection unless they agree to an alternative Ramp duration.) Default Ramps durations are as follows: • Default Ramp duration for the Eastern Interconnection shall be 10 minutes equally across the Interchange Schedule start and end times. • Default Ramp duration for the Western Interconnection shall be 20 minutes equally across the Interchange Schedule start and end times. • Ramp durations for Interchange Schedules implemented for compliance with NERC’s Disturbance Control Standard (recovery from a disturbance condition) and Interchange Transaction curtailment in response to line loading relief procedures may be shorter than the above defaults, but must be identical for the Sending Balancing Authority and Receiving Balancing Authority. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 1.3. | Balancing Authorities that implement Interchange Schedules that cross an Interconnection boundary shall use the same start time and Ramp durations. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 2. | Balancing Authorities shall implement Interchange Schedules only with Adjacent Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable
Inactive | INT | INT-003 | INT-003-0 | 3. | Balancing Authorities shall begin and end Interchange Schedules at a time agreed to by the Source Balancing Authority, Sink Balancing Authority, and Intermediate Balancing Authorities. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable
Inactive | INT | INT-003 | INT-003-0 | 4. | The Sink Balancing Authority shall be responsible for initiating implementation of each Interchange Transaction as tagged. Upon receiving composite approval from the Sink Balancing Authority, each Balancing Authority on the scheduling path shall enter confirmed Schedules into its Automatic Generation Control ACE equation. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable
Inactive | INT | INT-003 | INT-003-0 | 5. | Balancing Authorities shall operate such that Interchange Schedules do not knowingly cause any other systems to violate established operating criteria. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable
Inactive | INT | INT-003 | INT-003-0 | 6. | Balancing Authorities shall operate such that the maximum Net Interchange Schedule between any two Balancing Authorities does not exceed the lesser of: |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 6.1. | The total capacity of both the owned and arranged-for transmission facilities in service for any Transmission Service Provider along the path, or |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-0 | 6.2. | The established network Total Transfer Capability between Balancing Authorities, which considers other transmission facilities available to them under specific arrangements, and the overall physical constraints of the transmission network. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-0 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-1 | 1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. |  |  | 2006-05-02 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-1 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-1 | 1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  |  | 2006-05-02 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-1 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-1 | 1.1.1. | Interchange Schedule start and end time. |  |  | 2006-05-02 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-1 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-1 | 1.1.2. | Energy profile. |  |  | 2006-05-02 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-1 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-1 | 1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  |  | 2006-05-02 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 INT-003-1 was never enforceable | BA
Inactive | INT | INT-003 | INT-003-2 | 1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-003 | INT-003-2 | 1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-003 | INT-003-2 | 1.1.1. | Interchange Schedule start and end time. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-003 | INT-003-2 | 1.1.2. | Energy profile. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-003 | INT-003-2 | 1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2011-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA
Inactive | INT | INT-003 | INT-003-3 | 1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. |  |  | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | INT | INT-003 | INT-003-3 | 1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  |  | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | INT | INT-003 | INT-003-3 | 1.1.1. | Interchange Schedule start and end time. |  |  | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | INT | INT-003 | INT-003-3 | 1.1.2. | Energy profile. |  |  | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | INT | INT-003 | INT-003-3 | 1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  |  | 2009-11-05 | 2009-11-20 | 2011-01-06 | 2011-01-06 | 2011-04-01 | 2011-04-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RD10-4-000 | BA
Inactive | INT | INT-004 | INT-004-0 | 1. | If a Reliability Coordinator, Transmission Operator, or Source or Sink Balancing Authority, due to a reliability event, needs to modify an Interchange Transaction that is in progress or scheduled to be started, the entity shall, within 60 minutes of the start of the emergency Transaction, modify the Interchange Transaction tag, and shall communicate the modification to the Sink Balancing Authority. Reliability events may include: | The Sink Balancing Authority shall provide evidence that the responsible Purchasing-Selling Entity revised a tag when the deviation exceeded the criteria in Requirement R5. |  | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-0 | 1.1. | Transmission Loading Relief procedure curtailment — Eastern Interconnection. | The Sink Balancing Authority shall provide evidence that the responsible Purchasing-Selling Entity revised a tag when the deviation exceeded the criteria in Requirement R5. |  | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-0 | 1.2. | Interconnection, regional, or local overload relief or congestion management procedures. | The Sink Balancing Authority shall provide evidence that the responsible Purchasing-Selling Entity revised a tag when the deviation exceeded the criteria in Requirement R5. |  | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-0 | 1.3. | SOL or IROL potential or actual limit violation. | The Sink Balancing Authority shall provide evidence that the responsible Purchasing-Selling Entity revised a tag when the deviation exceeded the criteria in Requirement R5. |  | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-0 | 1.4. | Loss of generation. | The Sink Balancing Authority shall provide evidence that the responsible Purchasing-Selling Entity revised a tag when the deviation exceeded the criteria in Requirement R5. |  | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-0 | 1.5. | Loss of Load. | The Sink Balancing Authority shall provide evidence that the responsible Purchasing-Selling Entity revised a tag when the deviation exceeded the criteria in Requirement R5. |  | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-0 | 2. | A Generator Operator or Load Serving Entity may request the Host Balancing Authority to modify an Interchange Transaction due to loss of generation or Load. |  | Operations Planning, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA
Inactive | INT | INT-004 | INT-004-0 | 2.1. | When a loss of generation necessitates curtailing Interchange Transactions, the Source Balancing Authority shall coordinate the modifications to the appropriate tags. |  | Operations Planning, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA
Inactive | INT | INT-004 | INT-004-0 | 2.2. | When a loss of Load necessitates curtailing Interchange Transactions, the Sink Balancing Authority shall coordinate the modifications to the appropriate tags. |  | Operations Planning, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA
Inactive | INT | INT-004 | INT-004-0 | 3. | Upon receipt of modification to an Interchange Transaction as described in Requirement R1, the Sink Balancing Authority (Source Balancing Authority in the case of a loss of generation) shall communicate the modified information about the Interchange Transaction, including its composite approval status, to all Balancing Authorities and Transmission Service Providers on the Transaction path and the Purchasing-Selling Entity responsible for the Transaction. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA
Inactive | INT | INT-004 | INT-004-0 | No Parts for 3. |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable)
Inactive | INT | INT-004 | INT-004-0 | 4. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | BA
Inactive | INT | INT-004 | INT-004-0 | No Parts for 4. |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable)
Inactive | INT | INT-004 | INT-004-0 | 5. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occur: | M3. The Balancing Authority shall have evidence (such as dated and time-stamped electronic logs or other evidence) that it only implemented or operated a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication. | Operations Planning | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-0 | 5.1. | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. | M3. The Balancing Authority shall have evidence (such as dated and time-stamped electronic logs or other evidence) that it only implemented or operated a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication. | Operations Planning | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-0 | 5.2. | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. | M3. The Balancing Authority shall have evidence (such as dated and time-stamped electronic logs or other evidence) that it only implemented or operated a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication. | Operations Planning | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-0 | 5.3. | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. | M3. The Balancing Authority shall have evidence (such as dated and time-stamped electronic logs or other evidence) that it only implemented or operated a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication. | Operations Planning | 2005-02-08 | [8 empty] | 2007-01-01 | Replaced with INT-003-1 (INT-004-0 was never enforceable) | [12 empty] | PSE | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-1 | 1. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-004 | INT-004-1 | No Parts for 1. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | INT | INT-004 | INT-004-1 | 2. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occurs: |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-1 | 2.1. | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-1 | 2.2. | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-1 | 2.3. | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-2 | 1. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | BA | [11 empty] | PSE | RC | [6 empty] | TOP
Inactive | INT | INT-004 | INT-004-2 | No Parts for 1. |  |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000
Inactive | INT | INT-004 | INT-004-2 | 2. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occurs: |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-2 | 2.1. | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-2 | 2.2. | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-2 | 2.3. | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  |  | 2007-10-09 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM08-7-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3 | 1. | Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time1 Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3 | No Parts for 1. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-004 | INT-004-3 | 2. | The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Please see the standard for more information] |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3 | No Parts for 2. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-004 | INT-004-3 | 3. | Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-004 | INT-004-3 | No Parts for 3. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-004 | INT-004-3.1 | 1. | Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. | M1. The Purchasing-Selling Entity shall have evidence (such as dated and time-stamped electronic logs or other evidence) that a Request for Interchange was submitted for Dynamic Schedules and Pseudo-Ties as an on-time Arranged Interchange to the Sink Balancing Authority for the Dynamic Schedule or Pseudo-Tie. For Pseudo-Ties included in congestion management procedure(s) via an alternate method, the Purchasing-Selling Entity shall have evidence such as Interchange Distribution Calculator model data or written / electronic agreement with a Balancing Authority to include the Pseudo-Tie in the congestion management procedure(s). | Operations Planning, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3.1 | No Parts for 1. |  | M1. The Purchasing-Selling Entity shall have evidence (such as dated and time-stamped electronic logs or other evidence) that a Request for Interchange was submitted for Dynamic Schedules and Pseudo-Ties as an on-time Arranged Interchange to the Sink Balancing Authority for the Dynamic Schedule or Pseudo-Tie. For Pseudo-Ties included in congestion management procedure(s) via an alternate method, the Purchasing-Selling Entity shall have evidence such as Interchange Distribution Calculator model data or written / electronic agreement with a Balancing Authority to include the Pseudo-Tie in the congestion management procedure(s). | Operations Planning, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-004 | INT-004-3.1 | 2. | The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [See standard for additional information.] | M2. The Purchasing-Selling Entity shall have evidence (such as dated and time-stamped electronic logs, reliability studies or other evidence) that it updated its Confirmed Interchange Requests for Interchange when the deviation met the criteria in Requirement R2, Parts 2.1- 2.3. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3.1 | 2.1. | For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. | M2. The Purchasing-Selling Entity shall have evidence (such as dated and time-stamped electronic logs, reliability studies or other evidence) that it updated its Confirmed Interchange Requests for Interchange when the deviation met the criteria in Requirement R2, Parts 2.1- 2.3. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3.1 | 2.2. | For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. | M2. The Purchasing-Selling Entity shall have evidence (such as dated and time-stamped electronic logs, reliability studies or other evidence) that it updated its Confirmed Interchange Requests for Interchange when the deviation met the criteria in Requirement R2, Parts 2.1- 2.3. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3.1 | 2.3. | The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. | M2. The Purchasing-Selling Entity shall have evidence (such as dated and time-stamped electronic logs, reliability studies or other evidence) that it updated its Confirmed Interchange Requests for Interchange when the deviation met the criteria in Requirement R2, Parts 2.1- 2.3. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | [12 empty] | PSE
Inactive | INT | INT-004 | INT-004-3.1 | 3. | Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | M3. The Balancing Authority shall have evidence (such as dated and time-stamped electronic logs or other evidence) that it only implemented or operated a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication. | Operations Planning | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-004 | INT-004-3.1 | No Parts for 3. |  | M3. The Balancing Authority shall have evidence (such as dated and time-stamped electronic logs or other evidence) that it only implemented or operated a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication. | Operations Planning | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-005 | INT-005-1 | 1. | Prior to the expiration of the time period defined in the Timing Table, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-005 | INT-005-1 | 1.1. | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-005 | INT-005-2 | 1. | Prior to the expiration of the time period defined in the Timing Table, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [8 empty] | IA
Inactive | INT | INT-005 | INT-005-2 | 1.1. | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [8 empty] | IA
Inactive | INT | INT-005 | INT-005-3 | 1. | Prior to the expiration of the time period defined in the timing requirements tables in this standard, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [8 empty] | IA
Inactive | INT | INT-005 | INT-005-3 | 1.1. | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-01-25 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [8 empty] | IA
Inactive | INT | INT-006 | INT-006-1 | 1. | Prior to the expiration of the reliability assessment period defined in the Timing Table, Column B, the Balancing Authority and Transmission Service Provider shall respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [21 empty] | TSP
Inactive | INT | INT-006 | INT-006-1 | 1.1. | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-006 | INT-006-1 | 1.1.1. | Energy profile (ability to support the magnitude of the Interchange). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-006 | INT-006-1 | 1.1.2. | Ramp (ability of generation maneuverability to accommodate). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-006 | INT-006-1 | 1.1.3. | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-006 | INT-006-1 | 1.2. | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [22 empty] | TSP
Inactive | INT | INT-006 | INT-006-2 | 1. | Prior to the expiration of the reliability assessment period defined in the Timing Table, Column B, the Balancing Authority and Transmission Service Provider shall respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | BA | [21 empty] | TSP
Inactive | INT | INT-006 | INT-006-2 | 1.1. | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-006 | INT-006-2 | 1.1.1. | Energy profile (ability to support the magnitude of the Interchange). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-006 | INT-006-2 | 1.1.2. | Ramp (ability of generation maneuverability to accommodate). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-006 | INT-006-2 | 1.1.3. | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | BA
Inactive | INT | INT-006 | INT-006-2 | 1.2. | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [22 empty] | TSP
Inactive | INT | INT-006 | INT-006-3 | 1. | Prior to the expiration of the reliability assessment period defined in the timing requirements tables in this standard, Column B, the Balancing Authority and Transmission Service Provider shall respond to each On-time Request for Interchange (RFI), and to each Emergency RFI and Reliability Adjustment RFI from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. |  | Long-Term Planning | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | BA | [21 empty] | TSP
Inactive | INT | INT-006 | INT-006-3 | 1.1. | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | Long-Term Planning | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-01-25 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | BA
Inactive | INT | INT-006 | INT-006-3 | 1.1.1. | Energy profile (ability to support the magnitude of the Interchange). |  | Long-Term Planning | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | BA
Inactive | INT | INT-006 | INT-006-3 | 1.1.2. | Ramp (ability of generation maneuverability to accommodate). |  | Long-Term Planning | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | BA
Inactive | INT | INT-006 | INT-006-3 | 1.1.3. | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | Long-Term Planning | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | BA
Inactive | INT | INT-006 | INT-006-3 | 1.2. | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | Long-Term Planning | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-01-25 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [22 empty] | TSP
Inactive | INT | INT-006 | INT-006-4 | 1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | M2. Each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it responded to each Arranged Interchange or emergency Arranged Interchange within the time defined in Attachment 1, Column B. If the transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers is invalid, each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it denied the Arranged Interchange or curtailed confirmed Interchange. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | [22 empty] | TSP
Inactive | INT | INT-006 | INT-006-4 | 2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | M2. Each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it responded to each Arranged Interchange or emergency Arranged Interchange within the time defined in Attachment 1, Column B. If the transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers is invalid, each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it denied the Arranged Interchange or curtailed confirmed Interchange. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | [22 empty] | TSP
Inactive | INT | INT-006 | INT-006-4 | 3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | M3. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that when responding to a Reliability Adjustment Arranged Interchange, it either approved the request or denied the request and, if applicable, communicated denial to the Reliability Coordinator no more than 10 minutes after the denial. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 3.1. | If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | M3. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that when responding to a Reliability Adjustment Arranged Interchange, it either approved the request or denied the request and, if applicable, communicated denial to the Reliability Coordinator no more than 10 minutes after the denial. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 4. | Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: • It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | M4. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that, under the conditions in R4, it did not transition an Arranged Interchange to Confirmed Interchange. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | No Parts for 4. |  | M4. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that, under the conditions in R4, it did not transition an Arranged Interchange to Confirmed Interchange. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-006 | INT-006-4 | 5. | For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: [Please see the standard for more information] | M5. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it notified the entities of the on-time Confirmed Interchange such that the notification was delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 5.1. | The Source Balancing Authority, | M5. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it notified the entities of the on-time Confirmed Interchange such that the notification was delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 5.2. | Each Intermediate Balancing Authority, | M5. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it notified the entities of the on-time Confirmed Interchange such that the notification was delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 5.3. | Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | M5. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it notified the entities of the on-time Confirmed Interchange such that the notification was delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 5.4. | Each Transmission Service Provider included in the Arranged Interchange, and | M5. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it notified the entities of the on-time Confirmed Interchange such that the notification was delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-006 | INT-006-4 | 5.5. | Each Purchasing Selling Entity included in the Arranged Interchange. | M5. Each Sink Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it notified the entities of the on-time Confirmed Interchange such that the notification was delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 | 2014-06-30 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | M1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. | M2. Each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it responded to each Arranged Interchange or emergency Arranged Interchange within the time defined in Attachment 1, Column B. If the transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers is invalid, each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it denied the Arranged Interchange or curtailed confirmed Interchange. (R2) | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 | [22 empty] | TSP
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | M2. Each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it responded to each Arranged Interchange or emergency Arranged Interchange within the time defined in Attachment 1, Column B. If the transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers is invalid, each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it denied the Arranged Interchange or curtailed confirmed Interchange. (R2) | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 | [22 empty] | TSP
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | No Parts for 3. |  | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 4. | Reserved. |  |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | No Parts for 4. |  |  |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | 5. | Reserved. |  |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | INT | INT-006 | INT-006-5 | No Parts for 5. |  |  |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Inactive | INT | INT-007 | INT-007-1 | 1. | The Interchange Authority shall verify that Arranged Interchange is balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange by verifying the following: |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.1. | Source Balancing Authority megawatts equal sink Balancing Authority megawatts (adjusted for losses, if appropriate). |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.2. | All reliability entities involved in the Arranged Interchange are currently in the NERC registry. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.3. | The following are defined: |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.3.1. | Generation source and load sink. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.3.2. | Megawatt profile. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.3.3. | Ramp start and stop times. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.3.4. | Interchange duration. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-007 | INT-007-1 | 1.4. | Each Balancing Authority and Transmission Service Provider that received the Arranged Interchange information from the Interchange Authority for reliability assessment has provided approval. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-1 | 1. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on both sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-1 | 1.1. | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-1 | 1.1.1. | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-1 | 1.1.2. | Necessary Interchange information to NERC-identified reliability analysis services. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2008-08-26 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-2 | 1. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on both sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. |  |  | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 |  |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-2 | 1.1. | For Confirmed Interchange, the Interchange Authority shall also communicate: |  |  | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-2 | 1.1.1. | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  |  | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-2 | 1.1.2. | Necessary Interchange information to NERC-identified reliability analysis services. |  |  | 2007-05-02 | 2007-12-26 | 2008-07-21 | 2008-08-27 | 2008-08-27 | 2008-08-27 |  |  |  | 2010-06-30 | Filing/Order Docket No. RM08-7-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-3 | 1. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on both sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. |  |  | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-3 | 1.1. | For Confirmed Interchange, the Interchange Authority shall also communicate: |  |  | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-01-25 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-3 | 1.1.1. | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  |  | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [8 empty] | IA
Inactive | INT | INT-008 | INT-008-3 | 1.1.2. | Necessary Interchange information to NERC-identified reliability analysis services. |  |  | 2008-10-29 | 2009-02-05 | 2009-12-17 | 2010-01-25 | 2010-07-01 | 2010-07-01 |  |  |  | 2014-09-30 | Filing/Order Docket No. RM09-8-000 | [8 empty] | IA
Inactive | INT | INT-009 | INT-009-1 | 1. | The Balancing Authority shall implement Confirmed Interchange as received from the Interchange Authority. | M3. The Sink Balancing Authority shall have evidence such as dated and time-stamped electronic logs or other evidence that a Request for Interchange was submitted reflecting that Interchange Schedule within 60 minutes of the start of any scheduled Interchange that was directed by a Reliability Coordinator for actual or anticipated reliability-related reasons. | Real-Time Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-009 | INT-009-1 | No Parts for 1. |  | M3. The Sink Balancing Authority shall have evidence such as dated and time-stamped electronic logs or other evidence that a Request for Interchange was submitted reflecting that Interchange Schedule within 60 minutes of the start of any scheduled Interchange that was directed by a Reliability Coordinator for actual or anticipated reliability-related reasons. | Real-Time Operations | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | INT | INT-009 | INT-009-2 | 1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: [Please see the standard for more information] |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2 | No Parts for 1. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-009 | INT-009-2 | 2. | The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2 | No Parts for 2. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-009 | INT-009-2 | 3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2 | No Parts for 3. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-009 | INT-009-2.1 | 1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange as directed per INT-010-2 not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2.1 | 1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange as directed per INT-010-2 not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2.1 | 1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority. | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange as directed per INT-010-2 not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2.1 | 2. | The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | M2. The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, written agreement or other evidence) that it used a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2.1 | No Parts for 2. |  | M2. The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, written agreement or other evidence) that it used a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-009 | INT-009-2.1 | 3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | M3. The Balancing Authority shall have evidence (such as dated logs, electronic records, or other evidence) that it coordinated the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | Operations Planning, Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-009 | INT-009-2.1 | No Parts for 3. |  | M3. The Balancing Authority shall have evidence (such as dated logs, electronic records, or other evidence) that it coordinated the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | Operations Planning, Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2021-03-31 | Filing/Order Docket No. RD14-4-000
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | 1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, is: | M1. The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | Operations Planning, Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | 1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and | M1. The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | Operations Planning, Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | 1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority | M1. The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | Operations Planning, Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | 2. | Reserved. | M2. Reserved. |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | No Parts for 2. |  | M2. Reserved. |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | 3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | The Balancing Authority shall have evidence (such as dated logs, electronic records, or other evidence) that it coordinated the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. (R3) | Operations Planning, Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000 | BA
Mandatory Subject to Enforcement | INT | INT-009 | INT-009-3 | No Parts for 3. |  | The Balancing Authority shall have evidence (such as dated logs, electronic records, or other evidence) that it coordinated the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. (R3) | Operations Planning, Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-17-000
Inactive | INT | INT-010 | INT-010-1 | 1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement shall ensure that a request for an Arranged Interchange is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no request for Arranged Interchange is required. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA
Inactive | INT | INT-010 | INT-010-1 | No Parts for 1. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | INT | INT-010 | INT-010-1 | 2. | For a modification to an existing Interchange schedule that is directed by a Reliability Coordinator for current or imminent reliability-related reasons, the Reliability Coordinator shall direct a Balancing Authority to submit the modified Arranged Interchange reflecting that modification within 60 minutes of the initiation of the event. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | INT | INT-010 | INT-010-1 | No Parts for 2. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | INT | INT-010 | INT-010-1 | 3. | For a new Interchange schedule that is directed by a Reliability Coordinator for current or imminent reliability-related reasons, the Reliability Coordinator shall direct a Balancing Authority to submit an Arranged Interchange reflecting that Interchange schedule within 60 minutes of the initiation of the event. |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | INT | INT-010 | INT-010-1 | No Parts for 3. |  |  |  | 2006-05-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2014-09-30 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | INT | INT-010 | INT-010-2 | 1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-010 | INT-010-2 | No Parts for 1. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-010 | INT-010-2 | 2. | Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-010 | INT-010-2 | No Parts for 2. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-010 | INT-010-2 | 3. | Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-010 | INT-010-2 | No Parts for 3. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-010 | INT-010-2.1 | 1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | M1. The Balancing Authority that uses its energy sharing agreement where the duration exceeds 60 minutes shall have evidence such as dated and time-stamped RFI, electronic logs or other similar evidence that it submitted an RFI per Requirement R1. | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-010 | INT-010-2.1 | No Parts for 1. |  | M1. The Balancing Authority that uses its energy sharing agreement where the duration exceeds 60 minutes shall have evidence such as dated and time-stamped RFI, electronic logs or other similar evidence that it submitted an RFI per Requirement R1. | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-010 | INT-010-2.1 | 2. | Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | M2. The Sink Balancing Authority shall have evidence such as dated and time-stamped electronic logs or other similar evidence that a Reliability Adjustment Arranged Interchange was submitted within 60 minutes of the start of a modification to either a Confirmed Interchange or an Implemented Interchange that was directed by a Reliability Coordinator for actual or anticipated reliability-related reasons. | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-010 | INT-010-2.1 | No Parts for 2. |  | M2. The Sink Balancing Authority shall have evidence such as dated and time-stamped electronic logs or other similar evidence that a Reliability Adjustment Arranged Interchange was submitted within 60 minutes of the start of a modification to either a Confirmed Interchange or an Implemented Interchange that was directed by a Reliability Coordinator for actual or anticipated reliability-related reasons. | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-010 | INT-010-2.1 | 3. | Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | M3. The Sink Balancing Authority shall have evidence such as dated and time-stamped electronic logs or other evidence that a Request for Interchange was submitted reflecting that Interchange Schedule within 60 minutes of the start of any scheduled Interchange that was directed by a Reliability Coordinator for actual or anticipated reliability-related reasons. | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000 | BA
Inactive | INT | INT-010 | INT-010-2.1 | No Parts for 3. |  | M3. The Sink Balancing Authority shall have evidence such as dated and time-stamped electronic logs or other evidence that a Request for Interchange was submitted reflecting that Interchange Schedule within 60 minutes of the start of any scheduled Interchange that was directed by a Reliability Coordinator for actual or anticipated reliability-related reasons. | Real-Time Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2020-12-14 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-011 | INT-011-1 | 1. | Each Load-Serving Entity that uses Point to Point Transmission Service for intra-Balancing Authority Area transfers shall submit a Request for Interchange unless the information about intra-Balancing Authority transfers is included in congestion management procedure(s) via an alternate method. |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000 | [9 empty] | LSE
Inactive | INT | INT-011 | INT-011-1 | No Parts for 1. |  |  |  | 2014-02-06 | 2014-02-27 | 2014-06-30 | 2014-06-30 | 2014-10-01 |  |  |  |  | 2014-11-25 | Filing/Order Docket No. RD14-4-000
Inactive | INT | INT-011 | INT-011-1.1 | 1. | Each Load-Serving Entity that uses Point to Point Transmission Service for intra-Balancing Authority Area transfers shall submit a Request for Interchange unless the information about intra-Balancing Authority transfers is included in congestion management procedure(s) via an alternate method. | M1. Each Load-Serving Entity subject to R1 shall have evidence, such as dated and time-stamped electronic records, documentation of congestion management procedures, or other similar evidence, that a Request for Interchange was submitted for each Point to Point Transmission Service intra-Balancing Authority transfer subject to R1 or that each intra-Balancing Authority transfer subject to R1 was accounted for in congestion management procedure(s) via an alternate method. (R1) | Operations Planning, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2015-10-15 | Filing/Order Docket No. RD14-4-000 | [9 empty] | LSE
Inactive | INT | INT-011 | INT-011-1.1 | No Parts for 1. |  | M1. Each Load-Serving Entity subject to R1 shall have evidence, such as dated and time-stamped electronic records, documentation of congestion management procedures, or other similar evidence, that a Request for Interchange was submitted for each Point to Point Transmission Service intra-Balancing Authority transfer subject to R1 or that each intra-Balancing Authority transfer subject to R1 was accounted for in congestion management procedure(s) via an alternate method. (R1) | Operations Planning, Same-Day Operations | 2014-08-20 | 2014-08-22 | 2014-11-26 | 2014-11-26 | 2014-11-26 |  |  |  |  | 2015-10-15 | Filing/Order Docket No. RD14-4-000
Inactive | IRO | IRO-001 | IRO-001-0 | 1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [16 empty] | RRO
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERCcertified Reliability Coordinator operating personnel. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-0 | 9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-0 | No Parts for 9. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-001-0 was never enforceable
Inactive | IRO | IRO-001 | IRO-001-1 | 1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [16 empty] | RRO
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 3. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 4. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 5. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 6. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 7. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | M1. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 8. |  | M1. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1 | 9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. | M2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it complied with its Reliability Coordinator's Operating Instructions, unless the instruction could not be physically implemented, or such actions would have violated safety, equipment, regulatory or statutory requirements. In such cases, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Reliability Coordinator’s Operating Instructions. If such a situation has not occurred, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1 | No Parts for 9. |  | M2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it complied with its Reliability Coordinator's Operating Instructions, unless the instruction could not be physically implemented, or such actions would have violated safety, equipment, regulatory or statutory requirements. In such cases, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Reliability Coordinator’s Operating Instructions. If such a situation has not occurred, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-05-12 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. |  | Real-Time Operations, Same-Day Operations | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [16 empty] | RRO
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 1. |  |  | Real-Time Operations, Same-Day Operations | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. | M2. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, job descriptions, signed agreements, an authority letter signed by an officer of the company, or other equivalent evidence that will be used to confirm that the Reliability Coordinator has the authority to act as described in Requirement 3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, job descriptions, signed agreements, an authority letter signed by an officer of the company, or other equivalent evidence that will be used to confirm that the Reliability Coordinator has the authority to act as described in Requirement 3. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. | M3. The Reliability Coordinator shall have and provide upon request current formal operating agreements with entities that have been delegated any Reliability Coordinator tasks (Requirement 4 Part 1). |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 3. |  | M3. The Reliability Coordinator shall have and provide upon request current formal operating agreements with entities that have been delegated any Reliability Coordinator tasks (Requirement 4 Part 1). |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. | M4. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, job descriptions, signed agreements, records of training sessions, monitoring procedures or other equivalent evidence that will be used to confirm that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area (Requirement 4 Part 2 and Requirement 5). |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 4. |  | M4. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, job descriptions, signed agreements, records of training sessions, monitoring procedures or other equivalent evidence that will be used to confirm that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area (Requirement 4 Part 2 and Requirement 5). |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. | M5. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, records that show each operating person assigned to perform a Reliability Coordinator delegated task has a NERC Reliability Coordinator certification credential, or equivalent evidence confirming that delegated tasks were carried out by NERC certified Reliability Coordinator operating personnel, as specified in Requirement 6. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 5. |  | M5. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, records that show each operating person assigned to perform a Reliability Coordinator delegated task has a NERC Reliability Coordinator certification credential, or equivalent evidence confirming that delegated tasks were carried out by NERC certified Reliability Coordinator operating personnel, as specified in Requirement 6. |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. | M6. The Reliability Coordinator shall have and provide upon request as evidence, signed agreements with adjacent Reliability Coordinators that will be used to confirm that it will coordinate corrective actions in the event SOL and IROL mitigation actions within neighboring areas must be taken. (Requirement 7) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 6. |  | M6. The Reliability Coordinator shall have and provide upon request as evidence, signed agreements with adjacent Reliability Coordinators that will be used to confirm that it will coordinate corrective actions in the event SOL and IROL mitigation actions within neighboring areas must be taken. (Requirement 7) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. | M7. Each Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, or other equivalent evidence that will be used to confirm that it did comply with the Reliability Coordinator's directives, or if for safety, equipment, regulatory or statutory requirements it could not comply, it informed the Reliability Coordinator immediately. (Requirement 8) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 7. |  | M7. Each Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, or other equivalent evidence that will be used to confirm that it did comply with the Reliability Coordinator's directives, or if for safety, equipment, regulatory or statutory requirements it could not comply, it informed the Reliability Coordinator immediately. (Requirement 8) |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 8. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-1.1 | 9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-1.1 | No Parts for 9. |  |  |  | 2008-10-29 | 2009-02-06 | 2009-05-13 | 2009-05-13 | 2009-05-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD09-2-000
Inactive | IRO | IRO-001 | IRO-001-2 | 1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [16 empty] | RRO
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 1. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 2. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 3. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 4. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 5. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 6. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 7. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 7. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-2 | 8. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States). | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-2 | No Parts for 8. |  |  |  | 2011-08-04 | [8 empty] | 2012-08-16 | Replaced after BOT adoption of IRO-001-3 (IRO-001-2 never became enforceable in the United States).
Inactive | IRO | IRO-001 | IRO-001-3 | 1. | Each Reliability Coordinator shall have the authority to act or direct others to act (which could include issuing Reliability Directives) to prevent identified events or mitigate the magnitude or duration of actual events that result in an Emergency or Adverse Reliability Impact. | M1. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it had the authority to take action or direct action, which could have included issuing Reliability Directives, to prevent identified events or mitigate the magnitude or duration of actual events that resulted in an Emergency or Adverse Reliability Impact within its Reliability Coordinator Area. (R1.) | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-08-16 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-001 | IRO-001-3 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it had the authority to take action or direct action, which could have included issuing Reliability Directives, to prevent identified events or mitigate the magnitude or duration of actual events that resulted in an Emergency or Adverse Reliability Impact within its Reliability Coordinator Area. (R1.) | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-08-16 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-001 | IRO-001-3 | 2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s direction unless compliance with the direction cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | M2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include, but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it complied with its Reliability Coordinator's direction, unless the direction could not be physically implemented, or such actions would have violated safety, equipment, regulatory or statutory requirements. In such cases, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Reliability Coordinator’s direction. (R2.) | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-08-16 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | IRO | IRO-001 | IRO-001-3 | No Parts for 2. |  | M2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include, but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it complied with its Reliability Coordinator's direction, unless the direction could not be physically implemented, or such actions would have violated safety, equipment, regulatory or statutory requirements. In such cases, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Reliability Coordinator’s direction. (R2.) | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-08-16 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-001 | IRO-001-3 | 3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator upon recognition of its inability to perform as directed in accordance with Requirement R2. | M3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include, but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it informed the Reliability Coordinator of its inability to perform as directed in accordance with Requirement R2. (R3.) | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-08-16 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Inactive | IRO | IRO-001 | IRO-001-3 | No Parts for 3. |  | M3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include, but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it informed the Reliability Coordinator of its inability to perform as directed in accordance with Requirement R2. (R3.) | Operations Planning, Real-Time Operations, Same-Day Operations | 2012-08-16 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Mandatory Subject to Enforcement | IRO | IRO-001 | IRO-001-4 | 1. | Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. [Violation Risk Factor: | M1. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-001 | IRO-001-4 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-001 | IRO-001-4 | 2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | M2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it complied with its Reliability Coordinator's Operating Instructions, unless the instruction could not be physically implemented, or such actions would have violated safety, equipment, regulatory or statutory requirements. In such cases, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Reliability Coordinator’s Operating Instructions. If such a situation has not occurred, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Mandatory Subject to Enforcement | IRO | IRO-001 | IRO-001-4 | No Parts for 2. |  | M2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it complied with its Reliability Coordinator's Operating Instructions, unless the instruction could not be physically implemented, or such actions would have violated safety, equipment, regulatory or statutory requirements. In such cases, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Reliability Coordinator’s Operating Instructions. If such a situation has not occurred, the Transmission Operator, Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-001 | IRO-001-4 | 3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | M3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it informed its Reliability Coordinator of its inability to perform an Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  |  |  | GOP | [13 empty] | TOP
Mandatory Subject to Enforcement | IRO | IRO-001 | IRO-001-4 | No Parts for 3. |  | M3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it informed its Reliability Coordinator of its inability to perform an Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 | [5 empty] | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-002 | IRO-002-0 | 1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 2. | Each Reliability Coordinator shall determine the data requirements to support its reliability coordination tasks and shall request such data from its Transmission Operators, Balancing Authorities, Transmission Owners, Generation Owners, Generation Operators, and LoadServing Entities, or adjacent Reliability Coordinators. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 2. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 3. | Each Reliability Coordinator – or its Transmission Operators and Balancing Authorities – shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 4. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 5. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 6. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 7. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, preand post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 7. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 8. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 8. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-0 | 9. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-0 | No Parts for 9. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 IRO-002-0 was never enforceable
Inactive | IRO | IRO-002 | IRO-002-1 | 1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 1. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 2. | Each Reliability Coordinator shall determine the data requirements to support its reliability coordination tasks and shall request such data from its Transmission Operators, Balancing Authorities, Transmission Owners, Generation Owners, Generation Operators, and Load-Serving Entities, or adjacent Reliability Coordinators. | M1. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 2. |  | M1. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 3. | Each Reliability Coordinator - or its Transmission Operators and Balancing Authorities - shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 3. |  | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 4. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 4. |  | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 5. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 5. |  | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 6. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 6. |  | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 7. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, pre- and post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays. | M6. The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 7. |  | M6. The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 8. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. | M3. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that when responding to a Reliability Adjustment Arranged Interchange, it either approved the request or denied the request. | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 8. |  | M3. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that when responding to a Reliability Adjustment Arranged Interchange, it either approved the request or denied the request. | Operations Planning, Real-Time Operations, Same-Day Operations | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-1 | 9. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-1 | No Parts for 9. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-002 | IRO-002-2 | 1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. | M1. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, a document that lists its voice communications facilities with Transmission Operators, Balancing Authorities and Generator Operators within its Reliability Coordinator Area and with neighboring Reliability Coordinators, that will be used to confirm that it has communication facilities in accordance with Requirements 1 and 3. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, a document that lists its voice communications facilities with Transmission Operators, Balancing Authorities and Generator Operators within its Reliability Coordinator Area and with neighboring Reliability Coordinators, that will be used to confirm that it has communication facilities in accordance with Requirements 1 and 3. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 2. | Each Reliability Coordinator — or its Transmission Operators and Balancing Authorities — shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. |  | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 2. |  |  | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 3. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. | M3. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection system communications performance or equivalent evidence to demonstrate that it has real-time monitoring capability of its Reliability Coordinator Area and monitoring capability of its surrounding Reliability Coordinator Areas to identify potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection system communications performance or equivalent evidence to demonstrate that it has real-time monitoring capability of its Reliability Coordinator Area and monitoring capability of its surrounding Reliability Coordinator Areas to identify potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 4. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. | M4. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, documentation from suppliers, operating and planning staff training documents, examples of studies, or other equivalent evidence to show that it has analysis tools in accordance with Requirement 6. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, documentation from suppliers, operating and planning staff training documents, examples of studies, or other equivalent evidence to show that it has analysis tools in accordance with Requirement 6. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 5. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 5. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 6. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, pre- and post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays. |  | Operations Planning, Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 6. |  |  | Operations Planning, Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 7. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. |  | Operations Planning | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 7. |  |  | Operations Planning | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-2 | 8. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. |  | Operations Planning | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-2 | No Parts for 8. |  |  | Operations Planning | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-002 | IRO-002-3 | 1. | Each Reliability Coordinator shall provide its System Operators with the authority to approve, deny or cancel planned outages of its own analysis tools. | M1. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve, deny or cancel planned outages of its own analysis tools. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-3 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve, deny or cancel planned outages of its own analysis tools. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-002 | IRO-002-3 | 2. | Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | M2. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that that the Reliability Coordinator has procedures in place to mitigate the effects of analysis tool outages. (R2) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-3 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that that the Reliability Coordinator has procedures in place to mitigate the effects of analysis tool outages. (R2) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-002 | IRO-002-4 | 1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Reliability Coordinator shall have and provide upon request, evidence that could include but is not limited to a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-4 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have and provide upon request, evidence that could include but is not limited to a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-002 | IRO-002-4 | 2. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities | M2. Each Reliability Coordinator shall have and provide upon request evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-4 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have and provide upon request evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-002 | IRO-002-4 | 3. | Each Reliability Coordinator shall monitor Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-4 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-002 | IRO-002-4 | 4. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | The Reliability Coordinator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-4 | No Parts for 4. |  | The Reliability Coordinator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2017-09-30 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-002 | IRO-002-5 | 1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | M1. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-5 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000
Inactive | IRO | IRO-002 | IRO-002-5 | 2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. [Violation Risk Factor: | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-5 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000
Inactive | IRO | IRO-002 | IRO-002-5 | 3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-5 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000
Inactive | IRO | IRO-002 | IRO-002-5 | 4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-5 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000
Inactive | IRO | IRO-002 | IRO-002-5 | 5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-5 | No Parts for 5. |  | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000
Inactive | IRO | IRO-002 | IRO-002-5 | 6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | M6. The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-5 | No Parts for 6. |  | M6. The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2017-02-09 | 2017-03-06 | 2017-04-17 | 2017-04-17 | 2017-10-01 |  |  |  |  | 2019-12-31 | Filing/Order Docket No. RD17-4-000
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7. | Each Reliability Coordinator shall, in coordination with other Reliability Coordinators, develop a common Interconnection-wide methodology to determine the modeling and monitoring of BES and non-BES Elements that are internal and external to its Reliability Coordinator Area, necessary for providing operational awareness of the impacts on Bulk Electric System Facilities within its Reliability Coordinator Area, including at a minimum: | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7.1. | A method for development, maintenance, and periodic review of a Western Interconnection-wide reference model to serve as the baseline from which Reliability Coordinator’s operational models are derived | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 | 2019-07-11 |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7.2. | The impacts of Inter-area oscillations; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 | 2020-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7.3. | A method to determine Contingencies included in analyses and assessments; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 | 2020-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7.4. | A method to determine Remedial Action Schemes included in analyses and assessments; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 | 2020-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7.5. | A method to determine forecast data included in analyses and assessments; and | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 | 2020-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.7.6. | A method for the validation and periodic review of the Reliability Coordinator’s operational model for steady state and dynamic/oscillatory system response. | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 | 2020-01-01 |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | D.A.8. | Each Reliability Coordinator shall use the methodology developed in D.A.7. | M.D.A.8. Each Reliability Coordinator will have evidence that it uses the methodology developed in D.A.7., as required in D.A.8. above. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for D.A.8. |  | M.D.A.8. Each Reliability Coordinator will have evidence that it uses the methodology developed in D.A.7., as required in D.A.8. above. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Inactive | IRO | IRO-002 | IRO-002-6 | 1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | M1. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, a document that lists its data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Inactive | IRO | IRO-002 | IRO-002-6 | 2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Inactive | IRO | IRO-002 | IRO-002-6 | 3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Inactive | IRO | IRO-002 | IRO-002-6 | 4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Inactive | IRO | IRO-002 | IRO-002-6 | 5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for 5. |  | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Inactive | IRO | IRO-002 | IRO-002-6 | 6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | M6. The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000 | [13 empty] | RC
Inactive | IRO | IRO-002 | IRO-002-6 | No Parts for 6. |  | M6. The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2019-05-09 | 2019-05-30 | 2019-07-11 | 2019-07-11 | 2020-01-01 |  |  |  |  | 2021-03-31 | Filing/Order Docket No.RD19-6-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7. | Each Reliability Coordinator shall, in coordination with other Reliability Coordinators, develop a common Interconnection-wide methodology to determine the modeling and monitoring of BES and non-BES Elements that are internal and external to its Reliability Coordinator Area, necessary for providing operational awareness of the impacts on Bulk Electric System Facilities within its Reliability Coordinator Area, including at a minimum: | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7.1. | A method for development, maintenance, and periodic review of a Western Interconnection-wide reference model to serve as the baseline from which Reliability Coordinator’s operational models are derived; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7.2. | The impacts of Inter-area oscillations; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7.3. | A method to determine Contingencies included in analyses and assessments; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7.4. | A method to determine Remedial Action Schemes included in analyses and assessments; | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7.5. | A method to determine forecast data included in analyses and assessments; and | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.7.6. | A method for the validation and periodic review of the Reliability Coordinator’s operational model for steady state and dynamic/oscillatory system response. | M.D.A.7. Each Reliability Coordinator will have evidence that it developed a common Western Interconnection-wide methodology, addressing modeling and monitoring, in coordination with other Reliability Coordinators, that includes the features required in D.A.7. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | 2021-04-01 |  |  |  |  | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | D.A.8. | Each Reliability Coordinator shall use the methodology developed in D.A.7. | Each Reliability Coordinator will have evidence that it uses the methodology developed in D.A.7., as required in D.A.8. above. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for D.A.8. |  | Each Reliability Coordinator will have evidence that it uses the methodology developed in D.A.7., as required in D.A.8. above. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | 1. | Reserved. | Reserved |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for 1. |  | Reserved |  | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | 2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, as specified in the requirement. | Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | 3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R3. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | Operations Planning | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | 4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have, and provide upon request evidence that could include, but is not limited to, a documented procedure or equivalent evidence that will be used to confirm that the Reliability Coordinator has provided its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | 5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for 5. |  | M5. Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | 6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002 | IRO-002-7 | No Parts for 6. |  | The Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitoring systems consistent with the requirement. | Real-Time Operations | 2019-05-09 | 2019-06-07 | 2020-09-17 | 2020-09-17 | 2021-04-01 | [5 empty] | Filing/Order Docket No. RM19-16-000
Inactive | IRO | IRO-003 | IRO-003-0 | 1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with IRO-003-1 (IRO-003-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-0 | No Parts for 1. |  |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with IRO-003-1 (IRO-003-0 was never enforceable)
Inactive | IRO | IRO-003 | IRO-003-0 | 2. | When a Reliability Coordinator is aware of an operational concern, such as declining voltages, excessive reactive flows, or an IROL violation, in a neighboring Reliability Coordinator Area, it shall contact the Reliability Coordinator in whose area the operational concern was observed. The two Reliability Coordinators shall coordinate any actions, including emergency assistance, required to mitigate the operational concern. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with IRO-003-1 (IRO-003-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with IRO-003-1 (IRO-003-0 was never enforceable)
Inactive | IRO | IRO-003 | IRO-003-0 | 3. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with IRO-003-1 (IRO-003-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2006-08-01 | Replaced with IRO-003-1 (IRO-003-0 was never enforceable)
Inactive | IRO | IRO-003 | IRO-003-1 | 1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-1 | No Parts for 1. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-003 | IRO-003-1 | 2. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | [7 empty] | 2007-01-01 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-003 | IRO-003-2 | 1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors adjacent Reliability Coordinator Areas as necessary to ensure that, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-2 | No Parts for 1. |  | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors adjacent Reliability Coordinator Areas as necessary to ensure that, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-003 | IRO-003-2 | 2. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000 | [13 empty] | RC
Inactive | IRO | IRO-003 | IRO-003-2 | No Parts for 2. |  |  |  | 2006-11-01 | 2006-11-15 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM06-16-000, RM07-3-000
Inactive | IRO | IRO-004 | IRO-004-0 | 1. | Each Reliability Coordinator shall conduct next-day reliability analyses for its Reliability Coordinator Area to ensure that the Bulk Electric System can be operated reliably in anticipated normal and Contingency event conditions. The Reliability Coordinator shall conduct Contingency analysis studies to identify potential interface and other SOL and IROL violations, including overloaded transmission lines and transformers, voltage and stability limits, etc. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 1. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 2. | Each Reliability Coordinator shall pay particular attention to parallel flows to ensure one Reliability Coordinator Area does not place an unacceptable or undue Burden on an adjacent Reliability Coordinator Area. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 3. | Each Reliability Coordinator shall, in conjunction with its Transmission Operators and Balancing Authorities, develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or curtailment of Interchange Transactions, or reducing load to return transmission loading to within acceptable SOLs or IROLs. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 4. | Each Transmission Operator, Balancing Authority, Transmission Owner, Generator Owner, Generator Operator, and Load-Serving Entity in the Reliability Coordinator Area shall provide information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions. This information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | BA |  |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 4. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 5. | Each Reliability Coordinator shall share the results of its system studies, when conditions warrant or upon request, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers within its Reliability Coordinator Area. The Reliability Coordinator shall make study results available no later than 1500 Central Standard Time for the Eastern Interconnection and 1500 Pacific Standard Time for the Western Interconnection, unless circumstances warrant otherwise. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 5. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 6. | When conditions warrant, the Reliability Coordinator shall initiate a conference call or other appropriate communications to address the results of its reliability analyses. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 6. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 7. | If the results of these studies indicate potential SOL or IROL violations, the Reliability Coordinator shall issue the appropriate alerts via the Reliability Coordinator Information System (RCIS) and direct its Transmission Operators, Balancing Authorities and Transmission Service Providers to take any necessary action the Reliability Coordinator deems appropriate to address the potential SOL or IROL violation. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 7. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-0 | 8. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable) | BA | [19 empty] | TOP |  | TSP
Inactive | IRO | IRO-004 | IRO-004-0 | No Parts for 8. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-004-1 (IRO-004-0 was never enforceable)
Inactive | IRO | IRO-004 | IRO-004-1 | 1. | Each Reliability Coordinator shall conduct next-day reliability analyses for its Reliability Coordinator Area to ensure that the Bulk Electric System can be operated reliably in anticipated normal and Contingency event conditions. The Reliability Coordinator shall conduct Contingency analysis studies to identify potential interface and other SOL and IROL violations, including overloaded transmission lines and transformers, voltage and stability limits, etc. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 1. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-1 | 2. | Each Reliability Coordinator shall pay particular attention to parallel flows to ensure one Reliability Coordinator Area does not place an unacceptable or undue Burden on an adjacent Reliability Coordinator Area. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-1 | 3. | Each Reliability Coordinator shall, in conjunction with its Transmission Operators and Balancing Authorities, develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or curtailment of Interchange Transactions, or reducing load to return transmission loading to within acceptable SOLs or IROLs. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 3. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-1 | 4. | Each Transmission Operator, Balancing Authority, Transmission Owner, Generator Owner, Generator Operator, and Load-Serving Entity in the Reliability Coordinator Area shall provide information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions. This information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | BA |  |  |  | GO |  | GOP |  |  | LSE | [9 empty] | TO | TOP
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 4. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-1 | 5. | Each Reliability Coordinator shall share the results of its system studies, when conditions warrant or upon request, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers within its Reliability Coordinator Area. The Reliability Coordinator shall make study results available no later than 1500 Central Standard Time for the Eastern Interconnection and 1500 Pacific Standard Time for the Western Interconnection, unless circumstances warrant otherwise. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 5. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-1 | 6. | If the results of these studies indicate potential SOL or IROL violations, the Reliability Coordinator shall direct its Transmission Operators, Balancing Authorities and Transmission Service Providers to take any necessary action the Reliability Coordinator deems appropriate to address the potential SOL or IROL violation. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 6. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-1 | 7. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000 | BA | [19 empty] | TOP |  | TSP
Inactive | IRO | IRO-004 | IRO-004-1 | No Parts for 7. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-004 | IRO-004-2 | 1. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. | M1. None |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [19 empty] | TOP |  | TSP
Inactive | IRO | IRO-004 | IRO-004-2 | No Parts for 1. |  | M1. None |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-0 | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.10. | Contingency events. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.4. | System real and reactive reserves (actual versus required). |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.5. | Capacity and energy adequacy conditions. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.6. | Current ACE for all its Balancing Authorities. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.7. | Current local or Transmission Loading Relief procedures in effect. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.8. | Planned generation dispatches. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 1.9. | Planned transmission or generation outages. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | 2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 2. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those limits. If a potential or actual IROL violation cannot be avoided through proactive intervention, the Reliability Coordinator shall initiate control actions or emergency procedures to relieve the violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall ensure all resources, including load shedding, are available to address a potential or actual IROL violation. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 4. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 5. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 6. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 7. | The Reliability Coordinator shall participate in NERC hotline discussions, assist in the assessment of reliability of the overall interconnected system, and coordinate actions in anticipated or actual emergency situations. The Reliability Coordinator shall disseminate such information within its Reliability Coordinator Area, as required. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 7. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 8. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 9. | The Reliability Coordinator shall coordinate with other Reliability Coordinators and Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with other Reliability Coordinators and Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 9. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 10. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. If a Frequency Error, Time Error, or inadvertent problem occurs outside of the Reliability Coordinator Area, the Reliability Coordinator shall initiate a NERC hotline call to discuss the Frequency Error, Time Error, or Inadvertent Interchange with other Reliability Coordinators. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 11. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 12. | Whenever a Special Protection System that may have an inter-Balancing Authority, interTransmission Operator, or inter-Reliability Coordinator Area impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 12. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or nonaction in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 13. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 14. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area, and all impacted Reliability Coordinators within the Interconnection via the Reliability Coordinator Information System (RCIS) without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, and Reliability Coordinators when the transmission problem has been mitigated. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 15. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 16. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-0 | 17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-0 | No Parts for 17. |  |  |  | 2005-02-08 | [8 empty] | 2006-11-01 | Replaced with IRO-005-1 (IRO-005-0 was never enforceable)
Inactive | IRO | IRO-005 | IRO-005-1 | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.10. | Contingency events. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.4. | System real and reactive reserves (actual versus required). |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.5. | Capacity and energy adequacy conditions. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.6. | Current ACE for all its Balancing Authorities. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.7. | Current local or Transmission Loading Relief procedures in effect. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.8. | Planned generation dispatches. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 1.9. | Planned transmission or generation outages. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | 2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 2. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those limits. If a potential or actual IROL violation cannot be avoided through proactive intervention, the Reliability Coordinator shall initiate control actions or emergency procedures to relieve the violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall ensure all resources, including load shedding, are available to address a potential or actual IROL violation. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 3. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 4. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 5. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 6. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 7. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 7. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 8. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 9. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real-time and next-day reliability analysis timeframes. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 9. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 10. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 11. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 12. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 12. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or non-action in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | RC | [6 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 13. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC | [8 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 14. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 15. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 16. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-1 | 17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-1 | No Parts for 17. |  |  |  | 2006-02-07 | 2006-04-04 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-01-21 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-005 | IRO-005-2 | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.10. | Contingency events. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.4. | System real and reactive reserves (actual versus required). |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.5. | Capacity and energy adequacy conditions. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.6. | Current ACE for all its Balancing Authorities. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.7. | Current local or Transmission Loading Relief procedures in effect. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.8. | Planned generation dispatches. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 1.9. | Planned transmission or generation outages. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | 2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 2. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those limits. If a potential or actual IROL violation cannot be avoided through proactive intervention, the Reliability Coordinator shall initiate control actions or emergency procedures to relieve the violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall ensure all resources, including load shedding, are available to address a potential or actual IROL violation. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 3. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 4. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 5. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 6. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 7. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 7. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 8. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 9. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 9. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 10. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 11. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 12. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 12. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or nonaction in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | RC | [6 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 13. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC | [8 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 14. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 15. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 16. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2 | 17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2 | No Parts for 17. |  |  |  | 2006-11-01 | 2008-07-28 | 2009-01-22 | 2009-01-22 | 2009-01-22 |  |  |  |  | 2011-05-25 | Filing/Order Docket No. RM08-17-000
Inactive | IRO | IRO-005 | IRO-005-2a | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.10. | Contingency events. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.4. | System real and reactive reserves (actual versus required). |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.5. | Capacity and energy adequacy conditions. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.6. | Current ACE for all its Balancing Authorities. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.7. | Current local or Transmission Loading Relief procedures in effect. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.8. | Planned generation dispatches. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 1.9. | Planned transmission or generation outages. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 | 2011-05-26 |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | 2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 2. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 3. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 4. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 5. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 6. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 7. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 7. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 8. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 9. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 9. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 10. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 11. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 12. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 12. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or non-action in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | RC | [6 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 13. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC | [8 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 14. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 15. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 16. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-2a | 17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-2a | No Parts for 17. |  |  |  | 2009-11-05 | 2009-11-24 | 2011-04-21 | 2011-05-26 | 2011-05-26 |  |  |  |  | 2011-09-30 | Filing/Order Docket No. RM10-8-000
Inactive | IRO | IRO-005 | IRO-005-3 | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.10. | Contingency events. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.4. | System real and reactive reserves (actual versus required). | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.5. | Capacity and energy adequacy conditions. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.6. | Current ACE for all its Balancing Authorities. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.7. | Current local or Transmission Loading Relief procedures in effect. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.8. | Planned generation dispatches. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 1.9. | Planned transmission or generation outages. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | 2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | If one of its Balancing Authorities has insufficient operating reserves, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to computer printouts, operating logs, voice recordings or transcripts of voice recordings, or equivalent evidence that will be used to determine if the Reliability Coordinator directed and, if needed, assisted the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. (Requirement 2 and Requirement 7) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 2. |  | If one of its Balancing Authorities has insufficient operating reserves, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to computer printouts, operating logs, voice recordings or transcripts of voice recordings, or equivalent evidence that will be used to determine if the Reliability Coordinator directed and, if needed, assisted the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. (Requirement 2 and Requirement 7) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to determine if it informed Transmission Operators and Balancing Authorities of Geo-Magnetic Disturbance (GMD) forecast information and provided assistance as needed in the development of any required response plans. (Requirement 3) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 3. |  | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to determine if it informed Transmission Operators and Balancing Authorities of Geo-Magnetic Disturbance (GMD) forecast information and provided assistance as needed in the development of any required response plans. (Requirement 3) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it disseminated information within its Reliability Coordinator Area in accordance with Requirement 4. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 4. |  | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it disseminated information within its Reliability Coordinator Area in accordance with Requirement 4. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, computer printouts, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it monitored system frequency and Balancing Authority performance and directed any necessary rebalancing, as specified in Requirement 5 Part 1. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 5. |  | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, computer printouts, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it monitored system frequency and Balancing Authority performance and directed any necessary rebalancing, as specified in Requirement 5 Part 1. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | The Transmission Operators and Balancing Authorities shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it utilized all resources, including firm load shedding, as directed by its Reliability Coordinator, to relieve an emergent condition. (Requirement 5 Part 2) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 6. |  | The Transmission Operators and Balancing Authorities shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it utilized all resources, including firm load shedding, as directed by its Reliability Coordinator, to relieve an emergent condition. (Requirement 5 Part 2) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, operator logs or equivalent evidence that will be used to determine if it coordinated with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations including the coordination of pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities and Generator Operators. (Requirement 6 Part 1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 7. |  | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, operator logs or equivalent evidence that will be used to determine if it coordinated with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations including the coordination of pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities and Generator Operators. (Requirement 6 Part 1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | If a large Area Control Error has occurred, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it identified sources of the Area Control Errors, and initiated corrective actions with the appropriate Balancing Authority if the problem was within the Reliability Coordinator’s Area (Requirement 8 Part 1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 8. |  | If a large Area Control Error has occurred, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it identified sources of the Area Control Errors, and initiated corrective actions with the appropriate Balancing Authority if the problem was within the Reliability Coordinator’s Area (Requirement 8 Part 1) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | If a Special Protection System is armed and that system could have had an inter-area impact, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, agreements with their Transmission Operators, procedural documents, operator logs, computer analysis, training modules, training records or equivalent evidence that will be used to confirm that it was aware of the impact of that Special Protection System on inter-area flows. (Requirement 9) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 9. |  | If a Special Protection System is armed and that system could have had an inter-area impact, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, agreements with their Transmission Operators, procedural documents, operator logs, computer analysis, training modules, training records or equivalent evidence that will be used to confirm that it was aware of the impact of that Special Protection System on inter-area flows. (Requirement 9) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | If there is an instance where there is a disagreement on a derived limit, the Transmission Operator, Balancing Authority, Generator Operator, Load-serving Entity, Purchasing-selling Entity and Transmission Service Provider involved in the disagreement shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications or equivalent evidence that will be used to determine if it operated to the most limiting parameter. (Part 2 of Requirement 10) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 10. |  | If there is an instance where there is a disagreement on a derived limit, the Transmission Operator, Balancing Authority, Generator Operator, Load-serving Entity, Purchasing-selling Entity and Transmission Service Provider involved in the disagreement shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications or equivalent evidence that will be used to determine if it operated to the most limiting parameter. (Part 2 of Requirement 10) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | The Transmission Service Providers shall have and provide upon request evidence that could include, but is not limited to, procedural documents, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it respected the SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes.(Requirement 11 Part 2) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [22 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 11. |  | The Transmission Service Providers shall have and provide upon request evidence that could include, but is not limited to, procedural documents, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it respected the SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes.(Requirement 11 Part 2) |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3 | 12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it issued alerts when it foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area, to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area as specified in Requirement 12 Part 1. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3 | No Parts for 12. |  | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it issued alerts when it foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area, to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area as specified in Requirement 12 Part 1. |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2011-05-25 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.10. | Contingency events. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.4. | System real and reactive reserves (actual versus required). | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.5. | Capacity and energy adequacy conditions. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.6. | Current ACE for all its Balancing Authorities. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.7. | Current local or Transmission Loading Relief procedures in effect. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.8. | Planned generation dispatches. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 1.9. | Planned transmission or generation outages. | M1. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, a prepared report specifically detailing compliance to each of the bullets in Requirement 1, EMS availability, SCADA data collection system communications performance or equivalent evidence that will be used to confirm that it monitors the Reliability Coordinator Area parameters specified in Requirements 1.1 through 1.9. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | 2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | M2. If one of its Balancing Authorities has insufficient operating reserves, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to computer printouts, operating logs, voice recordings or transcripts of voice recordings, or equivalent evidence that will be used to determine if the Reliability Coordinator directed and, if needed, assisted the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. (Requirement 2 and Requirement 7) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 2. |  | M2. If one of its Balancing Authorities has insufficient operating reserves, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to computer printouts, operating logs, voice recordings or transcripts of voice recordings, or equivalent evidence that will be used to determine if the Reliability Coordinator directed and, if needed, assisted the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. (Requirement 2 and Requirement 7) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | M3. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to determine if it informed Transmission Operators and Balancing Authorities of Geo-Magnetic Disturbance (GMD) forecast information and provided assistance as needed in the development of any required response plans. (Requirement 3) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 3. |  | M3. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to determine if it informed Transmission Operators and Balancing Authorities of Geo-Magnetic Disturbance (GMD) forecast information and provided assistance as needed in the development of any required response plans. (Requirement 3) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | M4. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it disseminated information within its Reliability Coordinator Area in accordance with Requirement 4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 4. |  | M4. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it disseminated information within its Reliability Coordinator Area in accordance with Requirement 4. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | M5. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, computer printouts, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it monitored system frequency and Balancing Authority performance and directed any necessary rebalancing, as specified in Requirement 5 Part 1. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 5. |  | M5. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, computer printouts, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it monitored system frequency and Balancing Authority performance and directed any necessary rebalancing, as specified in Requirement 5 Part 1. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | M6. The Transmission Operators and Balancing Authorities shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it utilized all resources, including firm load shedding, as directed by its Reliability Coordinator, to relieve an emergent condition. (Requirement 5 Part 2) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 6. |  | M6. The Transmission Operators and Balancing Authorities shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it utilized all resources, including firm load shedding, as directed by its Reliability Coordinator, to relieve an emergent condition. (Requirement 5 Part 2) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | M7. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, operator logs or equivalent evidence that will be used to determine if it coordinated with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations including the coordination of pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities and Generator Operators. (Requirement 6 Part 1) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 7. |  | M7. The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, operator logs or equivalent evidence that will be used to determine if it coordinated with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations including the coordination of pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities and Generator Operators. (Requirement 6 Part 1) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | M8. If a large Area Control Error has occurred, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it identified sources of the Area Control Errors, and initiated corrective actions with the appropriate Balancing Authority if the problem was within the Reliability Coordinator’s Area (Requirement 8 Part 1) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 8. |  | M8. If a large Area Control Error has occurred, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, Hot Line recordings, electronic communications or equivalent evidence that will be used to determine if it identified sources of the Area Control Errors, and initiated corrective actions with the appropriate Balancing Authority if the problem was within the Reliability Coordinator’s Area (Requirement 8 Part 1) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | M9. If a Special Protection System is armed and that system could have had an inter-area impact, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, agreements with their Transmission Operators, procedural documents, operator logs, computer analysis, training modules, training records or equivalent evidence that will be used to confirm that it was aware of the impact of that Special Protection System on inter-area flows. (Requirement 9) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 9. |  | M9. If a Special Protection System is armed and that system could have had an inter-area impact, the Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, agreements with their Transmission Operators, procedural documents, operator logs, computer analysis, training modules, training records or equivalent evidence that will be used to confirm that it was aware of the impact of that Special Protection System on inter-area flows. (Requirement 9) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | If there is an instance where there is a disagreement on a derived limit, the Transmission Operator, Balancing Authority, Generator Operator, Load-serving Entity, Purchasing-selling Entity and Transmission Service Provider involved in the disagreement shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications or equivalent evidence that will be used to determine if it operated to the most limiting parameter. (Requirement 10) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 10. |  | If there is an instance where there is a disagreement on a derived limit, the Transmission Operator, Balancing Authority, Generator Operator, Load-serving Entity, Purchasing-selling Entity and Transmission Service Provider involved in the disagreement shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications or equivalent evidence that will be used to determine if it operated to the most limiting parameter. (Requirement 10) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | The Transmission Service Providers shall have and provide upon request evidence that could include, but is not limited to, procedural documents, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it respected the SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes.(Requirement 11) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [22 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 11. |  | The Transmission Service Providers shall have and provide upon request evidence that could include, but is not limited to, procedural documents, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it respected the SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes.(Requirement 11) |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1a | 12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it issued alerts when it foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area, to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area as specified in Requirement 12 Part 1. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1a | No Parts for 12. |  | The Reliability Coordinator shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications or equivalent evidence that will be used to confirm that it issued alerts when it foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area, to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area as specified in Requirement 12 Part 1. |  | 2012-03-08 | 2012-06-05 | 2012-09-13 | 2012-09-13 | 2012-09-13 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RD12-4-000
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Remedial Action Schemes) and system loading. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.10. | Contingency events. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.4. | System real and reactive reserves (actual versus required). |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.5. | Capacity and energy adequacy conditions. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.6. | Current ACE for all its Balancing Authorities. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.7. | Current local or Transmission Loading Relief procedures in effect. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.8. | Planned generation dispatches. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 1.9. | Planned transmission or generation outages. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 2. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 3. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 4. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 5. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 6. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 7. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 8. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 9. | Whenever a Remedial Action Scheme that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Remedial Action Scheme on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Remedial Action Scheme including any degradation or potential failure to operate as expected. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 9. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 10. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [22 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 11. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | 12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval. | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3.1(i)a | No Parts for 12. |  |  |  | 2014-11-13 | [8 empty] | 2014-11-13 | Version developed but never filed for approval.
Inactive | IRO | IRO-005 | IRO-005-3a | 1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.10. | Contingency events. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.4. | System real and reactive reserves (actual versus required). |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.5. | Capacity and energy adequacy conditions. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.6. | Current ACE for all its Balancing Authorities. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.7. | Current local or Transmission Loading Relief procedures in effect. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.8. | Planned generation dispatches. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 1.9. | Planned transmission or generation outages. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | 2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 2. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 3. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 4. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 5. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 6. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 7. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 8. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 9. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA | [5 empty] | GOP |  |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 10. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [22 empty] | TSP
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 11. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-3a | 12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-3a | No Parts for 12. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2012-09-12 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-005 | IRO-005-4 | 1. | When the results of an Operational Planning Analysis or Real-time Assessment indicate an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area, each Reliability Coordinator shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | M1. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to dated operator logs, dated voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it notified all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when it identified an anticipated or actual condition with Adverse Reliability Impacts, within its Reliability Coordinator Area. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-4 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to dated operator logs, dated voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it notified all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when it identified an anticipated or actual condition with Adverse Reliability Impacts, within its Reliability Coordinator Area. (R1) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-005 | IRO-005-4 | 2. | Each Reliability Coordinator that identifies an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when the problem has been mitigated. | M2. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to dated operator logs, dated voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it notified all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area had been mitigated. (R2) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000 | [13 empty] | RC
Inactive | IRO | IRO-005 | IRO-005-4 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have and provide evidence which may include, but is not limited to dated operator logs, dated voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it notified all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area had been mitigated. (R2) | Operations Planning, Real-Time Operations, Same-Day Operations | 2011-08-04 | 2013-04-16 | [7 empty] | 2016-01-26 | Filing/Order Docket No. RM13-15-000
Inactive | IRO | IRO-006 | IRO-006-0 | 1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | No Parts for 1. |  |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-0 | 2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | 2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | 2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001- clean_8-8-03.pdf. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | 2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotoc ols.htm. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | 3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | No Parts for 3. |  |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-0 | 4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | No Parts for 4. |  |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-0 | 5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | No Parts for 5. |  |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-0 | 6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable) | BA | [12 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-0 | No Parts for 6. |  |  |  | 2005-02-08 | [8 empty] | 2005-08-08 | Replaced with IRO-006-1 (IRO-006-0 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-1 | 1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | No Parts for 1. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable
Inactive | IRO | IRO-006 | IRO-006-1 | 2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | 2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | 2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001- clean_8-8-03.pdf. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | 2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotoc ols.htm. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | 3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | No Parts for 3. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable
Inactive | IRO | IRO-006 | IRO-006-1 | 4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | No Parts for 4. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable
Inactive | IRO | IRO-006 | IRO-006-1 | 5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | No Parts for 5. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable
Inactive | IRO | IRO-006 | IRO-006-1 | 6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable | BA | [12 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-1 | No Parts for 6. |  |  |  | 2005-02-08 | 2006-04-04 | [7 empty] | 2006-09-29 | Filing/Order Docket No. RM06-16-000 IRO-006-1 was never enforceable
Inactive | IRO | IRO-006 | IRO-006-2 | 1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | No Parts for 1. |  |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-2 | 2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | 2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | 2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001 -clean_8-8-03.pdf. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | 2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotp rotocols.htm. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | 3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | No Parts for 3. |  |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-2 | 4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | No Parts for 4. |  |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-2 | 5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | No Parts for 5. |  |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-2 | 6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable) | BA | [12 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-2 | No Parts for 6. |  |  |  | 2006-08-02 | [8 empty] | 2006-09-29 | Replaced with IRO-006-3 (IRO-006-2 was never enforceable)
Inactive | IRO | IRO-006 | IRO-006-3 | 1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | No Parts for 1. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | IRO | IRO-006 | IRO-006-3 | 2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | 2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | 2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_ mitigation_plan _rev_2001-clean_8-8-03.pdf. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | 2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 | 2007-06-18 |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | 3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | No Parts for 3. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | IRO | IRO-006 | IRO-006-3 | 4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | No Parts for 4. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | IRO | IRO-006 | IRO-006-3 | 5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | No Parts for 5. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | IRO | IRO-006 | IRO-006-3 | 6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000 | BA | [12 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-3 | No Parts for 6. |  |  |  | 2006-08-02 | 2006-08-28 | 2007-03-16 | 2007-06-18 | 2007-06-18 |  |  |  |  | 2009-04-22 | Filing/Order Docket No. RM06-16-000, RM06-22-000
Inactive | IRO | IRO-006 | IRO-006-4 | 1. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, with its authority and at its discretion, select one or more procedures to provide transmission loading relief. These procedures can be a ?local? (regional, interregional, or sub-regional) transmission loading relief procedure or one of the following Interconnection-wide procedures: [Time Horizon: Real-time Operations] |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | 1.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 | 2009-04-23 |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | 1.2. | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is WECC-IRO-STD-006-0 provided at: ftp://www.nerc.com/pub/sys/all_updl/standards/rrs/IRO-STD-006- 0_17Jan07.pdf. |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 | 2009-04-23 |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | 1.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/mktrules/protocols/current.html |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 | 2009-04-23 |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | 2. | The Reliability Coordinator shall only use local transmission loading relief or congestion management procedures to which the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party. [Time Horizon: Operations Planning] | M1. Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented in accordance with Requirement R1. | Real-Time Operations | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | No Parts for 2. |  | M1. Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented in accordance with Requirement R1. | Real-Time Operations | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000
Inactive | IRO | IRO-006 | IRO-006-4 | 3. | Each Reliability Coordinator with a relief obligation from an Interconnection-wide procedure shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall obtain prior approval of the local procedure from the ERO. [Time Horizon: Operations Planning] | M2. Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that within fifteen minutes of the receipt of a request, the Reliability Coordinator complied with the request by either 1) instructing the Sink Balancing Authority to implement the congestion management actions requested by the issuing Reliability Coordinator, or 2) instructing the Sink Balancing Authority to implement none or some of the communicated congestion management actions requested by the issuing Reliability Coordinator, and replacing the remainder with alternate congestion management actions if assessment showed that some or all of the requested congestion management actions would have resulted in a reliability concern or would have been ineffective in accordance with Requirement R2. | Real-Time Operations | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | No Parts for 3. |  | M2. Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that within fifteen minutes of the receipt of a request, the Reliability Coordinator complied with the request by either 1) instructing the Sink Balancing Authority to implement the congestion management actions requested by the issuing Reliability Coordinator, or 2) instructing the Sink Balancing Authority to implement none or some of the communicated congestion management actions requested by the issuing Reliability Coordinator, and replacing the remainder with alternate congestion management actions if assessment showed that some or all of the requested congestion management actions would have resulted in a reliability concern or would have been ineffective in accordance with Requirement R2. | Real-Time Operations | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000
Inactive | IRO | IRO-006 | IRO-006-4 | 4. | When Interconnection-wide procedures are implemented to curtail Interchange Transactions that cross an Interconnection boundary, each Reliability Coordinator shall comply with the provisions of the Interconnection-wide procedure. [Time Horizon: Real-time Operations] |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | No Parts for 4. |  |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000
Inactive | IRO | IRO-006 | IRO-006-4 | 5. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with applicable Interchange scheduling standards. [Time Horizon: Real-time Operations] |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000 | BA | [12 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4 | No Parts for 5. |  |  |  | 2007-10-09 | 2007-12-21 | 2009-03-19 | 2009-04-23 | 2009-04-23 |  |  |  |  | 2009-12-09 | Filing/Order Docket No. RM08-7-000
Inactive | IRO | IRO-006 | IRO-006-4.1 | 1. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, with its authority and at its discretion, select one or more procedures to provide transmission loading relief. These procedures can be a “local” (regional, interregional, or sub-regional) transmission loading relief procedure or one of the following Interconnection-wide procedures: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | 1.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | 1.2. | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the WECC Unscheduled Flow Reduction Procedure provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf. |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | 1.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/mktrules/protocols/current.html |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | 2. | The Reliability Coordinator shall only use local transmission loading relief or congestion management procedures to which the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] |  | Operations Planning | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | No Parts for 2. |  |  | Operations Planning | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000
Inactive | IRO | IRO-006 | IRO-006-4.1 | 3. | Each Reliability Coordinator with a relief obligation from an Interconnection-wide procedure shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall obtain prior approval of the local procedure from the ERO. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | M.D.A.8. Each Reliability Coordinator will have evidence that it uses the methodology developed in D.A.7., as required in D.A.8. above. | Operations Planning | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | No Parts for 3. |  | M.D.A.8. Each Reliability Coordinator will have evidence that it uses the methodology developed in D.A.7., as required in D.A.8. above. | Operations Planning | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000
Inactive | IRO | IRO-006 | IRO-006-4.1 | 4. | When Interconnection-wide procedures are implemented to curtail Interchange Transactions that cross an Interconnection boundary, each Reliability Coordinator shall comply with the provisions of the Interconnection-wide procedure. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | No Parts for 4. |  |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000
Inactive | IRO | IRO-006 | IRO-006-4.1 | 5. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with applicable Interchange scheduling standards. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000 | BA | [12 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-4.1 | No Parts for 5. |  |  |  | 2009-04-15 | 2009-08-12 | 2009-12-10 | 2009-12-10 | 2009-12-10 |  |  |  |  | 2011-06-30 | Filing/Order Docket No. RD09-9-000
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-5 | 1. | Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | M1. Each Reliability Coordinator and Balancing Authority shall provide evidence (such as dated logs, voice recordings, Tag histories, and studies, in electronic or hard copy format) that, when a request to curtail an Interchange Transaction crossing an Interconnection boundary pursuant to an Interconnection-wide transmission loading relief procedure was made from another Reliability Coordinator, Balancing Authority, or Transmission Operator in that other Interconnection, it complied with the request or provided a reliability reason why it could not comply with the request | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | [5 empty] | Filing/Order Docket No. RM06-16-000 | BA | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-5 | No Parts for 1. |  | M1. Each Reliability Coordinator and Balancing Authority shall provide evidence (such as dated logs, voice recordings, Tag histories, and studies, in electronic or hard copy format) that, when a request to curtail an Interchange Transaction crossing an Interconnection boundary pursuant to an Interconnection-wide transmission loading relief procedure was made from another Reliability Coordinator, Balancing Authority, or Transmission Operator in that other Interconnection, it complied with the request or provided a reliability reason why it could not comply with the request | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | [5 empty] | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 1. | R1. When acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s TV, each Reliability Coordinator shall initiate, prior to or concurrently with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated), one or more of the following actions: • Inter-area redispatch of generation • Intra-area redispatch of generation • Reconfiguration of the transmission system • Voluntary load reductions (e.g., Demand-side Management) • Controlled load reductions (e.g., load shedding) | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that when acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s Tv, the Reliability Coordinator initiated one or more of the actions listed in R1 prior to or concurrently with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated)(R1). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 |  |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | No Parts for 1. |  | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that when acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s Tv, the Reliability Coordinator initiated one or more of the actions listed in R1 prior to or concurrently with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated)(R1). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 |  |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 2. | To ensure operating entities are provided with information needed to maintain an awareness of changes to the Transmission System, when initiating the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance, and at least every clock hour (with the exception of TLR-1, where an hourly update is not required) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0, the Reliability Coordinator shall identify: | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented (R2). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 |  |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 2.1. | A list of congestion management actions to be implemented, and | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented (R2). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | 2011-04-21 |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 2.2. | One of the following TLR levels: TLR-1, TLR-2, TLR-3A, TLR-3B, TLR-4, TLR-5A, TLR-5B, TLR-6, TLR-0 | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented (R2). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | 2011-04-21 |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 3. | Upon the identification of the TLR level and a list of congestion management actions to be implemented, the Reliability Coordinator initiating this TLR procedure shall: | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that after it identified a TLR level and a list of congestion management actions to take, it 1.) notified all Reliability Coordinators in the Eastern Interconnection of the TLR Level, 2.) communicated the list of actions to all Reliability Coordinators in the Eastern Interconnection and those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions, and 3.) requested the Reliability Coordinators identified in Requirement R3 Part 3.2 to implement the congestion management actions identified in Requirement R2 Part 2.1 (R3). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 |  |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 3.1. | Notify all Reliability Coordinators in the Eastern Interconnection of the identified TLR level | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that after it identified a TLR level and a list of congestion management actions to take, it 1.) notified all Reliability Coordinators in the Eastern Interconnection of the TLR Level, 2.) communicated the list of actions to all Reliability Coordinators in the Eastern Interconnection and those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions, and 3.) requested the Reliability Coordinators identified in Requirement R3 Part 3.2 to implement the congestion management actions identified in Requirement R2 Part 2.1 (R3). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | 2011-04-21 |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 3.2. | Communicate the list of congestion management actions to be implemented to 1.) all Reliability Coordinators in the Eastern Interconnection, and 2.) those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions. | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that after it identified a TLR level and a list of congestion management actions to take, it 1.) notified all Reliability Coordinators in the Eastern Interconnection of the TLR Level, 2.) communicated the list of actions to all Reliability Coordinators in the Eastern Interconnection and those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions, and 3.) requested the Reliability Coordinators identified in Requirement R3 Part 3.2 to implement the congestion management actions identified in Requirement R2 Part 2.1 (R3). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | 2011-04-21 |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 3.3. | Request that the congestion management actions identified in Requirement R2, Part 2.1 be implemented by: 1.) Each Reliability Coordinator associated with a Sink Balancing Authority for which Interchange Transactions are to be curtailed, 2.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which Network Integration Transmission Service or Native Load is to be curtailed, and 3.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which its Market Flow is to be curtailed. | Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that after it identified a TLR level and a list of congestion management actions to take, it 1.) notified all Reliability Coordinators in the Eastern Interconnection of the TLR Level, 2.) communicated the list of actions to all Reliability Coordinators in the Eastern Interconnection and those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions, and 3.) requested the Reliability Coordinators identified in Requirement R3 Part 3.2 to implement the congestion management actions identified in Requirement R2 Part 2.1 (R3). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 | 2011-04-21 |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | 4. | Each Reliability Coordinator that receives a request as described in Requirement R3, Part 3.3. shall, within 15 minutes of receiving the request, implement the congestion management actions requested by the issuing Reliability Coordinator as follows: • Instruct its Balancing Authorities to implement the Interchange Transaction schedule change requests. • Instruct its Balancing Authorities to implement the Network Integration Transmission Service and Native Load schedule changes for which the Balancing Authorities are responsible. • Instruct its Balancing Authorities to implement the Market Flow schedule changes for which the Balancing Authorities are responsible. • If an assessment determines shows that one or more of the congestion management actions communicated in Requirement R3, Part 3.3 will result in a reliability concern or will be ineffective, the Reliability Coordinator may replace those specific actions with alternate congestion management actions, provided that: o The alternate congestion management actions have been agreed to by the initiating Reliability Coordinator, and o The assessment shows that the alternate congestion management actions will not adversely affect reliability. | M4. Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that within fifteen minutes of the receipt of a request as described in R3, the Reliability Coordinator complied with the request by either 1.) implementing the communicated congestion management actions requested by the issuing Reliability Coordinator, or 2.) implementing none or some of the communicated congestion management actions requested by the issuing Reliability Coordinator, and replacing the remainder with alternate congestion management actions if assessment showed that some or all of the congestion management actions communicated in R3 would have resulted in a reliability concern or would have been ineffective, the alternate congestion management actions were agreed to by the initiating Reliability Coordinator, and assessment showed that the alternate congestion management actions would not adversely affect reliability (R4). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 |  |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-EAST-1 | No Parts for 4. |  | M4. Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that within fifteen minutes of the receipt of a request as described in R3, the Reliability Coordinator complied with the request by either 1.) implementing the communicated congestion management actions requested by the issuing Reliability Coordinator, or 2.) implementing none or some of the communicated congestion management actions requested by the issuing Reliability Coordinator, and replacing the remainder with alternate congestion management actions if assessment showed that some or all of the congestion management actions communicated in R3 would have resulted in a reliability concern or would have been ineffective, the alternate congestion management actions were agreed to by the initiating Reliability Coordinator, and assessment showed that the alternate congestion management actions would not adversely affect reliability (R4). | Real-Time Operations | 2010-11-04 | 2011-01-13 | 2011-04-21 | 2011-04-21 | 2011-07-01 |  |  |  |  | 2016-03-31 | Filing/Order Docket No. RM06-16-000
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-EAST-2 | 1. | Each Reliability Coordinator that initiates the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance shall identify the TLR level and the congestion management actions to be implemented, and shall update this information at least every clock hour (except TLR-1) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0. Footnote: For more information on TLR levels, please see “Implementation Guideline for Reliability Coordinators: Eastern Interconnection TLR Levels Reference Document.” | M1. Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented in accordance with Requirement R1. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-04-01 | [5 empty] | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-EAST-2 | No Parts for 1. |  | M1. Each Reliability Coordinator shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that at the time it initiated the Eastern Interconnection TLR procedure, and at least every clock hour after initiation up to and including the hour when the TLR level was identified as TLR Level 0, the Reliability Coordinator identified both the TLR Level and a list of congestion management actions to be implemented in accordance with Requirement R1. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-04-01 | [5 empty] | Filing/Order Docket No. RD15-7-000
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-EAST-2 | 2. | Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall, within 15 minutes of receiving the request from the issuing Reliability Coordinator, instruct the Sink Balancing Authority to implement the congestion management actions, subject to the following exception: . Should an assessment determine that one or more of the congestion management actions communicated will result in a reliablity concern or will be ineffective, the Reliability Coordinator with a Sink Balancing Authority shall coordinate alternate congestion management actions with the issuing Reliabiltiy Coordinator. | M2. Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that within fifteen minutes of the receipt of a request, the Reliability Coordinator complied with the request by either 1) instructing the Sink Balancing Authority to implement the congestion management actions requested by the issuing Reliability Coordinator, or 2) instructing the Sink Balancing Authority to implement none or some of the communicated congestion management actions requested by the issuing Reliability Coordinator, and replacing the remainder with alternate congestion management actions if assessment showed that some or all of the requested congestion management actions would have resulted in a reliability concern or would have been ineffective in accordance with Requirement R2. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-04-01 | [5 empty] | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-EAST-2 | No Parts for 2. |  | M2. Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall provide evidence (such as dated logs, voice recordings, or other information in electronic or hard-copy format) that within fifteen minutes of the receipt of a request, the Reliability Coordinator complied with the request by either 1) instructing the Sink Balancing Authority to implement the congestion management actions requested by the issuing Reliability Coordinator, or 2) instructing the Sink Balancing Authority to implement none or some of the communicated congestion management actions requested by the issuing Reliability Coordinator, and replacing the remainder with alternate congestion management actions if assessment showed that some or all of the requested congestion management actions would have resulted in a reliability concern or would have been ineffective in accordance with Requirement R2. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-04-01 | [5 empty] | Filing/Order Docket No. RD15-7-000
Inactive | IRO | IRO-006 | IRO-006-TRE-1 | 1. | The RC shall have procedures to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits (IROL) and System Operating Limits (SOL) that will not be resolved by the automatic actions of the ERCOT Nodal market operations system. The procedures shall address, but not be limited to, one or more of the following: redispatch of generation; reconfiguration of the Transmission system; controlled load reductions (including both firm and non-firm load shedding). |  | Operations Planning, Same-Day Operations | 2011-11-03 | 2012-02-01 | 2012-05-31 | 2012-05-31 | 2012-07-01 |  |  |  |  | 2019-01-29 | Filing/Order Docket No. RD12-1-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-TRE-1 | No Parts for 1. |  |  | Operations Planning, Same-Day Operations | 2011-11-03 | 2012-02-01 | 2012-05-31 | 2012-05-31 | 2012-07-01 |  |  |  |  | 2019-01-29 | Filing/Order Docket No. RD12-1-000
Inactive | IRO | IRO-006 | IRO-006-TRE-1 | 2. | The RC shall act to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits and System Operating Limits that will not be resolved by the automatic actions of the ERCOT Nodal market operations system, in accordance with the procedures required by R1. | M2. To demonstrate compliance with Requirement R2, the RC shall provide evidence, such as system logs, voice recordings, or operating messages that shows that it acted to identify and to mitigate exceedances of IROLs and SOLs in accordance with the procedures required by R1. | Operations Planning, Same-Day Operations | 2011-11-03 | 2012-02-01 | 2012-05-31 | 2012-05-31 | 2012-07-01 |  |  |  |  | 2019-01-29 | Filing/Order Docket No. RD12-1-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-TRE-1 | No Parts for 2. |  | M2. To demonstrate compliance with Requirement R2, the RC shall provide evidence, such as system logs, voice recordings, or operating messages that shows that it acted to identify and to mitigate exceedances of IROLs and SOLs in accordance with the procedures required by R1. | Operations Planning, Same-Day Operations | 2011-11-03 | 2012-02-01 | 2012-05-31 | 2012-05-31 | 2012-07-01 |  |  |  |  | 2019-01-29 | Filing/Order Docket No. RD12-1-000
Inactive | IRO | IRO-006 | IRO-006-WECC-1 | 1. | Upon receiving a request of Step 4 or greater (see Attachment 1-IRO-006-WECC-1) from the Transmission Operator of a Qualified Transfer Path, the Reliability Coordinator shall approve (actively or passively) or deny that request within five minutes. [Time Horizon: Real-time Operations] |  | Operations Planning, Same-Day Operations | 2009-02-10 | 2009-06-17 | 2011-03-17 | 2011-05-24 | 2011-07-01 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM09-19-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-WECC-1 | No Parts for 1. |  |  | Operations Planning, Same-Day Operations | 2009-02-10 | 2009-06-17 | 2011-03-17 | 2011-05-24 | 2011-07-01 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM09-19-000
Inactive | IRO | IRO-006 | IRO-006-WECC-1 | 2. | The Balancing Authorities shall approve curtailment requests to the schedules as submitted, implement alternative actions, or a combination there of that collectively meets the Relief Requirement.[Time Horizon: Real-time Operations] | M2. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it initiated one or more Operating Processes, Procedures or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirements R1) in accordance with Requirement R2. This evidence could include, but is not limited to, Operating Processes, Procedures, or Plans from Requirement R1, dated operating logs, dated voice recordings, dated transcripts of voice recordings, or other evidence. | Real-Time Operations | 2009-02-10 | 2009-06-17 | 2011-03-17 | 2011-05-24 | 2011-07-01 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM09-19-000 | BA
Inactive | IRO | IRO-006 | IRO-006-WECC-1 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it initiated one or more Operating Processes, Procedures or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirements R1) in accordance with Requirement R2. This evidence could include, but is not limited to, Operating Processes, Procedures, or Plans from Requirement R1, dated operating logs, dated voice recordings, dated transcripts of voice recordings, or other evidence. | Real-Time Operations | 2009-02-10 | 2009-06-17 | 2011-03-17 | 2011-05-24 | 2011-07-01 |  |  |  |  | 2014-06-30 | Filing/Order Docket No. RM09-19-000
Inactive | IRO | IRO-006 | IRO-006-WECC-2 | 1. | Each Reliability Coordinator shall approve or deny a request within five minutes of receiving the request for unscheduled flow transmission relief from the Transmission Operator of a Qualified Transfer Path that will result in the calculation of a Relief Requirement. | M1. The Reliability Coordinator shall have evidence that it approved or denied the request within five minutes of receiving a request for relief, in accordance with Requirement R1. Evidence may include, but is not limited to, documentation of either an active or passive approval. M1.1.1 Each Balancing Authority shall have evidence that it provided the Relief Requirement through Contributing Schedules curtailments, alternative actions, or a combination that collectively meets the Relief Requirement as directed in Requirement R.2. | Real-Time Operations | 2013-02-07 | 2013-12-20 | 2014-05-13 | 2014-07-01 | 2014-07-01 |  |  |  |  | 2019-09-30 | Filing/Order Docket No. RD14-9-000 | [13 empty] | RC
Inactive | IRO | IRO-006 | IRO-006-WECC-2 | No Parts for 1. |  | M1. The Reliability Coordinator shall have evidence that it approved or denied the request within five minutes of receiving a request for relief, in accordance with Requirement R1. Evidence may include, but is not limited to, documentation of either an active or passive approval. M1.1.1 Each Balancing Authority shall have evidence that it provided the Relief Requirement through Contributing Schedules curtailments, alternative actions, or a combination that collectively meets the Relief Requirement as directed in Requirement R.2. | Real-Time Operations | 2013-02-07 | 2013-12-20 | 2014-05-13 | 2014-07-01 | 2014-07-01 |  |  |  |  | 2019-09-30 | Filing/Order Docket No. RD14-9-000
Inactive | IRO | IRO-006 | IRO-006-WECC-2 | 2. | Each Balancing Authority shall perform any combination of the following actions meeting the Relief Requirement upon receiving a request for relief as described in Requirement R1: • Approve curtailment requests to the schedules as submitted • Implement alternative actions |  | Real-Time Operations | 2013-02-07 | 2013-12-20 | 2014-05-13 | 2014-07-01 | 2014-07-01 |  |  |  |  | 2019-09-30 | Filing/Order Docket No. RD14-9-000 | BA
Inactive | IRO | IRO-006 | IRO-006-WECC-2 | No Parts for 2. |  |  | Real-Time Operations | 2013-02-07 | 2013-12-20 | 2014-05-13 | 2014-07-01 | 2014-07-01 |  |  |  |  | 2019-09-30 | Filing/Order Docket No. RD14-9-000
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-WECC-3 | 1. | Each Reliability Coordinator receiving a request for Curtailments for unscheduled flow transmission relief on a Qualified Path within its Reliability Coordinator Area shall either approve or deny that request within five minutes of receipt. | M1. Each Reliability Coordinator receiving a request for Curtailments for unscheduled flow transmission relief on a Qualified Path within its Reliability Coordinator Area, per requirement R1, will have evidence that it approved or denied that request within five minutes of receipt. Evidence may include, but is not limited to documentation of either an active or passive approval. | Real-Time Operations | 2019-02-07 | 2019-03-06 | 2019-05-10 | 2019-05-10 | 2019-10-01 | [5 empty] | Filing/Order Docket No. RD19-4-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-WECC-3 | No Parts for 1. |  | M1. Each Reliability Coordinator receiving a request for Curtailments for unscheduled flow transmission relief on a Qualified Path within its Reliability Coordinator Area, per requirement R1, will have evidence that it approved or denied that request within five minutes of receipt. Evidence may include, but is not limited to documentation of either an active or passive approval. | Real-Time Operations | 2019-02-07 | 2019-03-06 | 2019-05-10 | 2019-05-10 | 2019-10-01 | [5 empty] | Filing/Order Docket No. RD19-4-000
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-WECC-3 | 2. | Each Balancing Authority receiving an approved request for unscheduled flow transmission relief on a Qualified Path per Requirement R1, shall perform any of the following actions to meet that request: • Approve curtailment requests to the schedules as submitted • Implement alternative actions | M2. Each Balancing Authority receiving an approved request for unscheduled flow transmission relief on a Qualified Path per Requirement R1, will have evidence that it performed the actions allowed in Requirement R2, to meet that request. | Real-Time Operations | 2019-02-07 | 2019-03-06 | 2019-05-10 | 2019-05-10 | 2019-10-01 | [5 empty] | Filing/Order Docket No. RD19-4-000 | BA
Mandatory Subject to Enforcement | IRO | IRO-006 | IRO-006-WECC-3 | No Parts for 2. |  | M2. Each Balancing Authority receiving an approved request for unscheduled flow transmission relief on a Qualified Path per Requirement R1, will have evidence that it performed the actions allowed in Requirement R2, to meet that request. | Real-Time Operations | 2019-02-07 | 2019-03-06 | 2019-05-10 | 2019-05-10 | 2019-10-01 | [5 empty] | Filing/Order Docket No. RD19-4-000
Inactive | IRO | IRO-008 | IRO-008-1 | 1. | Each Reliability Coordinator shall perform an Operational Planning Analysis to assess whether the planned operations for the next day within its Wide Area, will exceed any of its Interconnection Reliability Operating Limits (IROLs) during anticipated normal and Contingency event conditions. | M1. The Reliability Coordinator shall have, and make available upon request, the results of its Operational Planning Analyses. | Operations Planning | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-1 | No Parts for 1. |  | M1. The Reliability Coordinator shall have, and make available upon request, the results of its Operational Planning Analyses. | Operations Planning | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-008 | IRO-008-1 | 2. | Each Reliability Coordinator shall perform a Real-Time Assessment at least once every 30 minutes to determine if its Wide Area is exceeding any IROLs or is expected to exceed any IROLs. | M2. The Reliability Coordinator shall have, and make available upon request, evidence to show it conducted a Real-Time Assessment at least once every 30 minutes. This evidence could include, but is not limited to, dated computer log showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-1 | No Parts for 2. |  | M2. The Reliability Coordinator shall have, and make available upon request, evidence to show it conducted a Real-Time Assessment at least once every 30 minutes. This evidence could include, but is not limited to, dated computer log showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-008 | IRO-008-1 | 3. | When a Reliability Coordinator determines that the results of an Operational Planning Analysis or Real-Time Assessment indicates the need for specific operational actions to prevent or mitigate an instance of exceeding an IROL, the Reliability Coordinator shall share its results with those entities that are expected to take those actions. | M3. The Reliability Coordinator shall have and make available upon request, evidence to confirm that it shared the results of its Operational Planning Analyses or Real-Time Assessments with those entities expected to take actions based on that information. This evidence could include, but is not limited to, dated operator logs, dated voice recordings, dated transcripts of voice records, dated facsimiles, or other evidence. | Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-1 | No Parts for 3. |  | M3. The Reliability Coordinator shall have and make available upon request, evidence to confirm that it shared the results of its Operational Planning Analyses or Real-Time Assessments with those entities expected to take actions based on that information. This evidence could include, but is not limited to, dated operator logs, dated voice recordings, dated transcripts of voice records, dated facsimiles, or other evidence. | Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-008 | IRO-008-2 | 1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | M1. Each Reliability Coordinator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-2 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-008 | IRO-008-2 | 2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | M2. Each Reliability Coordinator shall have evidence that it has a coordinated Operating Plan for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. Such evidence could include but is not limited to plans for precluding operating in excess of each SOL and IROL that were identified as a result of the Operational Planning Analysis. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-2 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have evidence that it has a coordinated Operating Plan for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. Such evidence could include but is not limited to plans for precluding operating in excess of each SOL and IROL that were identified as a result of the Operational Planning Analysis. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-008 | IRO-008-2 | 3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | M3. Each Reliability Coordinator shall have evidence that it notified impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-2 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have evidence that it notified impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-008 | IRO-008-2 | 4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | M4. Each Reliability Coordinator shall have, and make available upon request, evidence to show it ensured that a Real-time Assessment is performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-2 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have, and make available upon request, evidence to show it ensured that a Real-time Assessment is performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-008 | IRO-008-2 | 5. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | M5. Each Reliability Coordinator shall make available upon request, evidence that it informed impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, of its actual or expected operations that result in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-2 | No Parts for 5. |  | M5. Each Reliability Coordinator shall make available upon request, evidence that it informed impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, of its actual or expected operations that result in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-008 | IRO-008-2 | 6. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | M6. Each Reliability Coordinator shall make available upon request, evidence that it informed impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-008 | IRO-008-2 | No Parts for 6. |  | M6. Each Reliability Coordinator shall make available upon request, evidence that it informed impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  |  |  |  | 2024-03-31 | Filing/Order Docket No. RM15-16-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs) within its Wide Area. | M1. Each Reliability Coordinator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | M2. Each Reliability Coordinator shall have evidence that it has a coordinated Operating Plan for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. Such evidence could include but is not limited to plans for precluding operating in excess of each SOL and IROL that were identified as a result of the Operational Planning Analysis. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have evidence that it has a coordinated Operating Plan for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. Such evidence could include but is not limited to plans for precluding operating in excess of each SOL and IROL that were identified as a result of the Operational Planning Analysis. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | M3. Each Reliability Coordinator shall have evidence that it notified impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). Such evidence could include, but is not limited to, dated operator logs, or e-mail records. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 3. |  | M3. Each Reliability Coordinator shall have evidence that it notified impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). Such evidence could include, but is not limited to, dated operator logs, or e-mail records. | Operations Planning | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | M4. Each Reliability Coordinator shall have, and make available upon request, evidence to show it ensured that a Real-time Assessment is performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have, and make available upon request, evidence to show it ensured that a Real-time Assessment is performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 5. | Each Reliability Coordinator shall notify, in accordance with its SOL methodology, impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | M5. Each Reliability Coordinator shall make available upon request, evidence that it informed, in accordance with its SOL methodology impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, of its actual or expected operations that result in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 5. |  | M5. Each Reliability Coordinator shall make available upon request, evidence that it informed, in accordance with its SOL methodology impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, of its actual or expected operations that result in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 6. | Each Reliability Coordinator shall notify, in accordance with SOL methodology, impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | M6. Each Reliability Coordinator shall make available upon request, evidence that it informed, in accordance with its SOL methodology impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 6. |  | M6. Each Reliability Coordinator shall make available upon request, evidence that it informed, in accordance with its SOL methodology impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Reliability Coordinator may provide an attestation. | Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | 7. | Each Reliability Coordinator shall use its SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it used its SOL methodology for determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. Evidence could include, but is not limited to: Operating Plans, contingency sets, SOLs, alarming and study reporting thresholds, operator logs, voice recordings or other equivalent evidence. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008 | IRO-008-3 | No Parts for 7. |  | M7. Each Reliability Coordinator shall have, and provide upon request, evidence that it used its SOL methodology for determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. Evidence could include, but is not limited to: Operating Plans, contingency sets, SOLs, alarming and study reporting thresholds, operator logs, voice recordings or other equivalent evidence. | Operations Planning, Real-Time Operations, Same-Day Operations | 2021-05-13 | 2021-06-28 | 2022-03-04 | 2022-03-04 | 2024-04-01 | [5 empty] | Filing/Order Docket No. RD22-2-000
Inactive | IRO | IRO-009 | IRO-009-1 | 1. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions it shall take or actions it shall direct others to take (up to and including load shedding) that can be implemented in time to prevent exceeding those IROLs. | M1. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating instances of exceeding IROLs in accordance with Requirement R1 and Requirement R2. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that that will be used. | Operations Planning, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-009 | IRO-009-1 | No Parts for 1. |  | M1. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating instances of exceeding IROLs in accordance with Requirement R1 and Requirement R2. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that that will be used. | Operations Planning, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-009 | IRO-009-1 | 2. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions it shall take or actions it shall direct others to take (up to and including load shedding) to mitigate the magnitude and duration of exceeding that IROL such that the IROL is relieved within the IROL’s Tv. | M2. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it acted or directed others to act in accordance with Requirement R3 and Requirement R4. This evidence could include, but is not limited to, Operating Processes, Procedures, or Plans from Requirement R1, dated operating logs, dated voice recordings, dated transcripts of voice recordings, or other evidence. | Operations Planning, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-009 | IRO-009-1 | No Parts for 2. |  | M2. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it acted or directed others to act in accordance with Requirement R3 and Requirement R4. This evidence could include, but is not limited to, Operating Processes, Procedures, or Plans from Requirement R1, dated operating logs, dated voice recordings, dated transcripts of voice recordings, or other evidence. | Operations Planning, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-009 | IRO-009-1 | 3. | When an assessment of actual or expected system conditions predicts that an IROL in its Reliability Coordinator Area will be exceeded, the Reliability Coordinator shall implement one or more Operating Processes, Procedures or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirements R1) to prevent exceeding that IROL. | M3. For a situation where Reliability Coordinators disagree on the value of an IROL or its Tv the Reliability Coordinator shall have, and make available upon request, evidence to confirm that it used the most conservative of the values under consideration, without delay. Such evidence could include, but is not limited to, dated computer printouts, dated operator logs, dated voice recordings, dated transcripts of voice recordings, or other equivalent evidence. (R5) | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-009 | IRO-009-1 | No Parts for 3. |  | M3. For a situation where Reliability Coordinators disagree on the value of an IROL or its Tv the Reliability Coordinator shall have, and make available upon request, evidence to confirm that it used the most conservative of the values under consideration, without delay. Such evidence could include, but is not limited to, dated computer printouts, dated operator logs, dated voice recordings, dated transcripts of voice recordings, or other equivalent evidence. (R5) | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-009 | IRO-009-1 | 4. | When actual system conditions show that there is an instance of exceeding an IROL in its Reliability Coordinator Area, the Reliability Coordinator shall, without delay, act or direct others to act to mitigate the magnitude and duration of the instance of exceeding that IROL within the IROL’s Tv. |  | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-009 | IRO-009-1 | No Parts for 4. |  |  | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-009 | IRO-009-1 | 5. | If unanimity cannot be reached on the value for an IROL or its Tv, each Reliability Coordinator that monitors that Facility (or group of Facilities) shall, without delay, use the most conservative of the values (the value with the least impact on reliability) under consideration. |  | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-009 | IRO-009-1 | No Parts for 5. |  |  | Real-Time Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2015-12-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | 1. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions the Reliability Coordinator shall take or actions the Reliability Coordinator shall direct others to take (up to and including load shedding): | M1. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating the magnitude and duration of IROL exceedances in accordance with Requirement R1. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that will be used. | Operations Planning, Same-Day Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | 1.1. | That can be implemented in time to prevent the identified IROL exceedance. | M1. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating the magnitude and duration of IROL exceedances in accordance with Requirement R1. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that will be used. | Operations Planning, Same-Day Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | 2015-12-04 |  |  |  |  | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | 1.2. | To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv . | M1. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating the magnitude and duration of IROL exceedances in accordance with Requirement R1. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that will be used. | Operations Planning, Same-Day Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | 2016-01-01 |  |  |  |  | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | 2. | Each Reliability Coordinator shall initiate one or more Operating Processes, Procedures, or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirement R1) that are intended to prevent an IROL exceedance, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | M2. The Reliability Coordinator shall make available evidence that it has distributed its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. This evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | No Parts for 2. |  | M2. The Reliability Coordinator shall make available evidence that it has distributed its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. This evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | 3. | Each Reliability Coordinator shall act or direct others to act so that the magnitude and duration of an IROL exceedance is mitigated within the IROL’s Tv, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it acted or directed others to act in accordance with Requirement R3. This evidence could include, but is not limited to, Operating Processes, Procedures, or Plans, dated operating logs, dated voice recordings, dated transcripts of voice recordings, or other evidence. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | No Parts for 3. |  | Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it acted or directed others to act in accordance with Requirement R3. This evidence could include, but is not limited to, Operating Processes, Procedures, or Plans, dated operating logs, dated voice recordings, dated transcripts of voice recordings, or other evidence. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | 4. | Each Reliability Coordinator shall operate to the most limiting IROL and Tv in instances where there is a difference in an IROL or its Tv between Reliability Coordinators that are responsible for that Facility (or group of Facilities). | M4. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it operated to the most limiting IROL and Tv in instances where there was a difference in an IROL or its Tv. Such evidence could include, but is not limited to, dated computer printouts, dated operator logs, dated voice recordings, dated transcripts of voice recordings, or other equivalent evidence in accordance with Requirement R4. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000 | [13 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009 | IRO-009-2 | No Parts for 4. |  | M4. Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it operated to the most limiting IROL and Tv in instances where there was a difference in an IROL or its Tv. Such evidence could include, but is not limited to, dated computer printouts, dated operator logs, dated voice recordings, dated transcripts of voice recordings, or other equivalent evidence in accordance with Requirement R4. | Real-Time Operations | 2015-08-13 | 2015-09-16 | 2015-12-04 | 2015-12-04 | 2016-01-01 | [5 empty] | Filing/Order Docket No. RD15-7-000
Inactive | IRO | IRO-010 | IRO-010-1 | 1. | The Reliability Coordinator shall have a documented specification for data and information to build and maintain models to support Real-time monitoring, Operational Planning Analyses, and Real-time Assessments of its Reliability Coordinator Area to prevent instability, uncontrolled separation, and cascading outages. The specification shall include the following: (Time Horizon: Operations Planning) |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1 | 1.1. | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1 | 1.2. | Mutually agreeable format. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1 | 1.3. | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1 | 1.4. | Process for data provision when automated Real-Time system operating data is unavailable. |  | Operations Planning, Real-Time Operations, Same-Day Operations | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 |  | 2011-05-23 |  |  |  | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1 | 2. | The Reliability Coordinator shall distribute its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. (Time Horizon: Operations Planning) |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1 | No Parts for 2. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-010 | IRO-010-1 | 3. | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. (Time Horizon: Operations Planning; Same-day Operations; Real-time Operations) |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-010 | IRO-010-1 | No Parts for 3. |  |  |  | 2008-10-17 | 2009-12-31 | 2011-03-17 | 2011-05-23 | [5 empty] | 2009-08-05 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-010 | IRO-010-1a | 1. | The Reliability Coordinator shall have a documented specification for data and information to build and maintain models to support Real-time monitoring, Operational Planning Analyses, and Real-time Assessments of its Reliability Coordinator Area to prevent instability, uncontrolled separation, and cascading outages. The specification shall include the following: | M1. The Reliability Coordinator shall have, and make available upon request, a documented data specification that contains all elements identified in Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1a | 1.1. | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. | M1. The Reliability Coordinator shall have, and make available upon request, a documented data specification that contains all elements identified in Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1a | 1.2. | Mutually agreeable format. | M1. The Reliability Coordinator shall have, and make available upon request, a documented data specification that contains all elements identified in Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1a | 1.3. | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). | M1. The Reliability Coordinator shall have, and make available upon request, a documented data specification that contains all elements identified in Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-10-01 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1a | 1.4. | Process for data provision when automated Real-Time system operating data is unavailable. | M1. The Reliability Coordinator shall have, and make available upon request, a documented data specification that contains all elements identified in Requirement R1. | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 | 2011-05-23 |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1a | 2. | The Reliability Coordinator shall distribute its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. | M2. The Reliability Coordinator shall have, and make available upon request, evidence that it distributed its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. This evidence could include, but is not limited to, dated paper or electronic notice used to distribute its data specification showing recipient, and data or information requested or other equivalent evidence. (R2) | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-1a | No Parts for 2. |  | M2. The Reliability Coordinator shall have, and make available upon request, evidence that it distributed its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. This evidence could include, but is not limited to, dated paper or electronic notice used to distribute its data specification showing recipient, and data or information requested or other equivalent evidence. (R2) | Operations Planning | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-010 | IRO-010-1a | 3. | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. | M3. The Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Reliability Coordinator, Transmission Operator and Transmission Owner shall each have, and make available upon request, evidence to confirm that it provided data and information, as specified in Requirement R3. This evidence could include, but is not limited to, dated operator logs, dated voice recordings, dated computer printouts, dated SCADA data, or other equivalent evidence. | Operations Planning, Real-Time Operations, Same-Day Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000 | BA |  |  |  | GO |  | GOP |  | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-010 | IRO-010-1a | No Parts for 3. |  | M3. The Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Reliability Coordinator, Transmission Operator and Transmission Owner shall each have, and make available upon request, evidence to confirm that it provided data and information, as specified in Requirement R3. This evidence could include, but is not limited to, dated operator logs, dated voice recordings, dated computer printouts, dated SCADA data, or other equivalent evidence. | Operations Planning, Real-Time Operations, Same-Day Operations | 2009-08-05 | 2009-12-31 | 2011-03-17 | 2011-05-23 | 2011-10-01 |  |  |  |  | 2017-03-31 | Filing/Order Docket No. RM10-15-000, RM10-16-000
Inactive | IRO | IRO-010 | IRO-010-2 | 1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: | M1. The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-2 | 1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. | M1. The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2017-01-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-2 | 1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | M1. The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2017-01-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-2 | 1.3. | A periodicity for providing data. | M1. The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2017-01-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-2 | 1.4. | The deadline by which the respondent is to provide the indicated data. | M1. The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 | 2017-01-01 | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-2 | 2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M2. The Reliability Coordinator shall make available evidence that it has distributed its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. This evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | [13 empty] | RC
Inactive | IRO | IRO-010 | IRO-010-2 | No Parts for 2. |  | M2. The Reliability Coordinator shall make available evidence that it has distributed its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. This evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | Operations Planning | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-01-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000
Inactive | IRO | IRO-010 | IRO-010-2 | 3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: | M3. The Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Reliability Coordinator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall make available evidence that it satisfied the obligations of the documented specification using the specified criteria. Such evidence could include but is not limited to electronic or hard copies of data transmittals or attestations of receiving entities. | Operations Planning, Real-Time Operations, Same-Day Operations | 2014-11-13 | 2015-03-18 | 2015-11-19 | 2016-01-26 | 2017-04-01 |  | X |  |  | 2021-03-31 | Filing/Order Docket No. RM15-16-000 | BA | DP |  |  | GO |  | GOP |  |  | LSE |  |  |  | RC | [5 empty] | TO | TOP