4-22-O

Exhibit A

Interconnection Standards for

Installation and Parallel Operation of

Customer-Owned Renewable Electric

Generation Facilities

City of Celina, Ohio

________________________________________________

July 2021

Contents

Part 1.  Overview	1

1.	Purpose:	1

2.	Definitions:	1

3.	Eligibility:	3

5.	Interconnection Request:	5

6.	Electric Distribution System Impact Analysis:	5

7.	System Upgrades:	8

8.	Interconnection Agreement:	8

9.	Codes and Permits:	9

10.	Certificate of Completion:	9

11.	Normal Operation:	9

Part 2.  Technical Requirements	10

1.	Character of Service:	10

2.	Code Requirements:	10

3.	Generation Facility Control:	10

4.	System Protection:	11

5.	Fault Current Disconnection:	11

6.	Reclosing Coordination:	12

7.	External Generation Facility AC Disconnect Switch:	12

8.	Standards for Interconnection, Safety and Operating Reliability:	12

9.	Access and Inspection by Utility:	13

10.	Generation Facility Operation:	14

11.	Right to Disconnect Generation Facility:	15

12.	Rates and Other Charges:	15

13.	Insurance:	16

14.	Limitation of Liability and Indemnification:	16

15.	Effective Term and Termination Rights:	17

16.	Termination of any Applicable Prior Agreement:	18

17.	Force Majeure:	18

Part 3.  Interconnection Application	19

Part 3a.  Interconnection Application	25

Part 4.  Interconnection Agreement	31

Part 5.  Certificate of Completion	34

Part 6.  Approval to Energize Generation Facility	35

Part 7.  Renewable Electric Generation Application for Service	36

# Part 1.  Overview

## Purpose:

The purpose of this document is to establish standards for eligible customers (“Customer”) to interconnect and operate Customer-owned renewable Generation Facilities in parallel with the City of Celina Electric Utility (“Utility”) Electric Distribution System.

## Definitions:

  - AC – Alternating Current

  - Applicable Laws and Regulations – All duly promulgated applicable federal, state and local laws, regulations, rules, ordinances, codes, decrees, judgments, directives, or judicial or administrative orders, permits and other duly authorized actions of any Governmental Authority, including the Ordinances of the City of Celina and Electric General Rules and Regulations.

  - City – The City of Celina, Ohio.

  - Commercial Operation Date – The date on which the Generation Facility is operating and is in compliance with the requirements of these Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities as determined by the Utility.

  - Customer – an electric customer interconnected to the Utility Electric Distribution System for the purpose of receiving retail electric service that also owns and operates an approved renewable Generation Facility.

  - DC – Direct Current

  - Electric Distribution System – The Utility facilities and equipment used to provide electric service to customers, including the Customer.

  - Excess Generation – Energy delivered to Utility at any instance when a Customer’s renewable Generation Facility produces more energy than is consumed by the Customer at the same metering point.

  - Generation Facility – For purposes of these Interconnection Standards, the Customer device for conversion of renewable energy to electricity that:

    - Is fueled by solar or wind;

    - Is owned by the Customer;

    - Is located on the Customer’s premises;

    - Serves only the Customer’s premises (serves no other customers);

    - Is a Qualified Facility as defined herein;

    - Is interconnected with and operates in parallel phase and synchronization with the Electric Distribution System and is in compliance with these Interconnection Standards;

    - Contains a Utility-approved mechanism(s) that automatically disconnects the Generation Facility and interrupts the flow of electricity to the Electric Distribution System in the event that electric service to the Customer is interrupted.

  - Generator Meter – Revenue grade interval meter installed on the Customer-owned Generation Facility. A Generator Meter is required when Customer Generation Facility is certified as a Qualifying Facility under the Public Utility Regulatory Policies Act of 1978 or takes service under Utility’s Qualifying Facility schedule.

  - Governmental Authority – Any federal, state, local or other governmental regulatory or administrative agency, court, commission, department, board, or other governmental subdivision, legislature, rulemaking board, tribunal, or other governmental authority having jurisdiction over the Parties, their respective facilities, or the respective services they provide, and exercising or entitled to exercise any administrative, executive, police, or taxing authority or power; provided, however, that such term does not include the Customer or any Affiliate thereof.

  - Harmonic Distortion – Distortion of the normal AC sine wave typically caused by non-linear loads or inverters.

  - Interconnection Point – The physical connection of a Generation Facility to the Utility Electric Distribution System.

  - Interconnection Application – The Customer request to interconnect a new Generation Facility, or to increase the capacity of, or make a material modification to the operating characteristics of an existing Generation Facility that is interconnected with the Electric Distribution System.

  - Interconnection Standards – Interconnection Standards shall mean all provisions, forms and related documents described in the collective parts of these Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities, or successor document.

  - Metering Point – The Utility-owned electric meter as shown on the one-line diagram accompanying the Customer’s Interconnection Application.

  - Party – Individually the Utility and the Customer; collectively the “Parties.”

  - Prudent Utility Practice – Any of the practices, methods and acts engaged in or approved by a significant portion of the electric utility industry during the relevant time period, or any of the practices, methods and acts which, in the exercise of reasonable judgment in light of the facts known at the time the decision was made, could have been expected to accomplish the desired result at a reasonable cost consistent with good business practices, reliability, safety and expedition.  Prudent Utility Practice is not intended to be limited to the optimum practice, method, or act to the exclusion of all others, but rather to be acceptable practices, methods, or acts generally accepted in the region by the electric utility industry.

  - PURPA – Public Utility Regulatory Policies Act of 1978 and any subsequent amendments or revisions.

  - Qualifying Facility – For purposes of these Interconnection Standards, a Qualifying facility is defined as:

- A customer-owned facility that is either:

(a)	 A small power production facility with a net power production capacity of five (5) MW or less, whose primary energy source is renewable (hydro, wind or solar), biomass, waste, or geothermal resources.  In order to be considered a qualifying small power production facility, a facility must meet all of the requirements of 18 C.F.R. §§ 292.203(a), 292.203(c) and 292.204 and 170 IAC 4-4.1 for size and fuel use; or

(b) A cogeneration facility with a net power production capacity of twenty (20) MW or less, that sequentially produces electricity and another form of useful thermal energy (such as heat or steam) in a way that is more efficient than the separate production of both forms of energy. In order to be considered a Qualifying Facility, a facility must meet all of the requirements of 170 IAC 4-4.1 and 18 C.F.R. §§ 292.203(b) and 292.205 for operation, efficiency and use of energy output.

- A Qualifying Facility with a maximum net power production capacity of greater than one megawatt (1 MW) must be certified as a Qualifying Facility at FERC pursuant to 18 C.F.R. 292.207.

  - Reasonable Efforts – With respect to an action required to be attempted or taken by a Party under the Interconnection Agreement, efforts that are timely and consistent with Prudent Utility Practice and are otherwise substantially equivalent to those a Party would use to protect its own interests.

  - System Upgrades – Additions, modifications, improvements, and upgrades to the Electric Distribution System or Customer service connection at or beyond the point of interconnection to facilitate interconnection of the Customer Generation Facility.

  - Utility – City of Celina Electric Utility.

  - Voltage Flicker – A variation of voltage sufficient in duration to allow visual observation of a change in electric light source intensity.

## Eligibility:

  - Must be an electric customer with a Customer-owned Utility approved Generation Facility as defined herein that is interconnected with and operates in parallel phase and synchronization with the Electric Distribution System.

  - Customer’s utility account must be in good standing and in compliance with Utility electric rate schedules and Rules and Regulations.

- Pre-Application Report:

An applicant may submit a formal request along with a non-refundable fee of $300 for a pre-application report on a proposed project at a specific site.  The Utility shall provide the pre-application data described in subsection (a) to the applicant within ten business days of receipt of the written request and payment of the $300 fee.

  - Total AC capacity (kW) of substation/area bus, bank or circuit based on normal or operating ratings likely to serve the proposed site.

  - Existing aggregate generation capacity (kWAC) interconnected to a substation/area bus, bank or circuit, which is the online amount of generation, likely to serve the proposed site.

  - Aggregate queued generation capacity (kWAC) for substation a substation/area bus, bank or circuit, which is the amount of generation in the queue likely to serve the proposed site.

  - Available capacity (kWAC) of substation/area bus or bank and circuit most likely to serve the proposed site, which is the total capacity less the sum of existing aggregate generation capacity and aggregate queued generation capacity.

  - Substation nominal distribution voltage and/or transmission voltage, if applicable.

  - Nominal distribution circuit voltage at the proposed site.

  - Approximate circuit distance between the proposed site and the substation.

  - Relevant line section(s) peak load estimate, and minimum load data, when available.

  - Number and rating of protective devices and number and type (standard, bidirectional) of voltage regulating devices between the proposed site and the substation/area.  Identify whether substation has a load tap changer.

  - Number of phases available at the site.

  - Limiting conductor ratings from the proposed point of interconnection to the distribution substation.

  - Based on the proposed Interconnection Point, existing or known constraints such as, but not limited to, electrical dependencies at that location, short circuit interrupting capacity issues, power quality or stability issues on the circuit, capacity constraints, or secondary networks.

The pre-application report need only include pre-existing data.  A pre-application report request does not obligate the Utility to conduct a study or other analysis of the proposed generator in the event that data is not readily available.  If the Utility cannot complete some of a pre-application report due to lack of available data, the Utility shall provide the applicant with a pre-application report that includes the data that is available. The Pre-application Request can be found in Exhibit 1.

## Interconnection Request:

The Customer shall request interconnection of a Generation Facility by completing and submitting to the Utility the attached document entitled “Interconnection Application” together with the processing fee.  The Utility may require additional information or clarification to evaluate the Customer Interconnection Request.  Interconnection Applications will be reviewed by the Utility in the order in which they are received.  The Interconnection Application shall be date-and time-stamped upon receipt.  If an Interconnection Application is viewed as incomplete, the Utility will provide notice to the Customer that the Application is not complete, provide a description of the information needed to complete the Application, and include a statement that processing of the Interconnection Application cannot begin until the Interconnection Application is complete.

Any modification to the design or equipment configuration or to the interconnection site of the Generation Facility not agreed to in writing by the Utility and the Customer may be deemed a withdrawal of the Interconnection Request and may require submission of a new Interconnection Request, unless proper notification of each Party by the other and a reasonable time to cure the problems created by the changes are undertaken.

Documentation of site control must be submitted with the Interconnection Request.  Site control may be demonstrated through:

- ownership of, or a leasehold interest in, or a right to develop a site for the purpose of constructing a Generation Facility;

- an option to purchase or acquire a leasehold site for such purpose; or

- an exclusivity or other business relationship between Customer and the property owner having the right to sell, lease or grant the Customer the right to possess or occupy the site for such purpose.

The Utility shall assign a queue position to each Interconnection Request based upon the date-and time-stamp of the Interconnection Request. The queue position of each Interconnection Request shall be used to determine cost responsibility for system upgrades.

## Electric Distribution System Impact Analysis:

The purpose of the Distribution System Impact Analysis is to determine if the Generation Facility will have an adverse impact on the Electric Distribution System equipment.  If the proposed Generation Facility meets all of the requirements in a. through o. below, it will not be necessary to prepare a Feasibility Analysis and the proposed Generation Facility maybe installed without further analysis.  After receiving a properly completed Interconnection Application, the Utility will analyze the potential impact of the proposed Generation Facility on the Electric Distribution System and on other Utility customers.  Such analyses will be based on Prudent Utility Practice to determine thermal effects, voltage ranges, power quality, system stability, etc., and will include the following:

a.	The Customer Generation Facility’s proposed interconnection point is on a radial distribution circuit that is subject to the Tariff as defined under PURPA of 1978.

b.	The proposed Generation Facility complies with IEEE 1547 and UL 1741 or successor standards.

c.	The proposed Generation Facility’s capacity in aggregation with other generation on the circuit shall not exceed 15 percent (15%) of the line section annual peak demand (kW) as most recently measured at the substation during the previous 12-month period.

d.	The proposed Generation Facility, in aggregation with other generation on the distribution circuit, shall not contribute more than 10 percent (10%) to the distribution circuit’s maximum fault current at the point on the primary voltage distribution line nearest the proposed Interconnection point.

e.	The proposed Generation Facility, in aggregation with other generation located on the distribution circuit, may not cause any distribution protective devices and equipment (including, but not limited to, substation breakers, fuse cutouts, and line reclosers, or other customer equipment on the electric distribution system to be exposed to fault currents exceeding 87.5 percent (87.5%) of the short circuit interrupting capability.

f.	No additional Generation Facilities shall be interconnected on a circuit that equals or exceeds 87.5 percent (87.5%) of its short circuit interrupting capability.

g.	No Generation Facility in combination with Utility-owned generation shall be interconnected that would cause reverse power at Utility’s transmission interconnection points or cause the Utility to be in conflict with Utility’s network transmission provider.

h.	When a proposed Generation Facility is single-phase and is to be interconnected on a center tap neutral on a 240-volt service, its addition shall not create an imbalance between the two sides of the 240-volt service of more than 20 percent of the nameplate rating of the service transformer.

i.	The proposed Generation Facility installation must be certified to pass an applicable non-islanding test, or use reverse power relays or other means to meet IEEE 1547 unintentional islanding requirements.

j.	On a three-phase, three-wire primary electric distribution line, a three- or single-phase generator shall be connected phase-to-phase.

k.	When the Applicant’s facility is to be connected to three-phase, four-wire primary distribution lines, a three- or single-phase generator shall be connected line-to-neutral and shall be effectively grounded.

l.	When the proposed Generation Facility is to be interconnected on a single-phase shared secondary line, the aggregate generation capacity on the shared secondary line, including the proposed Generation Facility, shall not exceed 20 kW.

m.	For interconnection of a proposed Generation Facility to the load side of spot or area network protectors, the proposed Generation Facility must utilize an inverter-based equipment package, and together with the aggregated other inverter-based generation, shall not exceed the lesser of five percent (5%) of a spot or area network’s maximum load or fifty (50) kilowatts.

n.	Construction of facilities by the Utility on the Electric-Distribution System is not required to accommodate the customer-owned Generation Facility.

o.	The Generation Facility, in aggregate with other generation interconnected to the transmission side of a substation transformer feeding the circuit where the Generation Facility proposes to interconnect shall not exceed 10 MW in an area where there are transient stability limitations to generating units located in the general electrical vicinity (e.g. 3 or 4 transmission bases from the Interconnection Point).

Feasibility Analysis

If the proposed Generation Facility fails to meet one or more of the above requirements, the Customer may request that the Utility complete an analysis to determine the feasibility of interconnecting the proposed Generation Facility to the Electric Distribution System.  The Feasibility Analysis shall include:

- Initial identification of any circuit breaker short-circuit capability limits exceeded as a result of the interconnection.

- Initial identification of any thermal overload or voltage limit violations resulting from the interconnection.

- Initial review of grounding requirements and system protection.

- A description and nonbinding estimated cost of facilities required to interconnect the Generation Facility to the Electric Distribution System in a safe and reliable manner.

The actual cost of the Feasibility Analysis shall be paid by the Customer.  The Utility will provide an estimated cost of the Feasibility Analysis to Customer and Customer shall advance 50% of such estimate to Utility if Customer wants Utility to prepare a Feasibility Analysis.  When Feasibility Analysis cost exceeds 50% of the estimated cost, Utility shall bill Customer as such fees are incurred.

System Impact Study

If the Feasibility Analysis concludes that interconnection of the proposed Generation Facility would create an adverse system impact, a System Impact Study is required.

A System Impact Study shall evaluate the impact of the proposed Generation Facility interconnection on the safety and reliability of the Electric Distribution system. The study shall:

- Identify and detail the system impacts that result if the proposed Generation Facility is interconnected without project or system modifications.

- Consider the adverse system impacts or potential impacts identified in the Feasibility Analysis.

- Consider all Generating Facilities that, on the date the System Impact Study is commenced, are directly interconnected with the Electric Distribution System.

- Consider pending Interconnection Applications of Generation Facilities requesting interconnection to the Electric Distribution System.

The System Impact Study shall consider the following criteria:

1.	A load flow study.

2.	A short circuit analysis.

3.	A stability analysis.

4.	Voltage drop and flicker studies.

5.	Protection and set point coordination studies.

6.	Grounding reviews.

The Utility shall state the underlying assumptions of the Study and share the results of the analyses with the Customer, including the following:

1.	Any potential impediments to providing the requested interconnection service.

2.	Any required Electric Distribution System Upgrades and the estimated cost and time to engineer and construct said System Upgrades.

The actual cost of the System Impact Study shall be paid by the Customer.  The Utility will provide an estimated cost of the System Impact Study to Customer and Customer shall advance 50% of such estimate to the Utility if Customer wants the Utility to prepare a System Impact Study.  When System Impact Study cost exceeds 50% of the estimated cost, the Utility shall bill Customer as such fees are incurred.

## System Upgrades:

The Utility shall not be obligated to make upgrades or improvements to its Electric Distribution System to accommodate the Customer’s Generation Facility.  Where System Upgrades are required prior to interconnection of the Generation Facility as identified in the System Impact Study, the Utility will provide the Customer with an estimated schedule and the Customer’s cost for said System Upgrades.

## Interconnection Agreement:

After the Customer and the Utility have identified and mutually agreed on the project scope including the Generation Facility, System Upgrades and estimated costs (if any), the Customer and the Utility shall execute the attached document entitled “Interconnection Agreement.”  The Interconnection Agreement shall be between the Utility and the Customer and shall not include third parties.  Prior to commencement of System Upgrades required to allow interconnection of the Customer-owned Generation Facility, Customer shall deposit with the Utility an amount equal to the estimated cost of said System Upgrades.  See “Section 4. Interconnection Costs” of the Interconnection Agreement (Part 4) for additional information.

## Codes and Permits:

  - The Customer shall be responsible for procuring all building, operating, environmental or other permits for the Generation Facility and for the necessary ancillary structures to be installed that are required by any Governmental Authority having jurisdiction.

  - The Generation Facility and interconnecting equipment shall meet all requirements in “Part 2. Technical Requirements” of these Interconnection Standards.

  - The construction and facilities shall meet all applicable building and electrical codes.

## Certificate of Completion:

Upon completion of the Generation Facility and prior to the Commercial Operation Date of said Facility, the Customer shall complete and submit a signed copy of the attached document entitled “Certificate of Completion.”

## Normal Operation:

The Customer may begin Commercial Operation of the Generation Facility upon receipt of written approval from the Utility.

# Part 2.  Technical Requirements

## Character of Service:

The electric service shall be 60 cycles per second (60 Hertz) alternating current (AC) at supply voltages and number of phases under the applicable rate schedule that would apply if the Customer did not have an interconnected Generation Facility.

## Code Requirements:

The Generation Facility shall meet all requirements established by the National Electrical Code (NEC), National Electrical Safety Code (NESC), Institute of Electrical and Electronics Engineers (IEEE), Underwriters Laboratories (UL), and the Occupational Safety and Health Administration.  Specific applicable codes are shown in Section 8 of this Part 2 below as “Standards for Interconnection, Safety and Operating Reliability.”

## Generation Facility Control:

The control system of the Generation Facility shall comply with IEEE and UL specifications and standards for parallel operation with the Electric Distribution System and in particular as follows:

  - Power output control system shall automatically disconnect from the Electric Distribution System upon loss of System voltage and shall not reconnect until System voltage has been restored.

  - Power output control system shall automatically disconnect from the Electric Distribution System if system voltage fluctuates beyond plus or minus ten percent (10%) and phase angle beyond plus or minus (10%).

  - Generation Facility shall be operated such that the voltage unbalance attributable to the Generation Facility does not exceed 2.5% at the Interconnection Point.

  - Generation Facility shall be operated within a power factor range from 0.9 leading to 0.9 lagging. Operation outside this range is acceptable provided the reactive power of the Generation Facility is used to meet the reactive power needs of the electrical loads within the Customer’s facility. The Customer shall notify Utility if it is using Generation Facility for power factor correction.

  - Power output control system shall automatically disconnect from the Electric Distribution System if the generator fails to operate within the operating frequency range of 59.5 – 60.5 Hz.

  - Inverter output Harmonic Distortion shall meet IEEE and UL standards.

  - The Generation Facility shall meet applicable IEEE and UL standards concerning impacts to the Electric Distribution System with regard to Harmonic Distortion, Voltage Flicker, power factor, direct current injection and electromagnetic interference.

## System Protection:

The owner of the Customer-owned Generation Facility is responsible for providing adequate protection to electric Utility facilities for conditions arising from the operation of generation under all Utility distribution system operating conditions.  The owner is also responsible for providing adequate protection to its facility under any Utility distribution system operating condition whether or not its customer owned generator is in operation. Conditions may include but are not limited to:

  - Loss of a single phase of supply.

  - Distribution system faults,

  - Equipment failures,

  - Abnormal voltage or frequency,

  - Lightning and switching surges,

  - Excessive harmonic voltages,

  - Excessive negative sequence voltages,

  - Separation from supply,

  - Synchronizing generation,

  - Re-synchronizing the Owner’s generation after electric restoration of the supply.

## Fault Current Disconnection:

The Generation Facility shall be equipped with protective equipment designed to automatically disconnect from the Electric Distribution System during fault current conditions and remain disconnected until System voltage and frequency have stabilized.

Circuit Breaker – If a main circuit breaker (or circuit switcher) between the interconnection transformer and the Utility Electric Distribution System is required, the device must comply with the applicable current ANSI Standard from the C37 series of standards that specifies the requirements for circuit breakers, reclosers and interrupting switches.

Terminating Structure – When a new interconnection line is required, the Customer shall provide a suitable structure to terminate the interconnection line. The Customer is responsible for ensuring that terminating structure or substation structural material strengths are adequate for all requirements, incorporating appropriate safety factors. Utility will provide line tension information for maximum dead-end. The structure must be designed for the maximum line tension along with an adequate margin of safety.

Substation electrical clearances shall meet or exceed the requirements of the National Electrical Safety Code. Installation of disconnect switches, bus support insulators and other equipment shall comply with accepted industry practices.

Surge arresters shall be selected to coordinate with the BIL rating of major equipment components and shall comply with recommendations set forth in the applicable current ANSI Standard C62.2 that specifies the requirements for surge arresters and other surge protection devices.

## Reclosing Coordination:

The Generation Facility shall be coordinated with Electric Distribution System reclosing devices by disconnecting from the System during de-energized System operation. The Generation Facility shall remain disconnected until System voltage and frequency have stabilized.

Main Disconnect Switch (Voltages exceeding 480 volts) – A gang operated disconnecting device must be located at the Interconnection Point for all three phase interconnections. In all cases the disconnecting device must be clearly labeled, readily accessible to the Utility personnel for use at all times and suitable for use by Utility as a protective tagging location. The disconnecting device shall have a visible open gap when in the open position and be capable of being locked in the open position.

The disconnecting device must have a ground grid designed in accordance with specifications to be provided by Utility. Operation of the device must be restricted to Utility personnel and properly trained operators designated by the Customer. The disconnecting device must comply with the applicable current ANSI Standard from the C37 series of standards that specifies the requirements for circuit breakers, reclosers and interrupting switches.

## External Generation Facility AC Disconnect Switch:

The Customer shall install an external alternating current (AC) disconnect switch within six (6) feet of the Utility electric meter(s) that is visible and readily accessible to Utility representatives at all times. This switch shall be clearly labeled as “Generator AC Disconnect Switch”. The switch shall be capable of being locked in an open position and shall prevent the Generation Facility from supplying power to the Electric Distribution System while in the open position.

## Standards for Interconnection, Safety and Operating Reliability:

The interconnection of a Generation Facility and associated equipment to the Electric Distribution System shall meet the applicable provisions of the following publications or successor standards:

  - IEEE1547 Standard for Interconnecting Distributed Resources with Electric Power Systems (including use of IEEE 1547.1 testing protocols to establish conformity).  The following standards shall be used as guidance in applying IEEE 1574:

    - IEEE Standard 519-1992, IEEE Recommended Practices and Requirements for Harmonic Control in Electrical Power Systems

    - IEC/TR3 61000-3-7 Assessment of emission limits for fluctuating loads in MV and HV power systems

  - UL 1741 Standard for Inverters, Converters and Controllers for Use in Independent Power Systems

  - NFPA 70 (2017), National Electrical Code

  - IEEE Standard 929-2000, IEEE Recommended Practice for Utility Interface of Photovoltaic (PV) Systems

  - IEEE Standard C37.90.1-1989 (R1994), IEEE Standard Surge Withstand Capability (SWC) Tests for Protective Relays and Relay Systems

  - IEEE Standard C37.90.2 (1995), IEEE Standard Withstand Capability of Relay Systems to Radiated Electromagnetic Interference from Transceivers

  - IEEE Standard C37.108-1989 (R2002), IEEE Guide for the Protection of Network Transformers

  - IEEE Standard C57.12.44-2000, IEEE Standard Requirements for Secondary Network Protectors

  - IEEE Standard C62.41.2-2002, IEEE Recommended Practice on Characterization of Surges in Low Voltage (1000V and Less) AC Power Circuits

  - IEEE Standard C62.45-1992 (R2002), IEEE Recommended Practice on Surge Testing for Equipment Connected to Low-Voltage (1000V and Less) AC Power Circuits

  - IEEE Standard 100-2000, IEEE Standard Dictionary of Electrical and Electronic Terms

  - ANSI C84.1-1995 Electric Power Systems and Equipment – Voltage Ratings (60 Hertz)

  - NEMA MG 1-1998, Motors and Generators, Revision 3

  - IEEE Standard 2030.2, Guide for the Interoperability of Energy Storage Systems Integrated with the Electric Power Infrastructure (Including use of IEEE 2030.3 testing protocols to establish conformity).

## Access and Inspection by Utility:

Customer shall provide the Utility reasonable opportunity to inspect the Generation Facility prior to its interconnection and Commercial Operation Date and to witness initial testing and commissioning of the Generation Facility. The Utility may witness any commissioning tests required by IEEE 1547/UL 1741.

Following initial testing and inspection of the Generation Facility and upon reasonable advance notice to Customer, the Utility shall have access at all reasonable times to the Generation Facility to perform on-site inspections to verify that the installation, maintenance and operation of the Generation Facility complies with the requirements of these Interconnection Standards.  The Utility cost of such inspection(s) shall be at Utility expense; however, the Utility shall not be responsible for any cost Customer may incur as a result of such inspection(s).  Upon written request, Customer shall inform the Utility of the next scheduled maintenance and allow the Utility to witness the maintenance program and any associated testing.

The Utility shall at all times have immediate access to the external Generator AC Disconnect Switch to isolate the Generation Facility from the Electric Distribution System.

## Generation Facility Operation:

- Customer shall install, operate, and maintain, at Customer’s sole cost and expense, the Generation Facility in accordance with the manufacturer’s suggested practices for safe, efficient and reliable operation of the Generation Facility in parallel with the Electric Distribution System.  Customer shall bear full responsibility for the installation, maintenance and safe operation of the Generation Facility.  Upon request from the Utility, Customer shall supply copies of periodic test reports or inspection logs.

- Customer shall be responsible for protecting, at Customer’s sole cost and expense, the Generation Facility from any condition or disturbance on the Electric Distribution System, including, but not limited to, voltage sags or swells, system faults, outages, loss of a single phase of supply, equipment failures, and lightning or switching surges.

- Customer agrees that, without prior written permission from the Utility, no changes shall be made to the configuration of the Generation Facility as approved by the Utility, and no relay or other control or protection settings shall be set, reset, adjusted or tampered with, except to the extent necessary to verify that the Generation Facility complies with Utility-approved settings.

- Customer shall operate the Generation Facility in such a manner as not to cause undue voltage fluctuations, power quality issues, intermittent load characteristics or to otherwise interfere with the operation of the Electric Distribution System.  At all times when the Generation Facility is operated in parallel with the Electric Distribution System, Customer shall operate said Generation Facility in such a manner that no disturbance will be produced thereby to the service rendered by the Utility to any of its other customers or to any electric system interconnected with the Electric Distribution System.  Customer understands and agrees that the interconnection and operation of the Generation Facility pursuant to these Interconnection Standards is secondary to, and shall not reduce the safety, quality, or reliability of electric service provided by the Utility.

- Customer’s control equipment for the Generation Facility shall immediately, completely, and automatically disconnect and isolate the Generation Facility from the Electric Distribution System in the event of a fault on the Electric Distribution System, a fault on Customer’s electric system, or loss of a source or sources on the Electric Distribution System.  The automatic disconnecting device included in such control equipment shall not be capable of reclosing until after service is restored on the Electric Distribution System.  Additionally, if the fault is on Customer’s electric system, such automatic disconnecting device shall not be reclosed until after the fault is isolated from the Customer’s electric system.

## Right to Disconnect Generation Facility:

The Utility shall have the right and authority to disconnect and isolate the Generation Facility without notice at Utility’s sole discretion if the Utility believes that any of the following has occurred or is occurring:

  - Electric service to Customer’s premises is discontinued for any reason;

  - Adverse electrical effects (such as power quality problems) on the Electric Distribution System and/or the electrical equipment of other Utility customers attributed to the Generation Facility as determined by the Utility.

  - Electric Distribution System emergencies or maintenance requirements

  - Hazardous conditions existing on the Electric Distribution System as a result of the operation of the Generation Facility or protective equipment

  - Failure of the Customer to maintain required insurance and to provide the Utility with proof of insurance within ten (10) days of request.

  - Utility identification of uninspected or unapproved equipment or modifications to the Generation Facility after initial approval.

  - Recurring abnormal operation, substandard operation or inadequate maintenance of the Generation Facility.

  - Noncompliance with the obligations under the Interconnection Agreement. In non-emergency situations, the Utility shall give Customer notice of noncompliance including a description of the specific noncompliance condition and allow Customer a reasonable time to cure the noncompliance prior to disconnecting and isolating the Generation Facility.

  - In the event that the Utility disconnects the Generation Facility for routine maintenance, the Utility shall make reasonable efforts to reconnect the Generation Facility as soon as practicable.

  - The Customer retains the option to temporarily disconnect its Generation Facility from the Electric Distribution System at any time.  Such temporary disconnection shall not constitute termination of the Interconnection Agreement unless the Customer exercises its termination rights under Section 16 of Part 2.

## Rates and Other Charges:

  - Customer must participate in the applicable Utility Renewable Parallel Generation Rider or Qualifying Facility tariff as a condition of interconnecting a Customer-owned Generating Facility.

  - Customer must complete and submit to the Utility the Renewable Parallel Generation Application For Service in Part 7.  The Utility shall not approve a Customer-owned Generation Facility Interconnection Application that does not include a completed Renewable Parallel Generation Application For Service.

  - Terms and conditions of service are contained in the applicable Renewable Parallel Generation Rider and Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities.

  - Customer must participate in the electric Utility’s applicable Renewable Parallel Generation Rider or Qualifying Facility tariff if the customer wishes to receive compensation for any Excess Generation delivered to the Utility.

## Insurance:

Customer shall at its own expense obtain and continuously maintain bodily injury, property damage liability and general liability insurance, without any exclusion for liabilities related to the interconnection undertaken pursuant to the Interconnection Agreement. The amount of such insurance shall be sufficient to insure against all reasonably foreseeable liabilities and risks related to the Generation Facility, the ownership and operation of such Generation Facility, and the interconnection itself. Such insurance must be obtained from an insurance provider authorized to do business in the State of Ohio. Customer shall provide proof of insurance to the Utility not later than ten (10) days prior to the commercial operation date of the Generation Facility.  Utility shall not interconnect the Generation Facility absent submission by the Customer of proof of insurance in accordance with these Interconnection Standards. Thereafter Customer shall provide proof of insurance to the Utility within ten (10) days of such request by the Utility. Utility receipt of proof of insurance does not imply an endorsement of the terms and conditions of said coverage.  Customer shall promptly notify the Utility whenever an accident or incident occurs resulting in injuries or damages that are included within the scope of coverage of such insurance, whether or not Customer intends to submit a claim under such policy.

## Limitation of Liability and Indemnification:

  - Limitation of Liability

Each Party's liability to the other Party for any loss, cost, claim, injury, liability, or expense, including reasonable attorney's fees and court fees, relating to or arising from any act or omission in its performance of the Interconnection Agreement, shall be limited to the amount of direct damage actually incurred. In no event shall the Utility or the City of Celina be liable for any indirect, special, consequential, or punitive damages.

  - Indemnity

Customer assumes all liability for, and shall indemnify, defend and hold  the Utility and the City of Celina harmless from, any and all claims, losses, costs, and expenses of any kind or character, direct or indirect, including claims and actions relating to injury to or death of any person or damage to property, demand, suits, recoveries, costs and expenses, court costs, attorney fees, labor costs, and all other obligations by or to third parties arising out of or resulting from the design, construction, operation or maintenance of the Generation Facility, or the Customer’s actions or omissions in breach of its obligations under the Interconnection Agreement. Such indemnity shall include, but is not limited to, financial responsibility for: (a) Utility monetary losses; (b) reasonable costs and expenses of defending an action or claim made by a third party; (c) damages related to the death or injury of a third party; (d) damages to Utility property; (e) damages to the property of a third party; (f) damages for the disruption of the business of a third party. The limitations of liability provided in this paragraph do not apply in cases of gross negligence or intentional wrongdoing. If the Utility or the City incurs any costs as to which the indemnity provided in this section b. applies, the Utility or City shall invoice the Customer for such costs in writing. Customer shall remit payment to the Utility or the City, as appropriate, within 45 calendar days of the date of such invoice.

## Effective Term and Termination Rights:

The Interconnection Agreement shall become effective when executed by both Parties and shall continue in effect until terminated in accordance with the provisions of this Section.  The Interconnection Agreement may be terminated for the following reasons:

  - Electric service to Customer’s premises is discontinued for any reason. If electric service is disconnected for any reason or a change occurs in the account holder, a new Interconnection Application must be submitted to the electric Utility  for consideration;

- Customer may terminate the Interconnection Agreement at any time by giving the Utility at least sixty (60) days’ prior written notice stating Customer’s intent to terminate the Agreement at the expiration of such notice period;

- the Utility may terminate the Interconnection Agreement at any time following Customer’s failure to generate energy from the Generation Facility in parallel with the Electric Distribution System by the later of two (2) years from the date of execution of the Interconnection Agreement or twelve (12) months after completion of the interconnection;

- either Party may terminate the Interconnection Agreement at any time by giving the other Party at least sixty (60) days’ prior written notice that the other Party is in default of any of the material terms and conditions of the Interconnection Agreement or these Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities, so long as the notice specifies the basis for termination and there is reasonable opportunity for the Party in default to cure the default; or

- The Utility may terminate the Interconnection Agreement at any time by giving Customer at least sixty (60) days’ prior written notice in the event that there is a change in an applicable rule or statute affecting the Agreement.

Upon termination of the Interconnection Agreement, Customer’s Generation Facility shall be permanently disconnected from the Electric Distribution System.

Termination of the Interconnection Agreement shall not relieve either party of its liabilities and obligations, owed or continuing at the time of said termination.

## Termination of any Applicable Prior Agreement:

From and after the date when service commences under the Interconnection Agreement, the Agreement shall supersede any oral and/or written agreement or understanding between the Utility and Customer concerning the interconnection service covered by the Agreement. Any such prior agreement or understanding shall be deemed to be terminated as of the date interconnection service commences under the Interconnection Agreement.

## Force Majeure:

For purposes of the Interconnection Agreement, the term “Force Majeure” means any cause or event not reasonably within the control of the Party claiming Force Majeure, including, but not limited to, the following: acts of God, strikes, lockouts, or other industrial disturbances; acts of public enemies; orders or permits or the absence of the necessary orders or permits of any kind which have been properly applied for from the government of the United States, the State of Ohio, any political subdivision or municipal subdivision or any of their departments, agencies or officials, or any civil or military authority; unavailability of a fuel or resource used in connection with the generation of electricity; extraordinary delay in transportation; unforeseen soil conditions; equipment, material, supplies, labor or machinery shortages; epidemics; landslides; lightning; earthquakes; fires; hurricanes; tornadoes; storms; floods; washouts; drought; arrest; war; civil disturbances; explosions; breakage or accident to machinery, transmission lines, pipes or canals; partial or entire failure of utilities; breach of contract by any supplier, contractor, subcontractor, laborer or materialman; sabotage; injunction; blight; famine; blockade; or quarantine.  A Force Majeure event does not include an act of negligence or intentional wrongdoing.

If either Party is rendered wholly or partially unable to perform its obligations under the Interconnection Agreement because of Force Majeure, both Parties shall be excused from whatever obligations under the Agreement are affected by the Force Majeure (other than the obligation to pay money) and shall not be liable or responsible for any delay in the performance of, or the inability to perform, any such obligations for so long as the Force Majeure continues.  The Party suffering an occurrence of Force Majeure shall, as soon as is reasonably possible after such occurrence, give the other Party written notice describing the particulars of the occurrence and shall use reasonable efforts to remedy its inability to perform; provided, however, that the settlement of any strike, walkout, lockout or other labor dispute shall be entirely within the discretion of the Party involved in such labor dispute.

# Part 3.  Interconnection Application

Application No. _______

Customer-Owned Inverter-Based Generation Facility 25 kWAC or Less

This Application for Interconnection of a Customer-Owned inverter-based Generation Facility with a design capacity of 25 kWAC or less is considered complete when it provides all applicable and correct information required below.  The Utility may require additional information or clarification to evaluate the Interconnection Application.

Processing Fee

 A non-refundable processing fee of $250 must accompany this Application.

Customer

Name: ____________________________________ Utility Account Number: ____________________

Address: ___________________________________________________________________________

City:   	 State: 	  Zip:

Telephone (Day): 	 (Evening):

Fax: 	 E-Mail Address:

Is the Generation Facility owned by the Customer listed above?         Yes      No

Contact (if different from Customer)

Name:

Address:

City: 	 State: 	  Zip:

Telephone (Day): 	 (Evening):

Fax: 	 E-Mail Address:

- Description of Proposed Installation and Operation

Give a general description of the proposed installation, including how you plan to operate the Generation Facility.

- Generation Facility Information

Location (if different from above):

Energy Source: 	  Solar      Wind      Battery/Storage

Total Nameplate Rating:           (kW) ________ (kVA) ________

Generation Facility Capacity: (kWAC) ________ (kVAAC) _________

Generation Facility Output:  (kWh-annual)

Single Phase ________         Three Phase ________

Inverter Data

Manufacturer: ___________________________ Model: ________________________

Rate Power Factor (%): _______ Rated Voltage (Volts): _______ Rated Amperes: ___________

Inverter Type (square wave, modified sine wave, pure sine wave): _________________

Harmonic Distortion: Maximum Single Harmonic (%) __________________________

Maximum Total Harmonic (%) ___________________________

Note: Attach all available calculations, test reports, and specification sheets

Prime Mover (Solar, Wind, etc.)

Unit Number: _________ Type: ____________________________________________

Manufacturer: __________________________________________________________

Serial Number: _________________________________________________________

Is the Generation Facility equipment UL 1741 certified and IEEE 1547 compliant?       Yes	No

[Note: Requires a Yes for an application to be considered complete.]

If Yes, attach manufacturer’s documentation and technical specification sheet showing UL 1741 certification

Have all necessary government permits and approvals been obtained for the project prior to this application?

 Yes	   No    [Note: Requires a Yes for an application to be considered complete.]

Utility Accessible Exterior Generation Facility AC Disconnect Switch Provided (Required)         Yes	No

Location of Utility Accessible Exterior Generation Facility AC Disconnect Switch

(e.g. Two feet west of electric meter)

Estimated Installation Date: ________________	Estimated Commercial Operation Date: __________________

List components of the Generation Facility equipment package:

Equipment Type 	    Certifying Entity

1.  ______________________________________	    ______________________________________

2.  ______________________________________	    ______________________________________

3.  ______________________________________	    ______________________________________

4.  ______________________________________	    ______________________________________

Equipment Installation Contractor:     Indicate by owner if applicable  

Name:

Mailing Address:

City: 	   State: 	   Zip Code:

Contact Person (If other than Above):

Telephone (Daytime): 		   (Evening):

Facsimile Number: 		   E-Mail Address:

Electrical Contractor:  (As Applicable)     Indicate if not applicable  

Name:

Mailing Address:

City: 	   State: 	   Zip Code:

Contact Person (If other than Above):

Telephone (Daytime): 		   (Evening):

Facsimile Number: 		   E-Mail Address:

Consulting Engineer:  (As Applicable)    Indicate if not applicable  

Name:

Mailing Address:

City: 	   State: 	   Zip Code:

Contact Person (If other than Above):

Telephone (Daytime): 		   (Evening):

Facsimile Number: 		   E-Mail Address:

Provide a one line diagram of the Generation Facility.  The one line diagram is a basic drawing of an electric circuit in which one or more conductors are represented by a single line and each electrical device and major component of the installation, from the Generation Facility to the Point of Interconnection, are noted by symbols.  See attached example.

For this application to be considered complete, adequate documentation and information must be submitted that will allow Utility to determine the impact of the Generation Facility on Utility’s Electric Distribution System and to confirm compliance by Customer with the provisions set forth in the Interconnection Standards and other applicable requirements. Typically this should include the following:

- Single-line diagram of the Customer’s system showing all electrical equipment from the generator to the Point of Interconnection with Utility’s Electric Distribution System.

- Site Plans showing the physical location of major equipment.

- Relevant ratings of equipment.

- If protective relays are used, settings applicable to the interconnection protection. If programmable relays are used, a description of how the relay is programmed to operate as applicable to interconnection protection.

- For Certified equipment, documentation confirming that a nationally recognized testing and certification laboratory has listed the equipment.

- A description of how the generator system will be operated including all modes of operation.

This application is subject to further consideration and study by Utility and the possible need for additional documentation and information from Customer.

Copies of specifications for all Generation Facility equipment (generators, inverters, protective relays, etc.), and any other applicable drawings or documents necessary for the proper design of the interconnection must be submitted with this Application.

Customer Signature

I hereby certify that, to the best of my knowledge, the information provided in this Interconnection Application is true.  I agree to abide by the terms and conditions of the Utility’s Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities and will return the Certificate of Completion to the Electric Utility when the Generation Facility has been installed and prior to commencing operation of said Generation Facility.

Signature: 	   Date: _________________

Utility Use

Contingent Approval to Interconnect the Generation Facility

Interconnection of the Generation Facility is approved contingent upon Customer compliance with all of the terms and conditions of the Utility’s Interconnection Standards and upon return of the Certificate of Completion prior to commencement of Commercial Operation of said Generation Facility.

Utility Signature: __________________________________________________

Title: 	  Date:

Application Number: __________________

Utility waives inspection/witness test?  Yes	No    Initial __________

# Part 3a.  Interconnection Application

Application No. _______

Customer-Owned Renewable Electric Generation Facility Greater Than 25 kWAC or Non-Inverter Based

This Application for Interconnection of a Customer-Owned Renewable Electric Generation Facility with a design capacity greater than 25 kWAC or non-inverter based design is considered complete when it provides all applicable and correct information required below.  The Utility may require additional information or clarification to evaluate the Interconnection Application.

Processing Fee

 A non-refundable processing fee of $250 plus $1.00 per kW of the applicant’s nameplate rating for all kW 
      above 25 kW.

Customer

Name: ____________________________________ Utility Account Number: ____________________

Address: ___________________________________________________________________________

City:   	 State: 	  Zip:

Telephone (Day): 	 (Evening):

Fax: 	 E-Mail Address:

Is the Generation Facility owned by the Customer listed above?         Yes      No

Contact (if different from Customer)

Name:

Address:

City: 	 State: 	  Zip:

Telephone (Day): 	 (Evening):

Fax: 	 E-Mail Address:

- Description of Proposed Installation and Operation

Give a general description of the proposed installation, including how you plan to operate the Generation Facility.

- Generation Facility Information

Location (if different from above):

Type of Generator:   Inverter-Based      Synchronous      Induction      Biomass

  Landfill Gas      Hydropower

Energy Source: 	  Solar      Wind      Battery/Storage

Total Nameplate Rating:           (kW) ________ (kVA) ________

Generation Facility Capacity: (kWAC) ________ (kVAAC) _________

Generation Facility Output:  (kWh-annual)

Single Phase _______	Three Phase ________

Inverter Data (If Applicable)

Manufacturer: ___________________________ Model: ________________________

Rate Power Factor (%): ___ Rated Voltage (Volts): ___ Rated Amperes: ___________

Inverter Type (square wave, modified sine wave, pure sine wave): _________________

Harmonic Distortion: Maximum Single Harmonic (%) __________________________

Maximum Total Harmonic (%) ___________________________

Note: Attach all available calculations, test reports, and specification sheets

Synchronous Generator Data (If Applicable)

Model Number: ______ Total number of units on site: ________

Manufacturer: _________________________________________________________

Type: ______________________ Date of manufacture: _______________________

Serial Number (each): ___________________________________________________

Phases: Single ____Three ___ R.P.M.: _____________ Frequency (Hz): __________

Rated Output (for one unit): _______ Kilowatt _____________ Kilovolt-Amper_____

Rated Power Factor (%): _____ Rated Voltage (Volts) ________ Rated Amperes: _____

Synchronous Reactance (X’d): _____________ % on ________________ KVA base

Transient Reactance (X’d): ________________ % on _________________ KVA base

Subtransient Reactance (X’d): ______________ % on ________________ KVA base

Negative Sequence Reactance (Xs): _________ % on ________________ KVA base

Zero Sequence Reactance (Xo): _____________% on ________________ KVA base

Neutral Grounding Resistor (if applicable): ___________________________________

______________________________________________________________________

I22t of K (heating time constant): ____________________________________________

Additional Information: ___________________________________________________

Induction Generator Data (If Applicable)

Rotor Resistance (Rr): ___________ ohms Stator Resistance (Rs): ___________ ohms

Rotor Reactance (Xr): ___________ ohms Stator Reactance (Xs): ___________ ohms

Magnetizing Reactance (Xm): ______ ohms Short Circuit Reactance (Xd”): _____ ohms

Design letter: _______________________ Frame Size: _________________________

Exciting Current: ____________________ Temp Rise (deg Cº): _________________

Reactive Power Required: _____________ Vars (no load), Vars ________ (full load)

Additional Information: ____________________________________________________

______________________________________________________________________

Prime Mover (Solar, Wind, etc.)

Unit Number: _________ Type: ____________________________________________

Manufacturer: __________________________________________________________

Serial Number: _________________ Date of manufacturer: ______________________

H.P. Rates: ______ H.P. Max.: _______ Inertia Constant: _________________ lb.-ft2

Energy Source (hydro, steam, wind, etc.) _____________________________________

______________________________________________________________________

______________________________________________________________________

Generation Facility Transformer (Complete all applicable items)

TRANSFORMER (between generator and utility system)

Generator unit number: _________ Date of manufacturer: _______________________

Manufacturer: __________________________________________________________

Serial Number: ________________________________________________________

High Voltage: ____ KV, Connection: delta wye, Neutral solidly grounded? _______

Low Voltage: _____ KV, Connection: delta wye, Neutral solidly grounded? ______

Transformer Impedance (Z): ____________ % on ______________________ KVA base

Transformer Resistance (R): ____________ % on _____________________ KVA base

Transformer Reactance (X): ____________ % on _____________________ KVA base

Neutral Grounding Resistor (if applicable: ____________________________________

______________________________________________________________________

Is the Generation Facility equipment UL 1741 certified and IEEE 1547 compliant?       Yes	No

[Note: Requires a Yes for an application to be considered complete.]

If Yes, attach manufacturer’s documentation and technical specification sheet showing UL 1741 certification

Have all necessary government permits and approvals been obtained for the project prior to this application?

 Yes	   No    [Note: Requires a Yes for an application to be considered complete.]

Utility Accessible Exterior Generation Facility AC Disconnect Switch Provided (Required)         Yes	No

Location of Utility Accessible Exterior Generation Facility AC Disconnect Switch

(e.g. Two feet west of electric meter)

Estimated Installation Date: ________________	Estimated Commercial Operation Date: __________________

List components of the Generation Facility equipment package:

Equipment Type 	    Certifying Entity

1.  ______________________________________	    ______________________________________

2.  ______________________________________	    ______________________________________

3.  ______________________________________	    ______________________________________

4.  ______________________________________	    ______________________________________

Equipment Installation Contractor:     Indicate by owner if applicable  

Name:

Mailing Address:

City: 	   State: 	   Zip Code:

Contact Person (If other than Above):

Telephone (Daytime): 		   (Evening):

Facsimile Number: 		   E-Mail Address:

Electrical Contractor:  (As Applicable)     Indicate if not applicable  

Name:

Mailing Address:

City: 	   State: 	   Zip Code:

Contact Person (If other than Above):

Telephone (Daytime): 		   (Evening):

Facsimile Number: 		   E-Mail Address:

Consulting Engineer:  (As Applicable)    Indicate if not applicable  

Name:

Mailing Address:

City: 	   State: 	   Zip Code:

Contact Person (If other than Above):

Telephone (Daytime): 		   (Evening):

Facsimile Number: 		   E-Mail Address:

Provide a one line diagram of the Generation Facility.  The one line diagram is a basic drawing of an electric circuit in which one or more conductors are represented by a single line and each electrical device and major component of the installation, from the Generation Facility to the Point of Interconnection, are noted by symbols.  See attached example.

For this application to be considered complete, adequate documentation and information must be submitted that will allow Utility to determine the impact of the Generation Facility on Utility’s Electric Distribution System and to confirm compliance by Customer with the provisions set forth in the Interconnection Standards and other applicable requirements. Typically this should include the following:

- Single-line diagram of the Customer’s system showing all electrical equipment from the generator to the Point of Interconnection with Utility’s Electric Distribution System, including generators, transformers, switchgear, switches, breakers, fuses, voltage transformers, and current transformers.

- Control drawings for relays and breakers.

- Site Plans showing the physical location of major equipment.

- Relevant ratings of equipment. Transformer information should include capacity ratings, voltage ratings, winding arrangements, and impedance.

- If protective relays are used, settings applicable to the interconnection protection. If programmable relays are used, a description of how the relay is programmed to operate as applicable to interconnection protection.

- For Certified equipment, documentation confirming that a nationally recognized testing and certification laboratory has listed the equipment.

- A description of how the generator system will be operated including all modes of operation.

This application is subject to further consideration and study by Utility and the possible need for additional documentation and information from Customer.

Provide a site layout of the Generation Facility and nearby features.  The site layout is a basic drawing showing the location of the Generation Facility, electric meter(s), AC and DC disconnect switches, existing electrical panels, disconnects, and utility transformers, conduit/conductor runs and lockout locations.

Copies of manufacturer’s ownership, operating and maintenance manuals, specifications for all Generation Facility equipment (generators, transformers, inverters, circuit breakers, protective relays, etc.), test reports and any other applicable drawings or documents necessary for the proper design of the interconnection must be submitted with this Application.

Customer Signature

I hereby certify that, to the best of my knowledge, the information provided in this Interconnection Application is true.  I agree to abide by the terms and conditions of the Utility’s Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities and will return the Certificate of Completion to the Electric Utility when the Generation Facility has been installed and prior to commencing operation of said Generation Facility.

Signature: 	   Date: _________________

Utility Use

Contingent Approval to Interconnect the Generation Facility

Interconnection of the Generation Facility is approved contingent upon Customer compliance with all of the terms and conditions of the Utility’s Interconnection Standards and upon return of the Certificate of Completion prior to commencement of Commercial Operation of said Generation Facility.

Utility Signature: __________________________________________________

Title: 	  Date:

Application Number: __________________

Utility waives inspection/witness test?  Yes	No    Initial __________

# Part 4.  Interconnection Agreement

Application No. _______

City of Celina Electric Utility

Customer-Owned Renewable Electric Generation Facility

This Agreement, (“Agreement”) is entered into by and between the City of Celina Electric Utility (“Utility”) and ___________________________, (“Customer”).  The Customer electric account subject to this Agreement is Account Number _______________.  Customer and Utility are referenced in this Agreement collectively as “Parties” and individually as “Party.”

Recitals

WHEREAS, the Utility owns and operates an Electric Distribution System serving the City of Celina, Ohio, and surrounding area;

WHEREAS, Customer owns or desires to install, own and operate a Utility-approved renewable, electric Generation Facility with a rated output of ________ kWAC, interconnected with and operating in parallel with the Utility Electric Distribution System;

Agreement

NOW, THEREFORE, in consideration of the covenants and promises herein, the Parties mutually agree as follows:

- Scope of Agreement:

This Agreement governs the terms and conditions under which the Generation Facility will interconnect with and operate in parallel with the Electric Distribution System.

- Definitions:

The definitions used in this Interconnection Agreement are those found in Part 1, Section 2 of the Utility Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities.

- Parallel Operation:

Customer shall not interconnect or commence parallel operation of the Generation Facility until written Approval to Energize the Generation Facility under Part 6 of these Interconnection Standards has been provided by the Utility.  The Utility shall have the right to have representatives present during initial testing of the Generation Facility and its protective apparatus.

- Interconnection Costs:

Prior to commencement of System Upgrades that are required to allow interconnection of the Customer-owned Generation Facility, Customer shall deposit with the Utility an amount equal to the estimated cost of said System Upgrades.  If the actual costs of said System Upgrades are less than the amount deposited by the Customer, the Utility shall refund the difference to the Customer within 60 days of completing said System Upgrades.  If the actual costs of said System Upgrades exceed the amount deposited by the Customer, the Utility shall bill the Customer for the difference.  Customer agrees to pay the invoiced amount within 30 days of the invoice date.  The utility will supply, own, and maintain all necessary meters and associated equipment utilized for billing.  In addition, and for the purposes of monitoring customer generation and load, the utility may install at its expense, load research metering.  The customer shall supply, at no expense to the utility, a suitable location for meters and associated equipment used for billing and for load research. All costs related to installation of said meter or meters shall be borne by the Customer.

- Interruption or Reduction of Deliveries:

The Utility may require the Customer to interrupt or reduce energy deliveries when the Utility determines, in its sole discretion, that curtailment, interruption or reduction is necessary because of maintenance, safety, emergency, Force Majeure or compliance with Prudent Utility Practice.  No compensation or credit will be provided to the Customer by the Utility for such interruptions or reductions in energy deliveries.

- Adverse Operating Effects:

The interconnection of the Generation Facility shall not reduce the reliability and quality of Utility Electric Distribution System service.  This includes, but is not limited to power quality issues such as Harmonic Distortion, Voltage Flicker and frequency deviations.  The Utility shall notify the Customer as soon as practicable if, based on Prudent Utility Practice, operation of the Generation Facility causes disruption in or deterioration of service to other Utility electric customers or if operating the Generation Facility could damage the Electric Distribution System.  If, after notice, the Customer fails to timely remedy the adverse operating effect, the Utility may disconnect the Generation Facility with no further notice.

- Compliance with Interconnection Standards Requirements:

Customer has read the Utility Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities, as adopted by the Utility, and agrees to comply with all requirements included therein, including, but not limited to, all insurance and indemnity provisions identified in Paragraphs 13 and 14 therein.

- Access to Premises:

The Utility shall have access to the Customer premises or property and to the Generation Facility’s external AC generator disconnect switch as permitted in its policies, Rules and Regulations and Interconnection Standards.

- Governing Law:

This Agreement shall be interpreted and governed under the laws of the State of Ohio, the Ordinances of the City of Celina, and Utility Electric Rates and Regulations.

- Documents:

This Agreement incorporates all other provisions and related documents of these Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities as the same may be amended from time to time.

- Notices:

All written notices shall be directed as follows:

| Customer: Name: ______________________________ Address: ____________________________ City/State/Zip: ______________________ | Celina Electric Utility: Name: _______________________________ Title: ________________________________ City/State/Zip: _______________________ |
| --- | --- |

- Term of Agreement:

This Agreement shall be in effect when executed by the Customer and the Celina Electric Utility and shall remain in effect thereafter month to month unless terminated in accordance with the provisions of Section 15 of “Part 2 Technical Requirements”.

IN WITNESS WHEREOF, the Parties hereto have caused two originals of this Agreement to be executed by their duly authorized representatives. This Agreement is effective as of the last date set forth below.

| Customer: ___________________________________ Signature ___________________________________ Print Name ___________________________________ Date | Celina Electric Utility: ___________________________________ Signature ___________________________________ Print Name and Title ___________________________________ Date |
| --- | --- |

# Part 5.  Certificate of Completion

Application No. _______

City of Celina Electric Utility

Customer-Owned Renewable Electric Generation Facility

Is the Generation Facility installed, tested and ready for operation? Yes______ No ______

Customer: __________________________________	Utility Account Number:

Address: ____________________________________

Telephone (Day): _____________________________  	(Evening):

Fax: ________________________________________ 	E-Mail Address:

Location of the Generation Facility (if different from above): ________________________________________

Has the Generation Facility been installed in accordance with all applicable building codes, permits and ordinances (if applicable)?  Yes______ No ______

Electrician/Service Company:

Name: _____________________________________

Address: ___________________________________

City/State/Zip: _________________________________

Telephone (Day): ____________________________	(Evening):

Fax: _______________________________________	E-Mail Address:

License number: _____________________________

Date electric Utility approved Interconnection Application: ______________

Application Number: ___________

Inspection:

The Generation Facility has been installed and inspected in compliance with all applicable electrical codes.

A copy of the signed electrical inspection form is attached.  Yes  No

(If inspection form is not attached)

______________________________________ 	__________________

Signature of Inspector: 					Date

__________________________________

Printed name of Inspector

Insurance:

The Generation Facility is covered with an insurance policy as described in the Technical Requirements, 13 and 14.  A copy of proof of insurance is attached.  Yes  No

# Part 6.  Approval to Energize Generation Facility

Application No. _______

City of Celina Electric Utility

Customer-Owned Renewable Electric Generation Facility

The Celina Electric Utility, having entered into an Interconnection Agreement for the Generation Facility described in the Application noted by number above and having received a Certificate of Completion with proper documentation of the electrical inspection hereby authorizes the Generation Facility to be energized:

Electric Utility Signature:

Title: 	  Date:

# Part 7.  Renewable Electric Generation Application for Service

Application No. _______

City of Celina Electric Utility

Customer Name:

Service Address:

City: 	   State: 	   Zip:

Utility Account Number:

Contact Person:

Telephone Number:

Address:

City: 	   State: 	   Zip:

E-Mail Address:

This application is for electric service under the applicable City of Celina Electric Utility (“Utility”) rate schedule or rider for customer-owned parallel generation.  The Customer elects to operate the Generation Facility defined in Utility Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities under the following rate tariff or rider:

Rider “C” – Renewable Parallel Generation Rider   

Rider “D” – Qualifying Facility Service   

The Generation Facility meets the definitions and requirements of said Interconnection Standards.  Total rated output of the Generation Facility is __________ kWAC.  Customer acknowledges that he/she has read the Qualifying Facility (QF) schedule and/or applicable rider and agrees to all terms and conditions contained therein, including without limitation those specified in the Interconnection Standards for Installation and Parallel Operation of Customer-Owned Renewable Electric Generation Facilities.  Specifically, the Customer understands and agrees that an electric meter or meters capable of registering the flow of electricity in each direction must be in service at the Generation Facility.  If a Utility-approved meter with this capability is not in service, Customer must submit a written request to the Utility to acquire, install, maintain, and read an approved meter at the Customer’s cost.  All costs related to installation of said meter or meters shall be borne by the Customer.

Customer acknowledges that he/she understands and agrees the Qualifying Facility schedule or applicable rider language and rates are subject to change.  Customer further acknowledges there shall be no “grandfathering” pertaining to schedule/rider rates and language of customers operating Utility approved Customer-owned Generation Facility.

| Requested By: ___________________________________ Customer Name ___________________________________ Authorized Signature ___________________________________ Date | Approved By: ___________________________________ Name ___________________________________ Utility Signature ___________________________________ Date Rejected: ___________________________________ Name ___________________________________ Utility Signature ___________________________________ Reason for Rejection ___________________________________ Date |
| --- | --- |

Exhibit 1

Interconnection Service – Pre-application Request

I am considering the installation of a ____ kWAC Generation Facility that will require interconnection service with Utility’s Electric Distribution System. I am requesting a pre-application report for the site listed below. I understand the pre-application report will only include pre-existing data that is available as of the date it is prepared and that Utility is not obligated to conduct a study or other analysis in the event the data is not readily available. I also acknowledge the data is subject to change and may not be applicable at the time an interconnection service application is submitted. Enclosed is the $300 nonrefundable processing fee.

Please proceed with preparing the Interconnection Service Pre-application Report.

Account Number:

Street Address:

City:

Print Customer Name:

Customer Signature:

Date:

Type of Generation: