## Read Me
Appendix C. Railroad Utility Occupancy Policies and Requirements Author: Gina Filosa, Volpe Center The Excel workbook provides information on the seven class I railroad company's utility accomodation policies and requirements for the longitudinal installation of wireline utilities in the rail right-of-way. The table provides information on the policies and requirements for above-ground versus below-ground installations. Disclaimer: The information in the table is provided for informational purposes only and is not guaranteed to be accurate, complete, current or error-free. User should consult directly with the railroad company to obtain information on the applicable policies, procedures, and requirements for longitudinal installations in the rail right-of-way. This research is a part of the Electric Transmission in Transportation Rights-of-Way Gaps Analysis written by the U.S. Department of Transportation’s Volpe Center and the Pacific Northwest National Laboratory (PNNL) for the Joint Office of Energy and Transportation. The full report will be published late summer 2025. Questions or Feedback? Please contact the Volpe Center Point of Contact: Maiya Baum Email: maiya.baum@dot.gov | What was updated? | Date
| Initial version | 2025-06-30
O'Neil R.S., M. Baum, J. Yoshimura, G. Filosa, M.A. Cruz, V.A. Hamilton, and J.B. Kincaid. 2025. “Electric Transmission in Transportation Rights-of-Way: Gaps Analysis - Data Appendices.” PNNL-SA- 213383. Richland, WA: Pacific Northwest National Laboratory; Cambridge, MA: John A. Volpe National Transportation Systems Center.

## Rail Utility Policies
Disclaimer: The information in the table is provided for informational purposes only and is not guaranteed to be accurate, complete, current or error-free. User should consult directly with the railroad company to obtain information on the applicable policies, procedures, and requirements for longitudinal installations in the rail right-of-way.
Railroad | Policy/Manual Link | General Policy | General Process | Aboveground Wireline Installations | [5 empty] | Belowground Wireline Installations
|  |  |  | Poles/Towers Distance from Track | Distance from Property Line | Location Restrictions | Overhead Clearance | Design Codes | Inductive Interference Study | Distance from Property Line | Distance from Track | Location Restrictions | Depth of Installation | Encasement
CSX | https://www.csx.com/index.cfm/customers/value-added-services/property-real-estate/permitting-utility-wireless-infrastructure-installations-and-rights-of-entry/ | It is to be clearly understood that CSXT owns its right-of-way for the primary purpose of operating a railroad. All occupancies shall therefore be designed and constructed so that rail operations and facilities are not interfered with, interrupted, or endangered. In addition, the proposed facility shall be located to minimize encumbrance to the right-ofway so that the railroad will have unrestricted use of its property for current and future operations. | Receive approval by CSXT of all engineering and construction details, execute an appropriate CSXT occupational agreement, and remit payment of any required fees and/or rentals specified therein. | Located outside ROW or not less than 25 feet from nearest track, whichever is greater. If locating the poles or towers outside the right of way is not possible, the side clearance of poles and towers from the nearest track rail shall be not less than 25 feet. Structures and guy wires shall be placed in a location that does not interfere with drainage and ditches. | Wirelines running longitudinally along CSXT’s right-of-way shall be constructed as close to property lines as possible, except in cases where doing so will interfere with Railroad operations, surface drainage, or soil stability. |  | Guy wires and suspension cable systems may be located no closer than 27 feet above top of rail. Overhead Clearance is based on line to line voltage. Range is: 750V and below: 27', increasing up to 765KV: 54'10" | Conform to the requirements of the National Electrical Safety Code, as published by the National Standards Institute, Inc., the latest revised edition of same being controlling. The crossing and/or longitudinal is also to conform to the requirements of any local or state laws or regulations of any local code enforcing authority that may be in effect at the time of the installation. | An inductive interference coordination study is required for all proposed electrical power longitudinal occupations. | Located as far as practicable from any tracks or other important structures. | Located as close to the railroad property line as possible. | Longitudinal Wirelines must not be located in earth embankments or within ditches located on the right-of-way. Wirelines shall not be placed within a culvert, under railroad bridges, nor closer than 45 feet to any portion of any railroad bridge, building, or other important structure. | Under special circumstances, underground crossings of power supply cables with maximum voltage of 750 volts may be installed by pushing (jacking) a galvanized steel pipe under the tracks, provided such pipe extends at least 15 feet beyond the outside rail on each end of the crossing and the cable is buried at least 4 feet below the base of rail and 3 feet below ditch bottoms at all other points on the property of CSXT. | Underground crossings of power supply cables operating above 750 volts shall be enclosed in galvanized steel pipe or approved concrete encased duct for mechanical protection of the cable. No cable of this potential which is unprotected will be permitted.
BNSF Railway | https://www.bnsf.com/bnsf-resources/pdf/about-bnsf/utility.pdf | The policy was developed in the interest of safety, protection, utilization, and future development of BNSF with due consideration given to public and private service afforded by adequate and economical utility installations. Utility lines shall be located to avoid, or minimize, the need for adjustments for future railroad improvements and to permit access to the utility lines for their maintenance with minimum interference to railroad traffic. | Approved requests to install, maintain, relocate, or remove a utility within the property of BNSF shall be authorized by a Utility License Agreement. All applications for utility license agreements along with plans for the proposed installation shall be submitted to BNSF and approved before construction has commenced. | Poles must be located a minimum of fifty (50) feet out from the centerline of railroad main, branch and running tracks, CTC sidings, and heavy tonnage spurs. Pole location adjacent to industry tracks; must provide at least a 10-foot clearance from the centerline of track, when measured at right angles. If located adjacent to curved track, then said clearance must be increased at a rate of one and one-half (1-½) inches per degree of curved track. Regardless of the voltage, un-guyed poles shall be located a minimum distance from the centerline of any track, equal to the height of the pole above the ground-line plus 10 feet. If guying is required, the guys shall be placed in such a manner as to keep the pole from leaning/falling in the direction of the tracks. Poles (including steel poles) must be located a minimum distance from the railroad signal and communication line equal to the height of the pole above the ground-line or else be guyed at right angles to the lines. | Within ten (10) feet or less of the property line | High voltage towers (34.5 kV and higher) must be located off railroad right of way. Overhead crossings must not be installed within 500 feet of any railroad bridge, or 300 feet from the centerline of any culvert or track switch area. | To ensure that overhead wire crossings are clear from contact with any equipment passing under such wires, lines shall be constructed with a minimum clearance above top of rail (ATR) as required by NESC + 3 feet or greater. | Utility installations, on, over or under BNSF property shall conform with the requirements contained herein, or the appropriate requirements outlined in the following, whichever is deemed most safe: (1) Safety Rules for the Installation and Maintenance of Electric Supply and Communication Lines-National Electric Safety Code. (2) Title 49 C.F.R. Part 192, Transportation of Natural and Other Gas by Pipeline: Minimum Federal Safety Standards. (3) Title 49 C.F.R. Part 195, Transportation of Hazardous Liquids by Pipelines. (4) American Society for Testing and Materials (ASTM) Specifications - latest edition. (5) Manual on Uniform Traffic Control Devices for Streets and Highways (MUTCD) - latest edition, published by the Federal Highway Administration (FHWA) of the United States Department of Transportation (USDOT). (6) Rules and Regulations for Public Water Systems - latest edition, published by the appropriate State Health Department. (7) Occupational Safety and Health Administration (OSHA) Title 29 C.F.R. Standard 1926 – Safety and Health Regulations for Construction. | Generally, if the proposed electrical line exceeds 12.5 kV and runs parallel to the track for at least 1,000 feet, an inductive coordination study will be required. A study will be required if a new sub-station is to be located within 1,000 feet of the track. |  | Whenever feasible, all underground wirelines should be installed within five (5) feet from property lines. | The Utility Owner will not be permitted to route facilities through drainage structures or cattle passes. | A minimum depth of six (6) feet Below Natural Grade (BNG) for underground wirelines. All utilities crossing under ditches and railroad trackage using jacking and dry boring installation should have a minimum depth of cover of six (6) feet below the flowline of the ditch or ground surface and eight (8) feet – three (3) inches from base of rail. In fill sections, the natural ground line at the toe of slope will be considered as ditch grade. Boring pits shall be located outside railroad property, when possible, at a minimum of thirty (30) feet from the centerline of track and kept to the minimum size necessary. | Underground electric and fiber installations must be encased completely across the Railroad right-of-way with a rigid conduit. The conduit can be steel, HDPE SCH 80, HDPE SDR-11, or HDPE SDR-9 (with no casing pipe for a single conduit). Any installations crossing BNSF with multiple duct installations must be in a single casing unless they are placed 5’ or more apart. A metallic ribbon or wire must be included in the pipe to allow for radio locating later.
CN | https://www.cn.ca/-/media/files/delivering-responsibly/safety/utility-installation/utility-crossing-encroachment-application-packet.pdf |  |  | All utilities must be a minimum of 15 ft horizontally away from any existing or planned CN signals and facilities, when practicable. Minimum distance in any direction from a vertical road crossing gate shall be no less than 4 ft. | All longitudinal utilities shall be placed towards the outer edge of the railroad right-of-way, except in special cases and be of special design as approved by the CN Chief Engineer or the designated representative. | Utilities shall not be placed within a culvert, under railroad bridges, nor closer than 300 feet to any portion of any railroad bridge, building, or other structure | Minimum clearance above top of rail is 27' for voltage up to 750, and then a 0.5” increase for every 1,000 volts in excess of 50 KV and a 6.0” increase for every 12,000 volts in excess of 50 KVs. Minimum Clearance (Including Static Wires) Required above Communication and Signal Lines is 4' for voltage up to 750, with increases up to 16' for voltage of 290,000. | All clearances and safety provisions are subject to the National Electric Safety Code (American National Standard Institute) as well as any applicable National, State, and local codes, whicheveris more restrictive. | All overhead electrical utilities will require an induction interference study | No excavation can be closer than 25 ft. from the centerline of the nearest track. Longitudinal lines must be a minimum of 25 ft. from the center line of track, or outside the track embankment section, whichever is greater. |  | Utilities shall not be placed within a culvert, under railroad bridges, nor closer than 100 feet to any portion of any railroad bridge, building, or other structure, except in special cases and be of special design as approved by the CN Chief Engineer or the designated representative. | Uncased steel carrier pipe utilities laid longitudinally on the railroad right-of-way, 25 ft. to 50 ft. from the center line of the nearest rail shall be buried not less than 6 ft. from the natural ground surface to the top of pipe. If distance is more than 50 ft. from centerline of track, minimum cover shall be 5 ft. | All underground utilities shall have an adequate casing for protection
CP | https://www.cpkcr.com/content/dam/cpkc/documents/english/pdfs/community/CP-Utility-Specs-and-Application-Process.pdf | It is to be clearly understood that CPR owns its right-of-way for the primary purpose of operating a railroad. All utility occupancies shall therefore be designed and constructed so that rail operations and facilities are not interfered with, interrupted, or endangered. In addition, the proposed facility shall be located to minimize encumbrance to the right-of- way so that the railroad will have unrestricted use of its property for current and future operations. | Utility License Agreements are required when utility facilities are installed, relocated, removed, or maintained along or across all Canadian Pacific Railway (CPR) property. | Poles must be located fifty (50) feet out from the centerline of railroad main, branch and running tracks, CTC sidings, and heavy tonnage spurs. Pole locations adjacent to industry tracks; must provide at least ten (10)-foot clearance from the centerline of the nearest track, when measured at right angles. If located adjacent to curved track, then said clearance must be increased at a rate of one and one-half (1-1/2) inches per degree of curved track. Regardless of the voltage, un-guyed poles shall be located a minimum distance from the centerline of any track, equal to the height of the pole above the ground-line plus ten (10) feet. Poles (Including steel poles) must be located a minimum distance from the railroad signal and communication lines equal to the height of the pole above the ground-line or else be guyed at right angles to the lines. |  | High voltage towers (34.5 kV and higher) must be located off railroad right-of-way. | Overhead wire crossings must provide a minimum clearance of twenty-seven (27) feet above top of rail (ATR). High voltage power lines will require additional clearance as follows: • </= 750 volts (includes fiber optic) = 27’0” ATR (NESC + 3’) • > 750 V and < 50,000 V = 29’ 6” ATR (NESC + 3’) • >/= 50,000 V = 27’ (NESC) + 3 = 30’ 0” ATR plus 0.4” per 1,000 V over 50kV Poles, cross arms and anchors must provide at least a ten (10)-foot side clearance and four (4) feet above existing signal and communication lines. | Utilities will be located to provide a safe environment and shall conform to the current “National Electrical Safety Code,” and “The American Railway Engineering and Maintenance Association (AREMA) Recommendations.” Where laws or orders of public authority prescribe a higher degree of protection, then the higher degree of protection prescribed shall supersede the provisions of this document. | All applicants who have equipment in excess of 200 kilovolts (kV) and 250 feet in length; parallel occupancies of over one mile in length with voltage >= 69 kV; and cathodic protection using impressed current, should there expect to be, or in the future appear to be electrical interference with CPR equipment (electromagnetic, electrostatic, or ground potential rise) from nearby electrical facilities, the applicant must participate with CPR in a joint Electrical Coordination Study to find a technically viable and reasonably economical solution. |  | The minimum length of casing pipe, measured perpendicular to and on each side of any track, shall be the greater of: • La = In fill sections, two (2) ft beyond the toe of slope, or • Lb = In cut sections, three (3) ft beyond ditch, or • 25 ft beyond centerline of nearest track, or • The entire width of the railroad right-of-way. |  | Minimum pipe cover for steel and polyethylene pipe cased utilities parallel to any track shall be six (6) ft or depth below frost line, whichever is greater. | Steel casing pipes shall have a wall thickness conforming to E-80 loading requirements, be coated, and designed for the external applied pressures and installed in accordance with American Railway Engineering and Maintenance-of-way Association (AREMA) Manual for Railway Engineering Chapter 1 part 5 Section 5.1, latest edition. Corrugated metal (CMP) casing may also be used in accordance with CPR Standard plan B-1-4950-2. Polyethylene casing pipes shall have a wall thickness conforming to E-80 loading requirements and designed for the external applied pressures and installed in accordance with American Railway Engineering and Maintenance-of-way Association (AREMA) Manual for Railway Engineering Chapter 1 part 5 Section 5.1, latest edition. Polyethylene casing pipes shall not have an outside diameter greater than four and one half (4-1/2) inches
Norfolk Southern Corportation | https://www.norfolksouthern.com/en/rail-development-property/ns-property/projects-on-ns-property | It is to be clearly understood that NS owns its property for the primary purpose of operating a railroad. All occupancies shall therefore be designed and constructed so that rail operations and facilities are not interfered with, interrupted or endangered. In addition, the proposed facility shall be located to minimize encumbrance to the property so that the railroad will have unrestricted use of its property for current and future operations. | Individuals, corporations or municipalities desiring occupancy of NS property by wireline occupations must agree, upon approval of the engineering and construction details by NS, to execute an appropriate NS occupational license agreement, pay any required fees and/or rentals outlined in the agreement, and meet all NS insurance requirements. | Poles including guy cable, subs, or anchors shall be located in no instance closer than 28-feet from face of pole to centerline of nearest track. | Poles including guy cable, subs, or anchors shall be located as close to NS property line as possible. |  | Vertical clearance from the top of rail to the bottom of sag of aerial wire crossing, measured at 60- degrees Fahrenheit, shall be as follows: -Guy wires, messenger cables, and telecommunication cables: 27 feet - Electric supply lines and neutral wires (voltage is measured phase-to- ground) less than 750V: 30 feet 750V-15KV: 31 feet 15KV-50KV: 33 feet | Overhead power and communication lines shall be constructed in accordance with the National Electrical Safety code (current edition), Part 2, “Safety Rules for the Installation and Maintenance of Overhead Electric Supply and Communication Lines”, except as outlined further in this section. Any tower or steel pole to be installed on NS property must meet or exceed the industry standards regarding design and usage. | An inductive interference coordination study is required for all proposed longitudinal occupations. | Conduits laid longitudinally on NS property shall be located as far as practicable from any tracks or other important structures | Conduits laid longitudinally on NS property shall be located as close to the NS property line as possible. | Conduits shall not be placed within a culvert, under railroad bridges, nor closer than 50-feet to any portion of any railroad bridge, building, or other important structure, except in special cases, and then by special design, as approved by NS or its authorized representative. Longitudinal conduits must not be located in earth embankments or within ditches located on the property. | Parallel occupancy: 4-feet
Union Pacific | https://www.up.com/real_estate/utilities/encroach_procedure/encroach_guide/index.htm |  | Must submit an application for encroachment accompanied by complete engineering plan. If approved, an the railroad and the applicant will enter into a agreement. Licensing fees apply. | The wireline/pipeline (encroachment) must be located a minimum of 35 feet from centerline of nearest track. | The wireline/pipeline (encroachment) must be located at the outer limits of railroad right-of-way within 5 feet of property line. | Cannot be installed in the slope of cut or fill sections. |  |  |  |  | The ends of steel casing will have to be a minimum of 30 feet from centerline of the track when measured at right angle to the track. Also, bore pits must be a minimum of 30 feet from centerline of track when measured at right angle to the track. | No bore pits can be located in the slope of a cut or fill section of the roadbed. The encroachment must be located behind (field side) all signal facilities because of the numerous underground signal cable running between track and the signal facility. | If the proposed location of the encroachment crosses existing culverts, the top of the buried encroachment will have to be installed a minimum of 5' below the culvert invert. If the location crosses a ditch beyond the end of the culvert (field side) then the top of the buried encroachment must be installed 5' below the clean bottom elevation of the ditch.
Amtrak | https://www.amtrak.com/content/dam/projects/dotcom/english/public/documents/corporate/engineering-practices/engineering-specs/ce-4-specification-for-wire-conduit-cable-occupations-in-electrified-territory.pdf |  |  |  | Wires and cables running longitudinally along Railroad right of way shall be constructed as close to Railroad property lines as possible. |  |  | Power and communication lines shall be constructed in accordance with Amtrak’s Electrification Standards and “Safety Rules for the Installation and Maintenance of Electric Supply and Communications Lines, National Electrical Safety Code Handbook”, (current issue). | On agreements covering occupations, provisions will be included that the applicant will conduct appropriate EMI/EMF studies and provide appropriate remedies, at his own expense, to correct any inductive interference with Railroad facilities.