Penn Cove Water and Sewer District (#66950)

2025 Water Quality Report / Consumer Confidence Report

📋 Water Quality Terminology

• MCLG (Maximum Contaminant Level Goal): Level with no known health risk.
• MCL (Maximum Contaminant Level): Highest level allowed in drinking water.
• AL (Action Level): Triggers treatment requirements.
• Units: ppm/mg/L (milligrams/liter) | ppb/µg/L (micrograms/liter) | ppt/ng/L (nanograms/liter).

⚠️ 2025 Violations & Exceedances

| Contaminant | Limit (MCL) | 2025 Test Results | Health & Aesthetic Effects |
| --- | --- | --- | --- |
| Total Trihalomethanes (TTHM) | 80 µg/L | • Mar 11: 143 µg/L • May 13: 117.1 µg/L • Aug 12: 103.2 µg/L • Nov 18: 103.7 µg/L | Violation: Yes. Long-term exposure above MCL may cause liver, kidney, or central nervous system problems, and increased cancer risk. |
| Conductivity | 700 µmhos/cm (Secondary) | • Well 2: Apr 848 / Aug 900 µmhos/cm • Well 3: Apr 1027 / Aug 1100 µmhos/cm | Violation: Yes. Aesthetic only; poses no health risk. |
| Total Dissolved Solids (TDS) | 500 mg/L (Secondary) | • Aug 12: 510 mg/L | Violation: Yes. Aesthetic only; poses no health risk. |

✅ 2025 Tests Passed

• Total Coliform (MCL: 0 positive samples/month) | Violation: No
  All monthly samples: Absent /100ml
• Haloacetic Acids (HAA5) (MCL: 60 µg/L) | Violation: No
  Mar 11: 42.5 µg/L  |  May 13: 38.6 µg/L  |  Aug 12: 42.6 µg/L  |  Nov 18: 5.3 µg/L

ℹ️ Important Health Information

Vulnerable Populations: Some people may be more vulnerable to contaminants in drinking water than the general population (including immunocompromised individuals, the elderly, and infants). Please seek advice from your health care provider. Safe Drinking Water Hotline: 800-426-4791.

Lead and Copper: Elevated lead levels can cause serious health problems, especially for pregnant women and young children. If water has sat in your pipes for several hours, flush your tap for 30 seconds to 2 minutes before drinking. More information: epa.gov/safewater/lead

📞 Contact & Resources

• Phone: 360-679-4908  |  • Email: penncovewater@gmail.com
• Official Lab Results Online: https://fortress.wa.gov/doh/eh/portal/odw/si/Intro.aspx (Search: "sentry doh")