## Summary Output
Generation Scenarios Cost Comparison - Delivery of 1.4 GWh per annum
Base Case 1.4Gwh, 5% cost of capital diesel at 87p per litre delivered. |  | 100% Diesel (current) | Mix 1 Wind, Solar Diesel standby | Mix 2 Wind, Solar Diesel standby | Mix 3 Wind, Solar, Storage, Diesel standby | Mix 4 Wind, Solar,Storage, Diesel standby | 100% renewable, Wind,Solar, Storage (updated Narec) | 100% Wind & Storage | 100% Solar & Storage
Estimated total capital cost (£) |  | 2861023.9167 | 4058923.9167 | 4700223.9167 | 5014823.9167 | 5595623.9167 | 30279623.9167 | 9908063.9167 | 11057563.9167
tariff required at 5% cost of capital |  | 60.771 | 47.9423 | 50.9647 | 53.1664 | 57.5881 | 242.2251 | 90.2061 | 97.6256
Annual cost to deliver 1.4GWh per annum assuming 25 year loan at 5% (£s) | Fuel | 328133.9308 | 24717.1119 | 0 | 0 | 0 | 0 | 0 | 0
| Interest (year 1) | 214576.7938 | 304419.2938 | 352516.7938 | 376111.7938 | 419671.7938 | 2270971.7938 | 743104.7938 | 829317.2938
| Repayment of principal (year 1) | 42087.5834 | 59709.497 | 69143.4507 | 73771.428 | 82315.3861 | 445433.6051 | 145754.275 | 162664.192
| Operating costs | 265996.2392 | 282346.2392 | 291846.2392 | 294446.2392 | 304246.2392 | 674746.2392 | 374026.2392 | 374776.2392
| Total annual cost | 850794.5471 | 671192.1418 | 713506.4836 | 744329.4609 | 806233.419 | 3391151.638 | 1262885.3079 | 1366757.7249
Net profit before tax (year 1 £s) assuming tariff of 60p/kWh |  | -83147.9203 | 66160.3985 | 7628.0104 | -31150.9896 | -107742.9896 | -3316902.9896 | -673453.5896 | -806396.0896
Cash flow (year 1 £s)assuming tariff of 60p/kWh |  | -10794.5471 | 168807.8582 | 126493.5164 | 95670.5391 | 33766.581 | -2551151.638 | -422885.3079 | -526757.7249
NPV over 25 years at 5% (£s) |  | -152137.7484 | 2379168.5957 | 1782792.6076 | 1348375.2742 | 475904.3204 | -35955789.7659 | -5960122.087 | -7424094.175
Cost per kWh to deliver 1.4GWh per annum assuming 25 year loan at 5% (£000s) (p/kWh) | Fuel | 23.4381 | 1.7655 | 0 | 0 | 0 | 0 | 0 | 0
| Interest (year 1) | 15.3269 | 21.7442 | 25.1798 | 26.8651 | 29.9766 | 162.2123 | 53.0789 | 59.2369
| Repayment of principal (year 1) | 3.0063 | 4.265 | 4.9388 | 5.2694 | 5.8797 | 31.8167 | 10.411 | 11.6189
| Operating costs | 18.9997 | 20.1676 | 20.8462 | 21.0319 | 21.7319 | 48.1962 | 26.7162 | 26.7697
| Total annual cost | 60.771 | 47.9423 | 50.9647 | 53.1664 | 57.5881 | 242.2251 | 90.2061 | 97.6256
Margin at tariff of 60p /kWh |  | -0.77104 | 12.0577 | 9.0353 | 6.8336 | 2.4119 | -182.2251 | -30.2061 | -37.6256
check |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## Generation & Ops Scenarios
Notes
Tariff (p) | 60 | Gen Capital/100kW /Storage/100kWh (£) |  |  | Yield kWh/kW installed |  |  |  | Capital costs based on current prices for diesel, updated quotes on wind turbines, recent actual costs on Sark for Solar and storage. Economies should be available with firm quotes. Wind turbine costs are basedon 500MW unit, costs vary considerably with size of turbine.
Total Consumption (kWh) | 1400000 | Diesel | 15000 |  | Wind | 39%
Auxiliary diesel power station consumption (fixed) | 0.5% | Wind | 200000 |  | Solar | 12.5%
Auxiliary diesel power station consumption (variable) | 2% | Solar | 130000 | [5 empty] | Yields
Line losses | 4% | Storage /100kWh | 240000 | [5 empty] | Yield will depend on actual solar panels selected, this is mid range
| 1497326.2032 | [7 empty] | Yield will depend on actual turbine selected, this is mid range
Daylight hours consumption -45% (kWh) | 673796.7914
Darkness hours consumption (-55%kWh) | 823529.4118
Fuel
Debt Finance | 100% | Staff | [6 empty] | Based on 80p /litre plus 7p/litre transport
Debt Term (years) | 25 | Administration | 40000 | [5 empty] | Conversion efficiency from manufacturers data for Cummins 200kVA generator
Amortisation period (years) | 25 | Operational | 160000
Interest Rate | 7.5% | Rent | [6 empty] | Rent
|  | Office &PS fixed | 14000 | [5 empty] | Based on land rental of £200/acre/p.a. if not on island owned land
Operating Costs |  | Solar /100kW | 100 | [5 empty] | Based on nominal rental for turbine if not on island owned land
Fuel (diesel p/litre) need to update for firm price of diesel delivered to Sark | 87 | Wind/100kW | 50
Efficiency kWh/litre assuming 0.95 power factor- need to update for specific engine | 3.9583 | [7 empty] | Operating costs are realistic best estimates
Annual Operating Costs as % of capital
Operating Costs (diesel generation) | 15% |  |  |  | Discount rate | 5%
Operating Costs (solar generation) | 1%
Operating Costs (wind generation) | 2%
Operating Costs (Storage) | 2%
Operating Costs (distribution) | 1%
| 100% Diesel (current) | Mix 1 Wind, Solar Diesel standby | Mix 2 Wind, Solar Diesel standby | Mix 3 Wind, Solar, Storage, Diesel standby | Mix 4 Wind, Solar,Storage, Diesel standby | 100% renewable, Wind,Solar, Storage (updated Narec) | 100% Wind & Storage | 100% Solar & Storage
Total units generated to meet annual consumption (kWh) | 1492946.5241 | 1465878.1241 | 1463000 | 1463000 | 1463000 | 1456000 | 1456000 | 1456000 | Assume auxiliary consumption only required for diesel facilities
Auxiliary diesel power station consumption - fixed kWh) | 7000 | 7000 | 7000 | 7000 | 7000 | 0 | 0 | 0 | In the absence of any firm details for power station, auxiliary consumption and line losses taken as a percentage of units consumed.
Auxiliary diesel power station consumption - variable (kWh) | 29946.5241 | 2878.1241 | 0 | 0 | 0 | 0 | 0 | 0
Line losses (kWh) | 56000 | 56000 | 56000 | 56000 | 56000 | 56000 | 56000 | 56000
Total annual consumption (kWh) | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Diesel Generation Capacity (kW) | 600 | 600 | 600 | 600 | 600 | 0 | 0 | 0
Wind Generation Capacity (kW) | 0 | 300 | 500 | 500 | 500 | 500 | 500 | 0
Solar Generation Capacity (kW) | 0 | 300 | 400 | 600 | 600 | 3000 | 0 | 1500
Storage Capacity minimum firm peak output (kW) | 0 | 0 | 0 | 0 | 0 | 250 | 250 | 250
Storage Capacity (kWh) | 0 | 0 | 0 | 0 | 200 | 7500 | 2110 | 2110
Units from solar used at time of generation (kWh) | 0 | 328500 | 438000 | 657000 | 657000 | 673796.7914 | 0 | 673796.7914
Units from wind used at time of generation (kWh) | 0 | 1024920 | 1025000 | 806000 | 806000 | 782203.2086 | 1456000 | 0
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 2611203.2086 | 0 | 968703.2086
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 902200 | 925996.7914 | 252200 | 0
Total Renewable energy available for use(kWh) | 0 | 1353420 | 1463000 | 1463000 | 2365200 | 4993200 | 1708200 | 1642500
Renewabe energy used via storage (kWh) | 0 | 0 | 0 | 0 | -63000 | -56000 | -56000 | 726203.2086
Units generated by diesel (kWh) | 1492946.5241 | 112458.1241 | 0 | 0 | 0 | 0 | 0 | 0
Annual Energy Shortfall(kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximmum annual energy from all sources (kWh) | 3504000 | 4857420 | 5650200 | 5869200 | 5869200 | 4993200 | 1708200 | 1642500
Maximmum peak demand from all sources (daylight) (kW) | 400 | 1000 | 1300 | 1500 | 1500 | 3750 | 750 | 1750
Maximmum peak demand from all sources (darkness) (kW) | 400 | 700 | 900 | 900 | 900 | 750 | 750 | 250
Diesel Load Factor (%) | 28.4046 | 2.1396 | 0 | 0 | 0 | N/A | N/A | N/A
Diesel Generation Capital (£) | 90000 | 90000 | 90000 | 90000 | 90000 | 0 | 0 | 0
Wind Generation Capital (£) | 0 | 600000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 0
Solar Generation Capital (£) | 0 | 390000 | 520000 | 780000 | 780000 | 3900000 | 0 | 1950000
Storage Capacity Capital (£) | 0 | 0 | 0 | 0 | 480000 | 18000000 | 5064000 | 5064000
Balance of Plant Capital (£) | 250000 | 250000 | 250000 | 250000 | 250000 | 100000 | 100000 | 100000
Freight (10%) | 34000 | 133000 | 186000 | 212000 | 260000 | 2300000 | 616400 | 711400
Contingency (10%) | 37400 | 146300 | 204600 | 233200 | 286000 | 2530000 | 678040 | 782540
Generation Total | 411400 | 1609300 | 2250600 | 2565200 | 3146000 | 27830000 | 7458440 | 8607940
Underground Cable | 542630 | 542630 | 542630 | 542630 | 542630 | 542630 | 542630 | 542630
Substations | 359081.8 | 359081.8 | 359081.8 | 359081.8 | 359081.8 | 359081.8 | 359081.8 | 359081.8
Service Terminations | 196652.5 | 196652.5 | 196652.5 | 196652.5 | 196652.5 | 196652.5 | 196652.5 | 196652.5
Misc | 113166.5333 | 113166.5333 | 113166.5333 | 113166.5333 | 113166.5333 | 113166.5333 | 113166.5333 | 113166.5333
Civil Works | 855400 | 855400 | 855400 | 855400 | 855400 | 855400 | 855400 | 855400
Project Management | 160000 | 160000 | 160000 | 160000 | 160000 | 160000 | 160000 | 160000
Contingency (10%) | 222693.0833 | 222693.0833 | 222693.0833 | 222693.0833 | 222693.0833 | 222693.0833 | 222693.0833 | 222693.0833
Distribution Total | 2449623.9167 | 2449623.9167 | 2449623.9167 | 2449623.9167 | 2449623.9167 | 2449623.9167 | 2449623.9167 | 2449623.9167
|  | 0 | 52 | 15600 | 0 | 0 | 0 | 0
Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Tariff Build Up (p/kWh)
Average cost of fuel per kWh sent out | 23.4381 | 1.7655 | 0 | 0 | 0 | 0 | 0 | 0
Repayment of capital and interest (generation) | 2.6362 | 10.3122 | 14.4216 | 16.4376 | 20.1593 | 178.332 | 47.793 | 55.1589
Repayment of capital and interest (rebuild distribution system) | 15.697 | 15.697 | 15.697 | 15.697 | 15.697 | 15.697 | 15.697 | 15.697
Operating Costs (generation) | 0.96429 | 2.1 | 2.7643 | 2.95 | 2.95 | 4.2143 | 1.4286 | 1.3929
Operating Costs (distribution) | 1.7497 | 1.7497 | 1.7497 | 1.7497 | 1.7497 | 1.7497 | 1.7497 | 1.7497
Operating costs (storage) | 0 | 0 | 0 | 0 | 0.68571 | 25.7143 | 7.2343 | 7.2343
Other Admin costs | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Land rental | 1 | 1.0321 | 1.0464 | 1.0607 | 1.0607 | 1.2321 | 1.0179 | 1.1071
Adminsistration Staff Costs | 2.8571 | 2.8571 | 2.8571 | 2.8571 | 2.8571 | 2.8571 | 2.8571 | 2.8571
Operational Staff Costs | 11.4286 | 11.4286 | 11.4286 | 11.4286 | 11.4286 | 11.4286 | 11.4286 | 11.4286
Surplus/shortfall p/kWh | -0.77104 | 12.0577 | 9.0353 | 6.8193 | 2.4119 | -182.2251 | -30.2061 | -37.6256
Surplus/shortfall £ pa | -10794.5471 | 168807.8582 | 126493.5164 | 95470.5391 | 33766.581 | -2551151.638 | -422885.3079 | -526757.7249
| Single source of energy, but multiple units giving (n-1) security, expensive fuel | Retains (n-1) level of security on diesel, reduced diesel running hours | Retains (n-1) level of security on diesel, further reduced diesel running hours | Retains (n-1) level of security on diesel, but diesels unlikely to run -weather dependent | Retains (n-1) level of security on diesel, but diesels unlikely to run -weather dependent | 100% renewable, heavy capital cost. Requires 16 acres of land for solar (updated narec proposal) | Entirely Wind Single source of energy - high risk, single 77m high turbine | Entirely Solar, totally dependent upon storage for approximately 55% of time (hours of darkness)

## Diesel Summary
Scenario | 100% Diesel (current)
Project Capacity (kW) | 600
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 90000 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 0 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 0 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 2861023.9167
Storage Capacity Capital | 0 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 250000 |  | Operating Costs (diesel generation) |  |  |  | 13500 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 34000 |  | Operating Costs (solar generation) |  |  |  | 0 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 37400 |  | Operating Costs (wind generation) |  |  |  | 0 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 411400 |  | Operating Costs (Storage) |  |  |  | 0 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 14000 |  |  | Annual Generation Diesel (kWh) |  | 1492946.5241
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 265996.2392 |  |  | Annual Generatuion Solar(kWh) |  | 0
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 0
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1492946.5241
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 2861023.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total delivered |  |  |  | 23.4381
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699
EBITDA (£) | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301
Depreciation (£) | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567
EBIT (£) | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734
Loan Interest (£) | -214576.7938 | -211420.225 | -208026.9136 | -204379.1038 | -200457.7083 | -196242.2081 | -191710.5455 | -186839.0081 | -181602.1054 | -175972.435 | -169920.5394 | -163414.7515 | -156421.0296 | -148902.7785 | -140820.6586 | -132132.3798 | -122792.4799 | -112752.0877 | -101958.6659 | -90355.7376 | -77882.5896 | -64473.9556 | -50059.674 | -34564.3212 | -17906.817
EBT (£) | -83147.9203 | -79991.3516 | -76598.0402 | -72950.2304 | -69028.8349 | -64813.3347 | -60281.6721 | -55410.1347 | -50173.232 | -44543.5616 | -38491.666 | -31985.8781 | -24992.1562 | -17473.9051 | -9391.7852 | -703.5064 | 8636.3935 | 18676.7857 | 29470.2075 | 41073.1358 | 53546.2838 | 66954.9178 | 81369.1995 | 96864.5522 | 113522.0564
Net Cash flow (£) | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471
NPV
Discount rate | 5%
NPV over 10 years | -83352.6314
NPV over 15 years | -112043.7076
NPV over 20 years | -134523.9165
NPV over 25 years | -152137.7484
Minimum Debt Service Cover Ratio | 1.4636
Units from solar used at time of generation (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind used at time of generation (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units sold from diesel (kWh) | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Total units sold | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381 | 23.4381
Interest | 15.3269 | 15.1014 | 14.8591 | 14.5985 | 14.3184 | 14.0173 | 13.6936 | 13.3456 | 12.9716 | 12.5695 | 12.1372 | 11.6725 | 11.1729 | 10.6359 | 10.0586 | 9.438 | 8.7709 | 8.0537 | 7.2828 | 6.454 | 5.563 | 4.6053 | 3.5757 | 2.4689 | 1.2791
Repayment of principal | 3.0063 | 3.2317 | 3.4741 | 3.7347 | 4.0148 | 4.3159 | 4.6396 | 4.9875 | 5.3616 | 5.7637 | 6.196 | 6.6607 | 7.1602 | 7.6973 | 8.2746 | 8.8951 | 9.5623 | 10.2794 | 11.0504 | 11.8792 | 12.7701 | 13.7279 | 14.7575 | 15.8643 | 17.0541
Operating Costs | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 18.9997
| 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771 | 60.771
Surplus/shortfall p/kWh | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104 | -0.77104
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## Diesel Interest Calculations
Interest Calculation |  | 100% Diesel (current)
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 2861023.9167
Debt |  | 100%
| Loan: | 2861023.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 2861023.9167 | 2818936.3332 | 2773692.1811 | 2725054.7175 | 2672769.4441 | 2616562.7753 | 2556140.6062 | 2491186.7745 | 2421361.4055 | 2346299.1337 | 2265607.1916 | 2178863.3538 | 2085613.7281 | 1985370.3806 | 1877608.7819 | 1761765.0634 | 1637233.066 | 1503361.1688 | 1359448.8793 | 1204743.168 | 1038434.5285 | 859652.7409 | 667462.3193 | 460857.6161 | 238757.5602
| Principal repaid |  | -42087.5834 | -45244.1522 | -48637.4636 | -52285.2734 | -56206.6689 | -60422.169 | -64953.8317 | -69825.3691 | -75062.2718 | -80691.9421 | -86743.8378 | -93249.6256 | -100243.3476 | -107761.5986 | -115843.7185 | -124531.9974 | -133871.8972 | -143912.2895 | -154705.7112 | -166308.6396 | -178781.7875 | -192190.4216 | -206604.7032 | -222100.056 | -238757.5602
| Interest |  | -214576.7938 | -211420.225 | -208026.9136 | -204379.1038 | -200457.7083 | -196242.2081 | -191710.5455 | -186839.0081 | -181602.1054 | -175972.435 | -169920.5394 | -163414.7515 | -156421.0296 | -148902.7785 | -140820.6586 | -132132.3798 | -122792.4799 | -112752.0877 | -101958.6659 | -90355.7376 | -77882.5896 | -64473.9556 | -50059.674 | -34564.3212 | -17906.817
| C/fwd |  | 2818936.3332 | 2773692.1811 | 2725054.7175 | 2672769.4441 | 2616562.7753 | 2556140.6062 | 2491186.7745 | 2421361.4055 | 2346299.1337 | 2265607.1916 | 2178863.3538 | 2085613.7281 | 1985370.3806 | 1877608.7819 | 1761765.0634 | 1637233.066 | 1503361.1688 | 1359448.8793 | 1204743.168 | 1038434.5285 | 859652.7409 | 667462.3193 | 460857.6161 | 238757.5602 | 2.7649e-09
|  |  | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772 | -256664.3772
|  |  | -42087.5834 | 211420.225 | 208026.9136 | 204379.1038 | 200457.7083 | 196242.2081 | 191710.5455 | 186839.0081 | 181602.1054 | 175972.435 | 169920.5394 | 163414.7515

## Diesel Cash Flow
Cash flow | 100% Diesel (current)
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -8203348.2691
Operating costs |  | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392
EBITDA/Net cash flow from operations |  | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 12796651.7309
Interest paid |  | -214576.7938 | -211420.225 | -208026.9136 | -204379.1038 | -200457.7083 | -196242.2081 | -191710.5455 | -186839.0081 | -181602.1054 | -175972.435 | -169920.5394 | -163414.7515 | -156421.0296 | -148902.7785 | -140820.6586 | -132132.3798 | -122792.4799 | -112752.0877 | -101958.6659 | -90355.7376 | -77882.5896 | -64473.9556 | -50059.674 | -34564.3212 | -17906.817 | -3555585.5126
Net cash flow pre |  | 31293.0363 | 34449.6051 | 37842.9165 | 41490.7263 | 45412.1218 | 49627.6219 | 54159.2846 | 59030.822 | 64267.7247 | 69897.395 | 75949.2907 | 82455.0785 | 89448.8005 | 96967.0515 | 105049.1714 | 113737.4503 | 123077.3501 | 133117.7424 | 143911.1641 | 155514.0925 | 167987.2404 | 181395.8745 | 195810.1561 | 211305.5089 | 227963.0131 | 9241066.2184
Flow of Capital
Total start costs |  | -2861023.9167 | [24 empty] | -2861023.9167
Loan receipts |  | 2861023.9167 | [24 empty] | 2861023.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -42087.5834 | -45244.1522 | -48637.4636 | -52285.2734 | -56206.6689 | -60422.169 | -64953.8317 | -69825.3691 | -75062.2718 | -80691.9421 | -86743.8378 | -93249.6256 | -100243.3476 | -107761.5986 | -115843.7185 | -124531.9974 | -133871.8972 | -143912.2895 | -154705.7112 | -166308.6396 | -178781.7875 | -192190.4216 | -206604.7032 | -222100.056 | -238757.5602 | -2861023.9167
Net cash flow |  | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | -10794.5471 | 6380042.3017
Cash Balance b/fwd |  |  | -10794.5471 | -21589.0942 | -32383.6413 | -43178.1884 | -53972.7355 | -64767.2826 | -75561.8297 | -86356.3768 | -97150.9239 | -107945.471 | -118740.0181 | -129534.5652 | -140329.1123 | -151123.6594 | -161918.2065 | -172712.7536 | -183507.3007 | -194301.8478 | -205096.3949 | -215890.942 | -226685.4891 | -237480.0362 | -248274.5833 | -259069.1304 | 0
Cash Balance c/fwd |  | -10794.5471 | -21589.0942 | -32383.6413 | -43178.1884 | -53972.7355 | -64767.2826 | -75561.8297 | -86356.3768 | -97150.9239 | -107945.471 | -118740.0181 | -129534.5652 | -140329.1123 | -151123.6594 | -161918.2065 | -172712.7536 | -183507.3007 | -194301.8478 | -205096.3949 | -215890.942 | -226685.4891 | -237480.0362 | -248274.5833 | -259069.1304 | -269863.6775 | 6380042.3017
Debt Service Cover
Net operating income |  | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301
Debt Service |  | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772 | 256664.3772
Debt Service Cover Ratio |  | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794 | 0.95794
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Diesel Profit and Loss
Profit and Loss Account | 100% Diesel (current)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -328133.9308 | -8203348.2691
Operating Costs | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -265996.2392 | -6649905.9792
Total Operating Costs | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -594130.1699 | -14853254.2482
EBITDA | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 245869.8301 | 35853254.2482
| 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 29.27% | 170.7%
Depreciation | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -114440.9567 | -2861023.9167
EBIT | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 131428.8734 | 38714278.1649
Loan interest | -214576.7938 | -211420.225 | -208026.9136 | -204379.1038 | -200457.7083 | -196242.2081 | -191710.5455 | -186839.0081 | -181602.1054 | -175972.435 | -169920.5394 | -163414.7515 | -156421.0296 | -148902.7785 | -140820.6586 | -132132.3798 | -122792.4799 | -112752.0877 | -101958.6659 | -90355.7376 | -77882.5896 | -64473.9556 | -50059.674 | -34564.3212 | -17906.817 | -3555585.5126
Earnings Before Tax | -83147.9203 | -79991.3516 | -76598.0402 | -72950.2304 | -69028.8349 | -64813.3347 | -60281.6721 | -55410.1347 | -50173.232 | -44543.5616 | -38491.666 | -31985.8781 | -24992.1562 | -17473.9051 | -9391.7852 | -703.5064 | 8636.3935 | 18676.7857 | 29470.2075 | 41073.1358 | 53546.2838 | 66954.9178 | 81369.1995 | 96864.5522 | 113522.0564 | 42269863.6775
| -2.7716 | -2.6664 | -2.5533 | -2.4317 | -2.301 | -2.1604 | -2.0094 | -1.847 | -1.6724 | -1.4848 | -1.2831 | -1.0662 | -0.83307 | -0.58246 | -0.31306 | -0.02345 | 0.28788 | 0.62256 | 0.98234 | 1.3691 | 1.7849 | 2.2318 | 2.7123 | 3.2288 | 3.7841

## Mix 1 Summary
Scenario | Mix 1 Wind, Solar Diesel standby
Project Capacity (kW) | 1200
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 90000 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 600000 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 390000 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 4058923.9167
Storage Capacity Capital | 0 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 250000 |  | Operating Costs (diesel generation) |  |  |  | 13500 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 133000 |  | Operating Costs (solar generation) |  |  |  | 3900 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 146300 |  | Operating Costs (wind generation) |  |  |  | 12000 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 1609300 |  | Operating Costs (Storage) |  |  |  | 0 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 14450 |  |  | Annual Generation Diesel (kWh) |  | 112458.1241
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 282346.2392 |  |  | Annual Generatuion Solar(kWh) |  | 328500
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 1024920
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1465878.1241
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 4058923.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy delivered |  |  |  | 1.7655
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511
EBITDA (£) | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489
Depreciation (£) | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567
EBIT (£) | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923
Loan Interest (£) | -304419.2938 | -299941.0815 | -295127.0033 | -289951.8692 | -284388.6001 | -278408.0858 | -271979.0329 | -265067.8011 | -257638.2269 | -249651.4346 | -241065.6329 | -231835.896 | -221913.9289 | -211247.8143 | -199781.7411 | -187455.7124 | -174205.2315 | -159960.9645 | -144648.3776 | -128187.3466 | -110491.7383 | -91468.9593 | -71019.472 | -49036.2731 | -25404.3342
EBT (£) | 66160.3985 | 70638.6108 | 75452.689 | 80627.823 | 86191.0922 | 92171.6065 | 98600.6593 | 105511.8912 | 112941.4654 | 120928.2577 | 129514.0594 | 138743.7962 | 148665.7633 | 159331.878 | 170797.9512 | 183123.9799 | 196374.4608 | 210618.7277 | 225931.3147 | 242392.3457 | 260087.954 | 279110.7329 | 299560.2203 | 321543.4192 | 345175.358
Net Cash flow (£) | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582
NPV
Discount rate | 5%
NPV over 10 years | 1303489.5349
NPV over 15 years | 1752167.8422
NPV over 20 years | 2103719.0363
NPV over 25 years | 2379168.5957
Minimum Debt Service Cover Ratio | 1.4636
Units from solar used at time of generation (kWh) | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500
Units from wind used at time of generation (kWh) | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580
Total units sold | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655 | 1.7655
Interest | 21.7442 | 21.4244 | 21.0805 | 20.7108 | 20.3135 | 19.8863 | 19.4271 | 18.9334 | 18.4027 | 17.8322 | 17.219 | 16.5597 | 15.851 | 15.0891 | 14.2701 | 13.3897 | 12.4432 | 11.4258 | 10.332 | 9.1562 | 7.8923 | 6.5335 | 5.0728 | 3.5026 | 1.8146
Repayment of principal | 4.265 | 4.5848 | 4.9287 | 5.2984 | 5.6957 | 6.1229 | 6.5821 | 7.0758 | 7.6065 | 8.177 | 8.7902 | 9.4495 | 10.1582 | 10.9201 | 11.7391 | 12.6195 | 13.566 | 14.5834 | 15.6772 | 16.853 | 18.1169 | 19.4757 | 20.9364 | 22.5066 | 24.1946
Operating Costs | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676 | 20.1676
| 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423 | 47.9423
Surplus/shortfall p/kWh | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577 | 12.0577
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## Mix 1 Interest Calculations
Interest Calculation |  | Mix 1 Wind, Solar Diesel standby
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 4058923.9167
Debt |  | 100%
| Loan: | 4058923.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 4058923.9167 | 3999214.4197 | 3935026.7104 | 3866024.923 | 3791848.0014 | 3712107.8108 | 3626387.1059 | 3534237.3481 | 3435176.3585 | 3328685.7946 | 3214208.4385 | 3091145.2806 | 2958852.3859 | 2816637.5241 | 2663756.5477 | 2499409.498 | 2322736.4196 | 2132812.8604 | 1928645.0342 | 1709164.621 | 1473223.1768 | 1219586.1244 | 946926.2929 | 653816.9742 | 338724.4565
| Principal repaid |  | -59709.497 | -64187.7093 | -69001.7875 | -74176.9215 | -79740.1906 | -85720.7049 | -92149.7578 | -99060.9896 | -106490.5639 | -114477.3561 | -123063.1579 | -132292.8947 | -142214.8618 | -152880.9764 | -164347.0497 | -176673.0784 | -189923.5593 | -204167.8262 | -219480.4132 | -235941.4442 | -253637.0525 | -272659.8314 | -293109.3188 | -315092.5177 | -338724.4565
| Interest |  | -304419.2938 | -299941.0815 | -295127.0033 | -289951.8692 | -284388.6001 | -278408.0858 | -271979.0329 | -265067.8011 | -257638.2269 | -249651.4346 | -241065.6329 | -231835.896 | -221913.9289 | -211247.8143 | -199781.7411 | -187455.7124 | -174205.2315 | -159960.9645 | -144648.3776 | -128187.3466 | -110491.7383 | -91468.9593 | -71019.472 | -49036.2731 | -25404.3342
| C/fwd |  | 3999214.4197 | 3935026.7104 | 3866024.923 | 3791848.0014 | 3712107.8108 | 3626387.1059 | 3534237.3481 | 3435176.3585 | 3328685.7946 | 3214208.4385 | 3091145.2806 | 2958852.3859 | 2816637.5241 | 2663756.5477 | 2499409.498 | 2322736.4196 | 2132812.8604 | 1928645.0342 | 1709164.621 | 1473223.1768 | 1219586.1244 | 946926.2929 | 653816.9742 | 338724.4565 | 2.0373e-09
|  |  | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907 | -364128.7907
|  |  | -59709.497 | 299941.0815 | 295127.0033 | 289951.8692 | 284388.6001 | 278408.0858 | 271979.0329 | 265067.8011 | 257638.2269 | 249651.4346 | 241065.6329 | 231835.896

## Mix 1 Cash Flow
Cash flow | Mix 1 Wind, Solar Diesel standby
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -617927.7975
Operating costs |  | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392
EBITDA/Net cash flow from operations |  | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 20382072.2025
Interest paid |  | -304419.2938 | -299941.0815 | -295127.0033 | -289951.8692 | -284388.6001 | -278408.0858 | -271979.0329 | -265067.8011 | -257638.2269 | -249651.4346 | -241065.6329 | -231835.896 | -221913.9289 | -211247.8143 | -199781.7411 | -187455.7124 | -174205.2315 | -159960.9645 | -144648.3776 | -128187.3466 | -110491.7383 | -91468.9593 | -71019.472 | -49036.2731 | -25404.3342 | -5044295.8518
Net cash flow pre |  | 228517.3552 | 232995.5675 | 237809.6457 | 242984.7797 | 248548.0488 | 254528.5631 | 260957.616 | 267868.8478 | 275298.422 | 283285.2143 | 291871.016 | 301100.7529 | 311022.72 | 321688.8346 | 333154.9079 | 345480.9366 | 358731.4175 | 372975.6844 | 388288.2714 | 404749.3024 | 422444.9107 | 441467.6896 | 461917.177 | 483900.3759 | 507532.3147 | 15337776.3507
Flow of Capital
Total start costs |  | -4058923.9167 | [24 empty] | -4058923.9167
Loan receipts |  | 4058923.9167 | [24 empty] | 4058923.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -59709.497 | -64187.7093 | -69001.7875 | -74176.9215 | -79740.1906 | -85720.7049 | -92149.7578 | -99060.9896 | -106490.5639 | -114477.3561 | -123063.1579 | -132292.8947 | -142214.8618 | -152880.9764 | -164347.0497 | -176673.0784 | -189923.5593 | -204167.8262 | -219480.4132 | -235941.4442 | -253637.0525 | -272659.8314 | -293109.3188 | -315092.5177 | -338724.4565 | -4058923.9167
Net cash flow |  | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 168807.8582 | 11278852.4341
Cash Balance b/fwd |  |  | 168807.8582 | 337615.7164 | 506423.5746 | 675231.4328 | 844039.291 | 1012847.1492 | 1181655.0074 | 1350462.8656 | 1519270.7238 | 1688078.582 | 1856886.4402 | 2025694.2983 | 2194502.1565 | 2363310.0147 | 2532117.8729 | 2700925.7311 | 2869733.5893 | 3038541.4475 | 3207349.3057 | 3376157.1639 | 3544965.0221 | 3713772.8803 | 3882580.7385 | 4051388.5967 | 0
Cash Balance c/fwd |  | 168807.8582 | 337615.7164 | 506423.5746 | 675231.4328 | 844039.291 | 1012847.1492 | 1181655.0074 | 1350462.8656 | 1519270.7238 | 1688078.582 | 1856886.4402 | 2025694.2983 | 2194502.1565 | 2363310.0147 | 2532117.8729 | 2700925.7311 | 2869733.5893 | 3038541.4475 | 3207349.3057 | 3376157.1639 | 3544965.0221 | 3713772.8803 | 3882580.7385 | 4051388.5967 | 4220196.4549 | 11278852.4341
Debt Service Cover
Net operating income |  | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489
Debt Service |  | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907 | 364128.7907
Debt Service Cover Ratio |  | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636 | 1.4636
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Mix 1 Profit and Loss
Profit and Loss Account | Mix 1 Wind, Solar Diesel standby
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -24717.1119 | -617927.7975
Operating Costs | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -282346.2392 | -7058655.9792
Total Operating Costs | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -307063.3511 | -7676583.7767
EBITDA | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 532936.6489 | 28676583.7767
| 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 63.44% | 136.6%
Depreciation | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -162356.9567 | -4058923.9167
EBIT | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 370579.6923 | 32735507.6933
Loan interest | -304419.2938 | -299941.0815 | -295127.0033 | -289951.8692 | -284388.6001 | -278408.0858 | -271979.0329 | -265067.8011 | -257638.2269 | -249651.4346 | -241065.6329 | -231835.896 | -221913.9289 | -211247.8143 | -199781.7411 | -187455.7124 | -174205.2315 | -159960.9645 | -144648.3776 | -128187.3466 | -110491.7383 | -91468.9593 | -71019.472 | -49036.2731 | -25404.3342 | -5044295.8518
Earnings Before Tax | 66160.3985 | 70638.6108 | 75452.689 | 80627.823 | 86191.0922 | 92171.6065 | 98600.6593 | 105511.8912 | 112941.4654 | 120928.2577 | 129514.0594 | 138743.7962 | 148665.7633 | 159331.878 | 170797.9512 | 183123.9799 | 196374.4608 | 210618.7277 | 225931.3147 | 242392.3457 | 260087.954 | 279110.7329 | 299560.2203 | 321543.4192 | 345175.358 | 37779803.5451
| 2.2053 | 2.3546 | 2.5151 | 2.6876 | 2.873 | 3.0724 | 3.2867 | 3.5171 | 3.7647 | 4.0309 | 4.3171 | 4.6248 | 4.9555 | 5.3111 | 5.6933 | 6.1041 | 6.5458 | 7.0206 | 7.531 | 8.0797 | 8.6696 | 9.3037 | 9.9853 | 10.7181 | 11.5058

## Mix 2 Summary
Scenario | Mix 2 Wind, Solar Diesel standby
Project Capacity (kW) | 1500
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 90000 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 1000000 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 520000 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 4700223.9167
Storage Capacity Capital | 0 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 250000 |  | Operating Costs (diesel generation) |  |  |  | 13500 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 186000 |  | Operating Costs (solar generation) |  |  |  | 5200 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 204600 |  | Operating Costs (wind generation) |  |  |  | 20000 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 2250600 |  | Operating Costs (Storage) |  |  |  | 0 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 14650 |  |  | Annual Generation Diesel (kWh) |  | 0
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 291846.2392 |  |  | Annual Generatuion Solar(kWh) |  | 438000
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 1025000
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1463000
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 4700223.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy sent out |  |  |  | 0
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392
EBITDA (£) | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608
Depreciation (£) | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567
EBIT (£) | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042
Loan Interest (£) | -352516.7938 | -347331.0349 | -341756.3442 | -335763.5517 | -329321.2998 | -322395.8789 | -314951.0515 | -306947.862 | -298344.4333 | -289095.7475 | -279153.4102 | -268465.3977 | -256975.7841 | -244624.4496 | -231346.765 | -217073.254 | -201729.2298 | -185234.4037 | -167502.4656 | -148440.6322
EBT (£) | 7628.0104 | 12813.7692 | 18388.4599 | 24381.2525 | 30823.5044 | 37748.9253 | 45193.7527 | 53196.9422 | 61800.3708 | 71049.0567 | 80991.3939 | 91679.4065 | 103169.02 | 115520.3545 | 128798.0392 | 143071.5501 | 158415.5744 | 174910.4005 | 192642.3386 | 211704.172
Net Cash flow (£) | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164
NPV
Discount rate | 5%
NPV over 10 years | 976749.4036
NPV over 15 years | 1312959.4439
NPV over 20 years | 1576388.8079
NPV over 25 years | 1782792.6076
Minimum Debt Service Cover Ratio | 1.3
Units from solar used at time of generation (kWh) | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500
Units from wind used at time of generation (kWh) | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580
Total units sold | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 25.1798 | 24.8094 | 24.4112 | 23.9831 | 23.5229 | 23.0283 | 22.4965 | 21.9248 | 21.3103 | 20.6497 | 19.9395 | 19.1761 | 18.3554 | 17.4732 | 16.5248 | 15.5052 | 14.4092 | 13.231 | 11.9645 | 10.6029
Repayment of principal | 4.9388 | 5.3092 | 5.7074 | 6.1355 | 6.5956 | 7.0903 | 7.6221 | 8.1937 | 8.8083 | 9.4689 | 10.1791 | 10.9425 | 11.7632 | 12.6454 | 13.5938 | 14.6134 | 15.7094 | 16.8876 | 18.1541 | 19.5157
Operating Costs | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462 | 20.8462
| 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647 | 50.9647
Surplus/shortfall p/kWh | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353 | 9.0353
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## Mix 2 Interest Calculations
Interest Calculation |  | Mix 2 Wind, Solar Diesel standby
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 4700223.9167
Debt |  | 100%
| Loan: | 4700223.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 4700223.9167 | 4631080.4659 | 4556751.2564 | 4476847.3562 | 4390950.6634 | 4298611.7187 | 4199347.3532 | 4092638.1602 | 3977925.7777 | 3854609.9666 | 3722045.4696 | 3579538.6354 | 3426343.7886 | 3261659.3282 | 3084623.5334 | 2894310.0539 | 2689723.0635 | 2469792.0488 | 2233366.208 | 1979208.4291 | 1705988.8169 | 1412277.7337 | 1096538.3192 | 757118.4487 | 392242.0879
| Principal repaid |  | -69143.4507 | -74329.2095 | -79903.9002 | -85896.6928 | -92338.9447 | -99264.3656 | -106709.193 | -114712.3825 | -123315.8111 | -132564.497 | -142506.8342 | -153194.8468 | -164684.4603 | -177035.7948 | -190313.4795 | -204586.9904 | -219931.0147 | -236425.8408 | -254157.7789 | -273219.6123 | -293711.0832 | -315739.4144 | -339419.8705 | -364876.3608 | -392242.0879
| Interest |  | -352516.7938 | -347331.0349 | -341756.3442 | -335763.5517 | -329321.2998 | -322395.8789 | -314951.0515 | -306947.862 | -298344.4333 | -289095.7475 | -279153.4102 | -268465.3977 | -256975.7841 | -244624.4496 | -231346.765 | -217073.254 | -201729.2298 | -185234.4037 | -167502.4656 | -148440.6322 | -127949.1613 | -105920.83 | -82240.3739 | -56783.8837 | -29418.1566
| C/fwd |  | 4631080.4659 | 4556751.2564 | 4476847.3562 | 4390950.6634 | 4298611.7187 | 4199347.3532 | 4092638.1602 | 3977925.7777 | 3854609.9666 | 3722045.4696 | 3579538.6354 | 3426343.7886 | 3261659.3282 | 3084623.5334 | 2894310.0539 | 2689723.0635 | 2469792.0488 | 2233366.208 | 1979208.4291 | 1705988.8169 | 1412277.7337 | 1096538.3192 | 757118.4487 | 392242.0879 | 0
|  |  | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445 | -421660.2445
|  |  | -69143.4507 | 347331.0349 | 341756.3442 | 335763.5517 | 329321.2998 | 322395.8789 | 314951.0515 | 306947.862 | 298344.4333 | 289095.7475 | 279153.4102 | 268465.3977

## Mix 2 Cash Flow
Cash flow | Mix 2 Wind, Solar Diesel standby
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs |  | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392
EBITDA/Net cash flow from operations |  | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 21000000
Interest paid |  | -352516.7938 | -347331.0349 | -341756.3442 | -335763.5517 | -329321.2998 | -322395.8789 | -314951.0515 | -306947.862 | -298344.4333 | -289095.7475 | -279153.4102 | -268465.3977 | -256975.7841 | -244624.4496 | -231346.765 | -217073.254 | -201729.2298 | -185234.4037 | -167502.4656 | -148440.6322 | -127949.1613 | -105920.83 | -82240.3739 | -56783.8837 | -29418.1566 | -5841282.195
Net cash flow pre |  | 195636.9671 | 200822.7259 | 206397.4166 | 212390.2091 | 218832.4611 | 225757.8819 | 233202.7093 | 241205.8988 | 249809.3275 | 259058.0133 | 269000.3506 | 279688.3632 | 291177.9767 | 303529.3112 | 316806.9958 | 331080.5068 | 346424.5311 | 362919.3572 | 380651.2952 | 399713.1286 | 420204.5996 | 442232.9308 | 465913.3869 | 491369.8772 | 518735.6042 | 15158717.805
Flow of Capital
Total start costs |  | -4700223.9167 | [24 empty] | -4700223.9167
Loan receipts |  | 4700223.9167 | [24 empty] | 4700223.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -69143.4507 | -74329.2095 | -79903.9002 | -85896.6928 | -92338.9447 | -99264.3656 | -106709.193 | -114712.3825 | -123315.8111 | -132564.497 | -142506.8342 | -153194.8468 | -164684.4603 | -177035.7948 | -190313.4795 | -204586.9904 | -219931.0147 | -236425.8408 | -254157.7789 | -273219.6123 | -293711.0832 | -315739.4144 | -339419.8705 | -364876.3608 | -392242.0879 | -4700223.9167
Net cash flow |  | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 126493.5164 | 10458493.8883
Cash Balance b/fwd |  |  | 126493.5164 | 252987.0327 | 379480.5491 | 505974.0655 | 632467.5818 | 758961.0982 | 885454.6146 | 1011948.1309 | 1138441.6473 | 1264935.1637 | 1391428.68 | 1517922.1964 | 1644415.7128 | 1770909.2291 | 1897402.7455 | 2023896.2619 | 2150389.7782 | 2276883.2946 | 2403376.811 | 2529870.3273 | 2656363.8437 | 2782857.3601 | 2909350.8764 | 3035844.3928 | 0
Cash Balance c/fwd |  | 126493.5164 | 252987.0327 | 379480.5491 | 505974.0655 | 632467.5818 | 758961.0982 | 885454.6146 | 1011948.1309 | 1138441.6473 | 1264935.1637 | 1391428.68 | 1517922.1964 | 1644415.7128 | 1770909.2291 | 1897402.7455 | 2023896.2619 | 2150389.7782 | 2276883.2946 | 2403376.811 | 2529870.3273 | 2656363.8437 | 2782857.3601 | 2909350.8764 | 3035844.3928 | 3162337.9092 | 10458493.8883
Debt Service Cover
Net operating income |  | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608
Debt Service |  | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445 | 421660.2445
Debt Service Cover Ratio |  | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Mix 2 Profit and Loss
Profit and Loss Account | Mix 2 Wind, Solar Diesel standby
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Costs | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -7296155.9792
Total Operating Costs | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -291846.2392 | -7296155.9792
EBITDA | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 548153.7608 | 28296155.9792
| 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 65.26% | 134.7%
Depreciation | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -188008.9567 | -4700223.9167
EBIT | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 360144.8042 | 32996379.8958
Loan interest | -352516.7938 | -347331.0349 | -341756.3442 | -335763.5517 | -329321.2998 | -322395.8789 | -314951.0515 | -306947.862 | -298344.4333 | -289095.7475 | -279153.4102 | -268465.3977 | -256975.7841 | -244624.4496 | -231346.765 | -217073.254 | -201729.2298 | -185234.4037 | -167502.4656 | -148440.6322 | -127949.1613 | -105920.83 | -82240.3739 | -56783.8837 | -29418.1566 | -5841282.195
Earnings Before Tax | 7628.0104 | 12813.7692 | 18388.4599 | 24381.2525 | 30823.5044 | 37748.9253 | 45193.7527 | 53196.9422 | 61800.3708 | 71049.0567 | 80991.3939 | 91679.4065 | 103169.02 | 115520.3545 | 128798.0392 | 143071.5501 | 158415.5744 | 174910.4005 | 192642.3386 | 211704.172 | 232195.6429 | 254223.9741 | 277904.4302 | 303360.9205 | 330726.6476 | 38837662.0908
| 0.25427 | 0.42713 | 0.61295 | 0.81271 | 1.0275 | 1.2583 | 1.5065 | 1.7732 | 2.06 | 2.3683 | 2.6997 | 3.056 | 3.439 | 3.8507 | 4.2933 | 4.7691 | 5.2805 | 5.8303 | 6.4214 | 7.0568 | 7.7399 | 8.4741 | 9.2635 | 10.112 | 11.0242

## Mix 3 Summary
Scenario | Mix 3 Wind, Solar, Storage, Diesel standby
Project Capacity (kW) | 1700
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 90000 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 1000000 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 780000 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 5014823.9167
Storage Capacity Capital | 0 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 250000 |  | Operating Costs (diesel generation) |  |  |  | 13500 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 212000 |  | Operating Costs (solar generation) |  |  |  | 7800 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 233200 |  | Operating Costs (wind generation) |  |  |  | 20000 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 2565200 |  | Operating Costs (Storage) |  |  |  | 0 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 14650 |  |  | Annual Generation Diesel (kWh) |  | 0
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 294446.2392 |  |  | Annual Generatuion Solar(kWh) |  | 657000
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 806000
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1463000
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 5014823.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy sent out |  |  |  | 0
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392
EBITDA (£) | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608
Depreciation (£) | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567
EBIT (£) | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042
Loan Interest (£) | -376111.7938 | -370578.9366 | -364631.1153 | -358237.2073 | -351363.7562 | -343974.7963 | -336031.6644 | -327492.7976 | -318313.5157 | -308445.7878 | -297837.9802 | -286434.5871 | -274175.9395 | -260997.8934 | -246831.4937 | -231602.6141 | -215231.5685 | -197632.6946 | -178713.905 | -158376.2063 | -136513.1801 | -113010.427 | -87744.9674 | -60584.5983 | -31387.2015
EBT (£) | -31150.9896 | -25618.1325 | -19670.3111 | -13276.4031 | -6402.952 | 986.0079 | 8929.1398 | 17468.0066 | 26647.2884 | 36515.0164 | 47122.8239 | 58526.217 | 70784.8646 | 83962.9108 | 98129.3104 | 113358.19 | 129729.2356 | 147328.1096 | 166246.8992 | 186584.5979 | 208447.6241 | 231950.3772 | 257215.8368 | 284376.2059 | 313573.6026
Net Cash flow (£) | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391
NPV
Discount rate | 5%
NPV over 10 years | 738742.5432
NPV over 15 years | 993027.4798
NPV over 20 years | 1192266.3814
NPV over 25 years | 1348375.2742
Minimum Debt Service Cover Ratio | 1.2127
Units from solar used at time of generation (kWh) | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500
Units from wind used at time of generation (kWh) | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580
Total units | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 26.8651 | 26.4699 | 26.0451 | 25.5884 | 25.0974 | 24.5696 | 24.0023 | 23.3923 | 22.7367 | 22.0318 | 21.2741 | 20.4596 | 19.584 | 18.6427 | 17.6308 | 16.543 | 15.3737 | 14.1166 | 12.7653 | 11.3126 | 9.7509 | 8.0722 | 6.2675 | 4.3275 | 2.2419
Repayment of principal | 5.2694 | 5.6646 | 6.0894 | 6.5461 | 7.0371 | 7.5649 | 8.1323 | 8.7422 | 9.3978 | 10.1027 | 10.8604 | 11.6749 | 12.5505 | 13.4918 | 14.5037 | 15.5915 | 16.7608 | 18.0179 | 19.3692 | 20.8219 | 22.3836 | 24.0623 | 25.867 | 27.807 | 29.8926
Operating Costs | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319 | 21.0319
| 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664 | 53.1664
Surplus/shortfall p/kWh | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336 | 6.8336
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## Mix 3 Interest Calculations
Interest Calculation |  | Mix 3 Wind, Solar, Storage, Diesel standby
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 5014823.9167
Debt |  | 100%
| Loan: | 5014823.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 5014823.9167 | 4941052.4886 | 4861748.2035 | 4776496.097 | 4684850.0825 | 4586330.617 | 4480422.1915 | 4366570.6341 | 4244180.2098 | 4112610.5038 | 3971173.0698 | 3819127.8283 | 3655679.1937 | 3479971.9114 | 3291086.583 | 3088034.855 | 2869754.2473 | 2635102.5941 | 2382852.0669 | 2111682.7501 | 1820175.7346 | 1506805.6929 | 1169932.8981 | 807794.6437 | 418496.0202
| Principal repaid |  | -73771.428 | -79304.2851 | -85252.1065 | -91646.0145 | -98519.4656 | -105908.4255 | -113851.5574 | -122390.4242 | -131569.706 | -141437.434 | -152045.2415 | -163448.6346 | -175707.2822 | -188885.3284 | -203051.728 | -218280.6076 | -234651.6532 | -252250.5272 | -271169.3168 | -291507.0155 | -313370.0417 | -336872.7948 | -362138.2544 | -389298.6235 | -418496.0202
| Interest |  | -376111.7938 | -370578.9366 | -364631.1153 | -358237.2073 | -351363.7562 | -343974.7963 | -336031.6644 | -327492.7976 | -318313.5157 | -308445.7878 | -297837.9802 | -286434.5871 | -274175.9395 | -260997.8934 | -246831.4937 | -231602.6141 | -215231.5685 | -197632.6946 | -178713.905 | -158376.2063 | -136513.1801 | -113010.427 | -87744.9674 | -60584.5983 | -31387.2015
| C/fwd |  | 4941052.4886 | 4861748.2035 | 4776496.097 | 4684850.0825 | 4586330.617 | 4480422.1915 | 4366570.6341 | 4244180.2098 | 4112610.5038 | 3971173.0698 | 3819127.8283 | 3655679.1937 | 3479971.9114 | 3291086.583 | 3088034.855 | 2869754.2473 | 2635102.5941 | 2382852.0669 | 2111682.7501 | 1820175.7346 | 1506805.6929 | 1169932.8981 | 807794.6437 | 418496.0202 | -3.8999e-09
|  |  | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218 | -449883.2218
|  |  | -73771.428 | 370578.9366 | 364631.1153 | 358237.2073 | 351363.7562 | 343974.7963 | 336031.6644 | 327492.7976 | 318313.5157 | 308445.7878 | 297837.9802 | 286434.5871

## Mix 3 Cash Flow
Cash flow | Mix 3 Wind, Solar, Storage, Diesel standby
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs |  | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392
EBITDA/Net cash flow from operations |  | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 21000000
Interest paid |  | -376111.7938 | -370578.9366 | -364631.1153 | -358237.2073 | -351363.7562 | -343974.7963 | -336031.6644 | -327492.7976 | -318313.5157 | -308445.7878 | -297837.9802 | -286434.5871 | -274175.9395 | -260997.8934 | -246831.4937 | -231602.6141 | -215231.5685 | -197632.6946 | -178713.905 | -158376.2063 | -136513.1801 | -113010.427 | -87744.9674 | -60584.5983 | -31387.2015 | -6232256.6275
Net cash flow pre |  | 169441.9671 | 174974.8242 | 180922.6456 | 187316.5536 | 194190.0046 | 201578.9646 | 209522.0965 | 218060.9633 | 227240.2451 | 237107.973 | 247715.7806 | 259119.1737 | 271377.8213 | 284555.8675 | 298722.2671 | 313951.1467 | 330322.1923 | 347921.0663 | 366839.8558 | 387177.5546 | 409040.5807 | 432543.3339 | 457808.7935 | 484969.1626 | 514166.5593 | 14767743.3725
Flow of Capital
Total start costs |  | -5014823.9167 | [24 empty] | -5014823.9167
Loan receipts |  | 5014823.9167 | [24 empty] | 5014823.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -73771.428 | -79304.2851 | -85252.1065 | -91646.0145 | -98519.4656 | -105908.4255 | -113851.5574 | -122390.4242 | -131569.706 | -141437.434 | -152045.2415 | -163448.6346 | -175707.2822 | -188885.3284 | -203051.728 | -218280.6076 | -234651.6532 | -252250.5272 | -271169.3168 | -291507.0155 | -313370.0417 | -336872.7948 | -362138.2544 | -389298.6235 | -418496.0202 | -5014823.9167
Net cash flow |  | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 95670.5391 | 9752919.4558
Cash Balance b/fwd |  |  | 95670.5391 | 191341.0781 | 287011.6172 | 382682.1563 | 478352.6953 | 574023.2344 | 669693.7735 | 765364.3125 | 861034.8516 | 956705.3907 | 1052375.9297 | 1148046.4688 | 1243717.0079 | 1339387.5469 | 1435058.086 | 1530728.625 | 1626399.1641 | 1722069.7032 | 1817740.2422 | 1913410.7813 | 2009081.3204 | 2104751.8594 | 2200422.3985 | 2296092.9376 | 0
Cash Balance c/fwd |  | 95670.5391 | 191341.0781 | 287011.6172 | 382682.1563 | 478352.6953 | 574023.2344 | 669693.7735 | 765364.3125 | 861034.8516 | 956705.3907 | 1052375.9297 | 1148046.4688 | 1243717.0079 | 1339387.5469 | 1435058.086 | 1530728.625 | 1626399.1641 | 1722069.7032 | 1817740.2422 | 1913410.7813 | 2009081.3204 | 2104751.8594 | 2200422.3985 | 2296092.9376 | 2391763.4766 | 9752919.4558
Debt Service Cover
Net operating income |  | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608
Debt Service |  | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218 | 449883.2218
Debt Service Cover Ratio |  | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Mix 3 Profit and Loss
Profit and Loss Account | Mix 3 Wind, Solar, Storage, Diesel standby
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Costs | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -7361155.9792
Total Operating Costs | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -294446.2392 | -7361155.9792
EBITDA | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 545553.7608 | 28361155.9792
| 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 64.95% | 135.1%
Depreciation | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -200592.9567 | -5014823.9167
EBIT | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 344960.8042 | 33375979.8958
Loan interest | -376111.7938 | -370578.9366 | -364631.1153 | -358237.2073 | -351363.7562 | -343974.7963 | -336031.6644 | -327492.7976 | -318313.5157 | -308445.7878 | -297837.9802 | -286434.5871 | -274175.9395 | -260997.8934 | -246831.4937 | -231602.6141 | -215231.5685 | -197632.6946 | -178713.905 | -158376.2063 | -136513.1801 | -113010.427 | -87744.9674 | -60584.5983 | -31387.2015 | -6232256.6275
Earnings Before Tax | -31150.9896 | -25618.1325 | -19670.3111 | -13276.4031 | -6402.952 | 986.0079 | 8929.1398 | 17468.0066 | 26647.2884 | 36515.0164 | 47122.8239 | 58526.217 | 70784.8646 | 83962.9108 | 98129.3104 | 113358.19 | 129729.2356 | 147328.1096 | 166246.8992 | 186584.5979 | 208447.6241 | 231950.3772 | 257215.8368 | 284376.2059 | 313573.6026 | 39608236.5234
| -1.0384 | -0.85394 | -0.65568 | -0.44255 | -0.21343 | 0.032867 | 0.29764 | 0.58227 | 0.88824 | 1.2172 | 1.5708 | 1.9509 | 2.3595 | 2.7988 | 3.271 | 3.7786 | 4.3243 | 4.9109 | 5.5416 | 6.2195 | 6.9483 | 7.7317 | 8.5739 | 9.4792 | 10.4525

## Mix 4 Summary
Scenario | Mix 4 Wind, Solar,Storage, Diesel standby
Project Capacity (kW) | 1700
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 90000 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 1000000 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 780000 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 5595623.9167
Storage Capacity Capital | 480000 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 250000 |  | Operating Costs (diesel generation) |  |  |  | 13500 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 260000 |  | Operating Costs (solar generation) |  |  |  | 7800 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 286000 |  | Operating Costs (wind generation) |  |  |  | 20000 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 3146000 |  | Operating Costs (Storage) |  |  |  | 9600 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 14850 |  |  | Annual Generation Diesel (kWh) |  | 0
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 304246.2392 |  |  | Annual Generatuion Solar(kWh) |  | 657000
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 1708200
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 2365200
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 5595623.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy sent out |  |  |  | 0
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392
EBITDA (£) | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608
Depreciation (£) | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567
EBIT (£) | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042
Loan Interest (£) | -419671.7938 | -413498.1398 | -406861.4618 | -399727.0329 | -392057.5219 | -383812.7976 | -374949.7189 | -365421.9093 | -355179.514 | -344168.9391 | -332332.571 | -319608.4754 | -305930.0725 | -291225.7895 | -275418.6852 | -258426.0481 | -240158.9632 | -220521.847 | -199411.947 | -176718.8045 | -152323.6764 | -126098.9136 | -97907.2937 | -67601.3022 | -35022.3614
EBT (£) | -107742.9896 | -101569.3356 | -94932.6576 | -87798.2288 | -80128.7177 | -71883.9934 | -63020.9147 | -53493.1052 | -43250.7099 | -32240.1349 | -20403.7669 | -7679.6712 | 5998.7316 | 20703.0147 | 36510.119 | 53502.7561 | 71769.8409 | 91406.9572 | 112516.8572 | 135209.9996 | 159605.1278 | 185829.8905 | 214021.5105 | 244327.502 | 276906.4428
Net Cash flow (£) | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581
NPV
Discount rate | 5%
NPV over 10 years | 260736.5877
NPV over 15 years | 350485.5636
NPV over 20 years | 420806.2346
NPV over 25 years | 475904.3204
Minimum Debt Service Cover Ratio | 1.0673
Units from solar used at time of generation (kWh) | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500
Units from wind used at time of generation (kWh) | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580
Total units sold | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 29.9766 | 29.5356 | 29.0615 | 28.5519 | 28.0041 | 27.4152 | 26.7821 | 26.1016 | 25.37 | 24.5835 | 23.738 | 22.8292 | 21.8521 | 20.8018 | 19.6728 | 18.459 | 17.1542 | 15.7516 | 14.2437 | 12.6228 | 10.8803 | 9.0071 | 6.9934 | 4.8287 | 2.5016
Repayment of principal | 5.8797 | 6.3206 | 6.7947 | 7.3043 | 7.8521 | 8.441 | 9.0741 | 9.7547 | 10.4863 | 11.2727 | 12.1182 | 13.0271 | 14.0041 | 15.0544 | 16.1835 | 17.3972 | 18.702 | 20.1047 | 21.6125 | 23.2335 | 24.976 | 26.8492 | 28.8628 | 31.0276 | 33.3546
Operating Costs | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319 | 21.7319
| 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881 | 57.5881
Surplus/shortfall p/kWh | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119 | 2.4119
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## Mix 4 Interest Calcualtions
Interest Calculation |  | Mix 4 Wind, Solar,Storage, Diesel standby
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 5595623.9167
Debt |  | 100%
| Loan: | 5595623.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 5595623.9167 | 5513308.5306 | 5424819.4905 | 5329693.7724 | 5227433.6255 | 5117503.9675 | 4999329.5852 | 4872292.1243 | 4735726.8537 | 4588919.1879 | 4431100.9471 | 4261446.3383 | 4079067.6338 | 3883010.5265 | 3672249.1361 | 3445680.6414 | 3202119.5097 | 2940291.293 | 2658825.9602 | 2356250.7273 | 2030982.352 | 1681318.8485 | 1305430.5823 | 901350.6961 | 466964.8185
| Principal repaid |  | -82315.3861 | -88489.0401 | -95125.7181 | -102260.1469 | -109929.658 | -118174.3823 | -127037.461 | -136565.2705 | -146807.6658 | -157818.2408 | -169654.6088 | -182378.7045 | -196057.1073 | -210761.3904 | -226568.4947 | -243561.1318 | -261828.2166 | -281465.3329 | -302575.2328 | -325268.3753 | -349663.5035 | -375888.2662 | -404079.8862 | -434385.8777 | -466964.8185
| Interest |  | -419671.7938 | -413498.1398 | -406861.4618 | -399727.0329 | -392057.5219 | -383812.7976 | -374949.7189 | -365421.9093 | -355179.514 | -344168.9391 | -332332.571 | -319608.4754 | -305930.0725 | -291225.7895 | -275418.6852 | -258426.0481 | -240158.9632 | -220521.847 | -199411.947 | -176718.8045 | -152323.6764 | -126098.9136 | -97907.2937 | -67601.3022 | -35022.3614
| C/fwd |  | 5513308.5306 | 5424819.4905 | 5329693.7724 | 5227433.6255 | 5117503.9675 | 4999329.5852 | 4872292.1243 | 4735726.8537 | 4588919.1879 | 4431100.9471 | 4261446.3383 | 4079067.6338 | 3883010.5265 | 3672249.1361 | 3445680.6414 | 3202119.5097 | 2940291.293 | 2658825.9602 | 2356250.7273 | 2030982.352 | 1681318.8485 | 1305430.5823 | 901350.6961 | 466964.8185 | -3.376e-09
|  |  | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799 | -501987.1799
|  |  | -82315.3861 | 413498.1398 | 406861.4618 | 399727.0329 | 392057.5219 | 383812.7976 | 374949.7189 | 365421.9093 | 355179.514 | 344168.9391 | 332332.571 | 319608.4754

## Mix 4 Cash Flow
Cash flow | Mix 4 Wind, Solar,Storage, Diesel standby
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs |  | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392
EBITDA/Net cash flow from operations |  | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 21000000
Interest paid |  | -419671.7938 | -413498.1398 | -406861.4618 | -399727.0329 | -392057.5219 | -383812.7976 | -374949.7189 | -365421.9093 | -355179.514 | -344168.9391 | -332332.571 | -319608.4754 | -305930.0725 | -291225.7895 | -275418.6852 | -258426.0481 | -240158.9632 | -220521.847 | -199411.947 | -176718.8045 | -152323.6764 | -126098.9136 | -97907.2937 | -67601.3022 | -35022.3614 | -6954055.5799
Net cash flow pre |  | 116081.9671 | 122255.621 | 128892.299 | 136026.7279 | 143696.2389 | 151940.9633 | 160804.0419 | 170331.8515 | 180574.2468 | 191584.8217 | 203421.1898 | 216145.2855 | 229823.6883 | 244527.9713 | 260335.0756 | 277327.7127 | 295594.7976 | 315231.9139 | 336341.8138 | 359034.9563 | 383430.0844 | 409654.8472 | 437846.4672 | 468152.4586 | 500731.3994 | 14045944.4201
Flow of Capital
Total start costs |  | -5595623.9167 | [24 empty] | -5595623.9167
Loan receipts |  | 5595623.9167 | [24 empty] | 5595623.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -82315.3861 | -88489.0401 | -95125.7181 | -102260.1469 | -109929.658 | -118174.3823 | -127037.461 | -136565.2705 | -146807.6658 | -157818.2408 | -169654.6088 | -182378.7045 | -196057.1073 | -210761.3904 | -226568.4947 | -243561.1318 | -261828.2166 | -281465.3329 | -302575.2328 | -325268.3753 | -349663.5035 | -375888.2662 | -404079.8862 | -434385.8777 | -466964.8185 | -5595623.9167
Net cash flow |  | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 33766.581 | 8450320.5035
Cash Balance b/fwd |  |  | 33766.581 | 67533.1619 | 101299.7429 | 135066.3239 | 168832.9049 | 202599.4858 | 236366.0668 | 270132.6478 | 303899.2287 | 337665.8097 | 371432.3907 | 405198.9717 | 438965.5526 | 472732.1336 | 506498.7146 | 540265.2955 | 574031.8765 | 607798.4575 | 641565.0385 | 675331.6194 | 709098.2004 | 742864.7814 | 776631.3623 | 810397.9433 | 0
Cash Balance c/fwd |  | 33766.581 | 67533.1619 | 101299.7429 | 135066.3239 | 168832.9049 | 202599.4858 | 236366.0668 | 270132.6478 | 303899.2287 | 337665.8097 | 371432.3907 | 405198.9717 | 438965.5526 | 472732.1336 | 506498.7146 | 540265.2955 | 574031.8765 | 607798.4575 | 641565.0385 | 675331.6194 | 709098.2004 | 742864.7814 | 776631.3623 | 810397.9433 | 844164.5243 | 8450320.5035
Debt Service Cover
Net operating income |  | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608
Debt Service |  | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799 | 501987.1799
Debt Service Cover Ratio |  | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 1.0673
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Mix 4 Profit and Loss
Profit and Loss Account | Mix 4 Wind, Solar,Storage, Diesel standby
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Costs | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -7606155.9792
Total Operating Costs | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -304246.2392 | -7606155.9792
EBITDA | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 535753.7608 | 28606155.9792
| 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 63.78% | 136.2%
Depreciation | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -223824.9567 | -5595623.9167
EBIT | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 311928.8042 | 34201779.8958
Loan interest | -419671.7938 | -413498.1398 | -406861.4618 | -399727.0329 | -392057.5219 | -383812.7976 | -374949.7189 | -365421.9093 | -355179.514 | -344168.9391 | -332332.571 | -319608.4754 | -305930.0725 | -291225.7895 | -275418.6852 | -258426.0481 | -240158.9632 | -220521.847 | -199411.947 | -176718.8045 | -152323.6764 | -126098.9136 | -97907.2937 | -67601.3022 | -35022.3614 | -6954055.5799
Earnings Before Tax | -107742.9896 | -101569.3356 | -94932.6576 | -87798.2288 | -80128.7177 | -71883.9934 | -63020.9147 | -53493.1052 | -43250.7099 | -32240.1349 | -20403.7669 | -7679.6712 | 5998.7316 | 20703.0147 | 36510.119 | 53502.7561 | 71769.8409 | 91406.9572 | 112516.8572 | 135209.9996 | 159605.1278 | 185829.8905 | 214021.5105 | 244327.502 | 276906.4428 | 41155835.4757
| -3.5914 | -3.3856 | -3.1644 | -2.9266 | -2.671 | -2.3961 | -2.1007 | -1.7831 | -1.4417 | -1.0747 | -0.68013 | -0.25599 | 0.19996 | 0.6901 | 1.217 | 1.7834 | 2.3923 | 3.0469 | 3.7506 | 4.507 | 5.3202 | 6.1943 | 7.1341 | 8.1443 | 9.2302

## 100% Renewable Summary
Scenario | 100% renewable, Wind,Solar, Storage (updated Narec)
Project Capacity (kW) | 3500
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 0 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 1000000 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 3900000 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 30279623.9167
Storage Capacity Capital | 18000000 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 100000 |  | Operating Costs (diesel generation) |  |  |  | 0 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 2300000 |  | Operating Costs (solar generation) |  |  |  | 39000 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 2530000 |  | Operating Costs (wind generation) |  |  |  | 20000 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 27830000 |  | Operating Costs (Storage) |  |  |  | 360000 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 17250 |  |  | Annual Generation Diesel (kWh) |  | 0
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 674746.2392 |  |  | Annual Generatuion Solar(kWh) |  | 673796.7914
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 782203.2086
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1456000
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 30279623.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy sent out |  |  |  | 0
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392
EBITDA (£) | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608
Depreciation (£) | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567
EBIT (£) | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958
Loan Interest (£) | -2270971.7938 | -2237564.2734 | -2201651.189 | -2163044.6232 | -2121542.565 | -2076927.8525 | -2028967.0365 | -1977409.1594 | -1921984.4414 | -1862402.8696 | -1798352.6799 | -1729498.726 | -1655480.7255 | -1575911.375 | -1490374.3232 | -1398421.9925 | -1299573.2371 | -1193310.8249 | -1079078.7319 | -956279.2318 | -824269.7693 | -682359.5971 | -529806.162 | -365811.2192 | -189516.6557
EBT (£) | -3316902.9896 | -3283495.4692 | -3247582.3848 | -3208975.819 | -3167473.7609 | -3122859.0483 | -3074898.2324 | -3023340.3552 | -2967915.6372 | -2908334.0654 | -2844283.8757 | -2775429.9218 | -2701411.9213 | -2621842.5708 | -2536305.519 | -2444353.1884 | -2345504.4329 | -2239242.0207 | -2125009.9277 | -2002210.4277 | -1870200.9652 | -1728290.7929 | -1575737.3578 | -1411742.415 | -1235447.8516
Net Cash flow (£) | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638
NPV
Discount rate | 5%
NPV over 10 years | -19699316.713
NPV over 15 years | -26480081.6062
NPV over 20 years | -31792988.3288
NPV over 25 years | -35955789.7659
Minimum Debt Service Cover Ratio | 0.060835
Units from solar used at time of generation (kWh) | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500
Units from wind used at time of generation (kWh) | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580
Total units | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 162.2123 | 159.826 | 157.2608 | 154.5032 | 151.5388 | 148.352 | 144.9262 | 141.2435 | 137.2846 | 133.0288 | 128.4538 | 123.5356 | 118.2486 | 112.5651 | 106.4553 | 99.8873 | 92.8267 | 85.2365 | 77.0771 | 68.3057 | 58.8764 | 48.74 | 37.8433 | 26.1294 | 13.5369
Repayment of principal | 31.8167 | 34.2029 | 36.7682 | 39.5258 | 42.4902 | 45.677 | 49.1027 | 52.7854 | 56.7444 | 61.0002 | 65.5752 | 70.4933 | 75.7803 | 81.4639 | 87.5736 | 94.1417 | 101.2023 | 108.7925 | 116.9519 | 125.7233 | 135.1525 | 145.289 | 156.1857 | 167.8996 | 180.4921
Operating Costs | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962 | 48.1962
| 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251 | 242.2251
Surplus/shortfall p/kWh | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251 | -182.2251
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## 100% Renewable Interest Calcula
Interest Calculation |  | 100% renewable, Wind,Solar, Storage (updated Narec)
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 30279623.9167
Debt |  | 100%
| Loan: | 30279623.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 30279623.9167 | 29834190.3116 | 29355349.1861 | 28840594.9762 | 28287234.2005 | 27692371.3667 | 27052893.8204 | 26365455.458 | 25626459.2185 | 24832038.2611 | 23978035.7318 | 23059983.0128 | 22073076.3399 | 21012151.6665 | 19871657.6427 | 18645626.567 | 17327643.1607 | 15910810.9989 | 14387716.4249 | 12750389.758 | 10990263.5909 | 9098127.9614 | 7064082.1597 | 4877482.9228 | 2526888.7431
| Principal repaid |  | -445433.6051 | -478841.1255 | -514754.2099 | -553360.7756 | -594862.8338 | -639477.5464 | -687438.3623 | -738996.2395 | -794420.9575 | -854002.5293 | -918052.719 | -986906.6729 | -1060924.6734 | -1140494.0239 | -1226031.0757 | -1317983.4063 | -1416832.1618 | -1523094.5739 | -1637326.667 | -1760126.167 | -1892135.6295 | -2034045.8018 | -2186599.2369 | -2350594.1796 | -2526888.7431
| Interest |  | -2270971.7938 | -2237564.2734 | -2201651.189 | -2163044.6232 | -2121542.565 | -2076927.8525 | -2028967.0365 | -1977409.1594 | -1921984.4414 | -1862402.8696 | -1798352.6799 | -1729498.726 | -1655480.7255 | -1575911.375 | -1490374.3232 | -1398421.9925 | -1299573.2371 | -1193310.8249 | -1079078.7319 | -956279.2318 | -824269.7693 | -682359.5971 | -529806.162 | -365811.2192 | -189516.6557
| C/fwd |  | 29834190.3116 | 29355349.1861 | 28840594.9762 | 28287234.2005 | 27692371.3667 | 27052893.8204 | 26365455.458 | 25626459.2185 | 24832038.2611 | 23978035.7318 | 23059983.0128 | 22073076.3399 | 21012151.6665 | 19871657.6427 | 18645626.567 | 17327643.1607 | 15910810.9989 | 14387716.4249 | 12750389.758 | 10990263.5909 | 9098127.9614 | 7064082.1597 | 4877482.9228 | 2526888.7431 | 2.794e-08
|  |  | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989 | -2716405.3989
|  |  | -445433.6051 | 2237564.2734 | 2201651.189 | 2163044.6232 | 2121542.565 | 2076927.8525 | 2028967.0365 | 1977409.1594 | 1921984.4414 | 1862402.8696 | 1798352.6799 | 1729498.726

## 100% Renewable Cash Flow
Cash flow | 100% renewable, Wind,Solar, Storage (updated Narec)
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs |  | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392
EBITDA/Net cash flow from operations |  | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 21000000
Interest paid |  | -2270971.7938 | -2237564.2734 | -2201651.189 | -2163044.6232 | -2121542.565 | -2076927.8525 | -2028967.0365 | -1977409.1594 | -1921984.4414 | -1862402.8696 | -1798352.6799 | -1729498.726 | -1655480.7255 | -1575911.375 | -1490374.3232 | -1398421.9925 | -1299573.2371 | -1193310.8249 | -1079078.7319 | -956279.2318 | -824269.7693 | -682359.5971 | -529806.162 | -365811.2192 | -189516.6557 | -37630511.0548
Net cash flow pre |  | -2105718.0329 | -2072310.5125 | -2036397.4281 | -1997790.8624 | -1956288.8042 | -1911674.0917 | -1863713.2757 | -1812155.3985 | -1756730.6806 | -1697149.1087 | -1633098.919 | -1564244.9651 | -1490226.9647 | -1410657.6142 | -1325120.5624 | -1233168.2317 | -1134319.4762 | -1028057.0641 | -913824.971 | -791025.471 | -659016.0085 | -517105.8363 | -364552.4011 | -200557.4584 | -24262.8949 | -16630511.0548
Flow of Capital
Total start costs |  | -30279623.9167 | [24 empty] | -30279623.9167
Loan receipts |  | 30279623.9167 | [24 empty] | 30279623.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -445433.6051 | -478841.1255 | -514754.2099 | -553360.7756 | -594862.8338 | -639477.5464 | -687438.3623 | -738996.2395 | -794420.9575 | -854002.5293 | -918052.719 | -986906.6729 | -1060924.6734 | -1140494.0239 | -1226031.0757 | -1317983.4063 | -1416832.1618 | -1523094.5739 | -1637326.667 | -1760126.167 | -1892135.6295 | -2034045.8018 | -2186599.2369 | -2350594.1796 | -2526888.7431 | -30279623.9167
Net cash flow |  | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -2551151.638 | -46910134.9714
Cash Balance b/fwd |  |  | -2551151.638 | -5102303.276 | -7653454.9141 | -10204606.5521 | -12755758.1901 | -15306909.8281 | -17858061.4662 | -20409213.1042 | -22960364.7422 | -25511516.3802 | -28062668.0183 | -30613819.6563 | -33164971.2943 | -35716122.9323 | -38267274.5704 | -40818426.2084 | -43369577.8464 | -45920729.4844 | -48471881.1224 | -51023032.7605 | -53574184.3985 | -56125336.0365 | -58676487.6745 | -61227639.3126 | 0
Cash Balance c/fwd |  | -2551151.638 | -5102303.276 | -7653454.9141 | -10204606.5521 | -12755758.1901 | -15306909.8281 | -17858061.4662 | -20409213.1042 | -22960364.7422 | -25511516.3802 | -28062668.0183 | -30613819.6563 | -33164971.2943 | -35716122.9323 | -38267274.5704 | -40818426.2084 | -43369577.8464 | -45920729.4844 | -48471881.1224 | -51023032.7605 | -53574184.3985 | -56125336.0365 | -58676487.6745 | -61227639.3126 | -63778790.9506 | -46910134.9714
Debt Service Cover
Net operating income |  | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608
Debt Service |  | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989 | 2716405.3989
Debt Service Cover Ratio |  | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835 | 0.060835
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 100% Renewable Profit and Loss
Profit and Loss Account | 100% renewable, Wind,Solar, Storage (updated Narec)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Costs | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -16868655.9792
Total Operating Costs | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -674746.2392 | -16868655.9792
EBITDA | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 165253.7608 | 37868655.9792
| 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 19.67% | 180.3%
Depreciation | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -1211184.9567 | -30279623.9167
EBIT | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | -1045931.1958 | 68148279.8958
Loan interest | -2270971.7938 | -2237564.2734 | -2201651.189 | -2163044.6232 | -2121542.565 | -2076927.8525 | -2028967.0365 | -1977409.1594 | -1921984.4414 | -1862402.8696 | -1798352.6799 | -1729498.726 | -1655480.7255 | -1575911.375 | -1490374.3232 | -1398421.9925 | -1299573.2371 | -1193310.8249 | -1079078.7319 | -956279.2318 | -824269.7693 | -682359.5971 | -529806.162 | -365811.2192 | -189516.6557 | -37630511.0548
Earnings Before Tax | -3316902.9896 | -3283495.4692 | -3247582.3848 | -3208975.819 | -3167473.7609 | -3122859.0483 | -3074898.2324 | -3023340.3552 | -2967915.6372 | -2908334.0654 | -2844283.8757 | -2775429.9218 | -2701411.9213 | -2621842.5708 | -2536305.519 | -2444353.1884 | -2345504.4329 | -2239242.0207 | -2125009.9277 | -2002210.4277 | -1870200.9652 | -1728290.7929 | -1575737.3578 | -1411742.415 | -1235447.8516 | 105778790.9506
| -110.5634 | -109.4498 | -108.2527 | -106.9659 | -105.5825 | -104.0953 | -102.4966 | -100.778 | -98.9305 | -96.9445 | -94.8095 | -92.5143 | -90.0471 | -87.3948 | -84.5435 | -81.4784 | -78.1835 | -74.6414 | -70.8337 | -66.7403 | -62.34 | -57.6097 | -52.5246 | -47.0581 | -41.1816

## 100% Wind Summary
Scenario | 100% Wind & Storage
Project Capacity (kW) | 500
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 0 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 1000000 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 0 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 9908063.9167
Storage Capacity Capital | 5064000 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 100000 |  | Operating Costs (diesel generation) |  |  |  | 0 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 616400 |  | Operating Costs (solar generation) |  |  |  | 0 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 678040 |  | Operating Costs (wind generation) |  |  |  | 20000 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 7458440 |  | Operating Costs (Storage) |  |  |  | 101280 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 14250 |  |  | Annual Generation Diesel (kWh) |  | 0
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 374026.2392 |  |  | Annual Generatuion Solar(kWh) |  | 0
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 1456000
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1456000
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 9908063.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy sent out |  |  |  | 0
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392
EBITDA (£) | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608
Depreciation (£) | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567
EBIT (£) | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042
Loan Interest (£) | -743104.7938 | -732173.2231 | -720421.7847 | -707788.9884 | -694208.7324 | -679609.9572 | -663916.2738 | -647045.5642 | -628909.5513 | -609413.3375 | -588454.9077 | -565924.5956 | -541704.5101 | -515667.9182 | -487678.582 | -457590.0455 | -425244.8687 | -390473.8037 | -353094.9088 | -312912.5968 | -269716.6115 | -223280.9272 | -173362.5665 | -119700.3289 | -62013.4234
EBT (£) | -673453.5896 | -662522.019 | -650770.5805 | -638137.7842 | -624557.5282 | -609958.753 | -594265.0696 | -577394.36 | -559258.3472 | -539762.1334 | -518803.7035 | -496273.3915 | -472053.306 | -446016.7141 | -418027.3778 | -387938.8413 | -355593.6645 | -320822.5995 | -283443.7047 | -243261.3927 | -200065.4073 | -153629.723 | -103711.3624 | -50049.1247 | 7637.7808
Net Cash flow (£) | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079
NPV
Discount rate | 5%
NPV over 10 years | -3265408.2529
NPV over 15 years | -4389404.8851
NPV over 20 years | -5270085.6575
NPV over 25 years | -5960122.087
Minimum Debt Service Cover Ratio | 0.52424
Units from solar used at time of generation (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind used at time of generation (kWh) | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000 | 1456000
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200 | 252200
Total wind energy available (kWh) | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200 | 1708200
Renewabe energy dependent upon storage (kWh) | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000 | -56000
Minimum Storage Capacity to handle available wind energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200 | -308200
Total units | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 53.0789 | 52.2981 | 51.4587 | 50.5564 | 49.5863 | 48.5436 | 47.4226 | 46.2175 | 44.9221 | 43.5295 | 42.0325 | 40.4232 | 38.6932 | 36.8334 | 34.8342 | 32.685 | 30.3746 | 27.891 | 25.2211 | 22.3509 | 19.2655 | 15.9486 | 12.383 | 8.55 | 4.4295
Repayment of principal | 10.411 | 11.1918 | 12.0312 | 12.9336 | 13.9036 | 14.9464 | 16.0673 | 17.2724 | 18.5678 | 19.9604 | 21.4574 | 23.0667 | 24.7968 | 26.6565 | 28.6557 | 30.8049 | 33.1153 | 35.5989 | 38.2689 | 41.139 | 44.2245 | 47.5413 | 51.1069 | 54.9399 | 59.0604
Operating Costs | 26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162 | -26.7162
| 90.2061 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738 | 36.7738
Surplus/shortfall p/kWh | -30.2061 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262 | 23.2262
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## 100% Wind Interest Calculations
Interest Calculation
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 9908063.9167
Debt |  | 100%
| Loan: | 9908063.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 9908063.9167 | 9762309.6417 | 9605623.7961 | 9437186.5121 | 9256116.4318 | 9061466.0955 | 8852216.984 | 8627274.189 | 8385460.6845 | 8125511.1671 | 7846065.436 | 7545661.275 | 7222726.8019 | 6875572.2433 | 6502381.0928 | 6101200.6061 | 5669931.5828 | 5206317.3828 | 4707932.1178 | 4172167.958 | 3596221.4861 | 2977079.0288 | 2311500.8873 | 1596004.3851 | 826845.6453
| Principal repaid |  | -145754.275 | -156685.8456 | -168437.284 | -181070.0803 | -194650.3363 | -209249.1115 | -224942.7949 | -241813.5045 | -259949.5174 | -279445.7312 | -300404.161 | -322934.4731 | -347154.5586 | -373191.1505 | -401180.4867 | -431269.0233 | -463614.2 | -498385.265 | -535764.1599 | -575946.4719 | -619142.4573 | -665578.1415 | -715496.5022 | -769158.7398 | -826845.6453
| Interest |  | -743104.7938 | -732173.2231 | -720421.7847 | -707788.9884 | -694208.7324 | -679609.9572 | -663916.2738 | -647045.5642 | -628909.5513 | -609413.3375 | -588454.9077 | -565924.5956 | -541704.5101 | -515667.9182 | -487678.582 | -457590.0455 | -425244.8687 | -390473.8037 | -353094.9088 | -312912.5968 | -269716.6115 | -223280.9272 | -173362.5665 | -119700.3289 | -62013.4234
| C/fwd |  | 9762309.6417 | 9605623.7961 | 9437186.5121 | 9256116.4318 | 9061466.0955 | 8852216.984 | 8627274.189 | 8385460.6845 | 8125511.1671 | 7846065.436 | 7545661.275 | 7222726.8019 | 6875572.2433 | 6502381.0928 | 6101200.6061 | 5669931.5828 | 5206317.3828 | 4707932.1178 | 4172167.958 | 3596221.4861 | 2977079.0288 | 2311500.8873 | 1596004.3851 | 826845.6453 | -2.3283e-09
|  |  | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687 | -888859.0687
|  |  | -145754.275 | 732173.2231 | 720421.7847 | 707788.9884 | 694208.7324 | 679609.9572 | 663916.2738 | 647045.5642 | 628909.5513 | 609413.3375 | 588454.9077 | 565924.5956

## 100% Wind Cash Flow
Cash flow
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs |  | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392
EBITDA/Net cash flow from operations |  | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 21000000
Interest paid |  | -743104.7938 | -732173.2231 | -720421.7847 | -707788.9884 | -694208.7324 | -679609.9572 | -663916.2738 | -647045.5642 | -628909.5513 | -609413.3375 | -588454.9077 | -565924.5956 | -541704.5101 | -515667.9182 | -487678.582 | -457590.0455 | -425244.8687 | -390473.8037 | -353094.9088 | -312912.5968 | -269716.6115 | -223280.9272 | -173362.5665 | -119700.3289 | -62013.4234 | -12313412.8011
Net cash flow pre |  | -277131.0329 | -266199.4623 | -254448.0239 | -241815.2276 | -228234.9716 | -213636.1963 | -197942.513 | -181071.8033 | -162935.7905 | -143439.5767 | -122481.1469 | -99950.8348 | -75730.7493 | -49694.1574 | -21704.8211 | 8383.7154 | 40728.8921 | 75499.9571 | 112878.852 | 153061.164 | 196257.1494 | 242692.8337 | 292611.1943 | 346273.4319 | 403960.3374 | 8686587.1989
Flow of Capital
Total start costs |  | -9908063.9167 | [24 empty] | -9908063.9167
Loan receipts |  | 9908063.9167 | [24 empty] | 9908063.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -145754.275 | -156685.8456 | -168437.284 | -181070.0803 | -194650.3363 | -209249.1115 | -224942.7949 | -241813.5045 | -259949.5174 | -279445.7312 | -300404.161 | -322934.4731 | -347154.5586 | -373191.1505 | -401180.4867 | -431269.0233 | -463614.2 | -498385.265 | -535764.1599 | -575946.4719 | -619142.4573 | -665578.1415 | -715496.5022 | -769158.7398 | -826845.6453 | -9908063.9167
Net cash flow |  | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -422885.3079 | -1221476.7177
Cash Balance b/fwd |  |  | -422885.3079 | -845770.6158 | -1268655.9236 | -1691541.2315 | -2114426.5394 | -2537311.8473 | -2960197.1551 | -3383082.463 | -3805967.7709 | -4228853.0788 | -4651738.3866 | -5074623.6945 | -5497509.0024 | -5920394.3103 | -6343279.6181 | -6766164.926 | -7189050.2339 | -7611935.5418 | -8034820.8497 | -8457706.1575 | -8880591.4654 | -9303476.7733 | -9726362.0812 | -10149247.389 | 0
Cash Balance c/fwd |  | -422885.3079 | -845770.6158 | -1268655.9236 | -1691541.2315 | -2114426.5394 | -2537311.8473 | -2960197.1551 | -3383082.463 | -3805967.7709 | -4228853.0788 | -4651738.3866 | -5074623.6945 | -5497509.0024 | -5920394.3103 | -6343279.6181 | -6766164.926 | -7189050.2339 | -7611935.5418 | -8034820.8497 | -8457706.1575 | -8880591.4654 | -9303476.7733 | -9726362.0812 | -10149247.389 | -10572132.6969 | -1221476.7177
Debt Service Cover
Net operating income |  | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608
Debt Service |  | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687 | 888859.0687
Debt Service Cover Ratio |  | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424 | 0.52424
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 100% Wind Profit and Loss
Profit and Loss Account
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Costs | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -9350655.9792
Total Operating Costs | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -374026.2392 | -9350655.9792
EBITDA | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 465973.7608 | 30350655.9792
| 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 55.47% | 144.5%
Depreciation | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -396322.5567 | -9908063.9167
EBIT | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 69651.2042 | 40258719.8958
Loan interest | -743104.7938 | -732173.2231 | -720421.7847 | -707788.9884 | -694208.7324 | -679609.9572 | -663916.2738 | -647045.5642 | -628909.5513 | -609413.3375 | -588454.9077 | -565924.5956 | -541704.5101 | -515667.9182 | -487678.582 | -457590.0455 | -425244.8687 | -390473.8037 | -353094.9088 | -312912.5968 | -269716.6115 | -223280.9272 | -173362.5665 | -119700.3289 | -62013.4234 | -12313412.8011
Earnings Before Tax | -673453.5896 | -662522.019 | -650770.5805 | -638137.7842 | -624557.5282 | -609958.753 | -594265.0696 | -577394.36 | -559258.3472 | -539762.1334 | -518803.7035 | -496273.3915 | -472053.306 | -446016.7141 | -418027.3778 | -387938.8413 | -355593.6645 | -320822.5995 | -283443.7047 | -243261.3927 | -200065.4073 | -153629.723 | -103711.3624 | -50049.1247 | 7637.7808 | 52572132.6969
| -22.4485 | -22.0841 | -21.6924 | -21.2713 | -20.8186 | -20.332 | -19.8088 | -19.2465 | -18.6419 | -17.9921 | -17.2935 | -16.5424 | -15.7351 | -14.8672 | -13.9342 | -12.9313 | -11.8531 | -10.6941 | -9.4481 | -8.1087 | -6.6688 | -5.121 | -3.457 | -1.6683 | 0.25459

## 100% Solar Summary
Scenario | 100% Solar & Storage
Project Capacity (kW) | 1500
Project Build Costs |  |  | Operating Costs | [6 empty] | Revenue |  |  |  |  | Financing/Economic
Diesel Generation Capital | 0 |  | Operating Salaries |  |  |  | 160000 |  |  | Total consumption |  | 1400000 |  |  | Debt Finance % |  | 100%
Wind Generation Capital | 0 |  | Admin/billing |  |  |  | 40000 |  |  | Tariff p/kWh |  | 60 |  |  | Senior Debt Rate |  | 7.5%
Solar Generation Capital | 1950000 |  | Salaries total |  |  |  | 200000 |  |  | Demand growth % |  | 0 |  |  | Initial Debt |  | 11057563.9167
Storage Capacity Capital | 5064000 | [8 empty] | Years 1-5 |  | 0% |  |  | Debt term years |  | 25
Balance of Plant Capital | 100000 |  | Operating Costs (diesel generation) |  |  |  | 0 |  |  | Years 6-10 |  | 0% |  |  | Depreciation years |  | 25
Freight (10%) | 711400 |  | Operating Costs (solar generation) |  |  |  | 19500 |  |  | Years 11-15 |  | 0% |  |  | Inflation |  | 0%
Contingency (10%) | 782540 |  | Operating Costs (wind generation) |  |  |  | 0 |  |  | Years 16-25 |  | 0% |  |  | fuel cost escalation |  | 0%
Generation Total | 8607940 |  | Operating Costs (Storage) |  |  |  | 101280 | [7 empty] | tariff price escalation |  | 0%
|  |  | Operating Costs (distribution) |  |  |  | 24496.2392 |  |  | Generation
Underground Cable | 542630 |  | Other Admin Costs |  |  |  | 14000 |  |  | Pre losses and auxiliary consumption
Substations | 359081.8 |  | Land Rental |  |  |  | 15500 |  |  | Annual Generation Diesel (kWh) |  | 0
Service Terminations | 196652.5 |  | Total operating costs (ex fuel) |  |  |  | 374776.2392 |  |  | Annual Generatuion Solar(kWh) |  | 1456000
Misc | 113166.5333 | [8 empty] | Annual Generationn Wind (kWh) |  | 0
Civil Works | 855400 |  | Fuel cost per litre (pence) |  |  |  | 87 |  |  | Total Generation required |  | 1456000
Project Management | 160000 |  | Efficiency (kWh/litre) |  |  |  | 3.9583
Contingency (10%) | 222693.0833
Distribution Total | 2449623.9167 |  | Annual Electrical Consumption (kWh) |  |  |  | 1400000
Total | 11057563.9167
|  |  | Fuel cost per KWh (p/KWh)of diesel generation |  |  |  | 21.9789
|  |  | Fuel cost/kWh (p/kWh) of total energy sent out |  |  |  | 0 | 0
Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Total Revenue(£) | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000
Total Operating Costs (£) | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392
EBITDA (£) | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608
Depreciation (£) | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567
EBIT (£) | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042
Loan Interest (£) | -829317.2938 | -817117.4793 | -804002.6789 | -789904.2683 | -774748.477 | -758456.0014 | -740941.5901 | -722113.5979 | -701873.5063 | -680115.4078 | -656725.452 | -631581.2494 | -604551.2317 | -575493.9627 | -544257.3984 | -510678.0919 | -474580.3373 | -435775.2512 | -394059.7836 | -349215.656
EBT (£) | -806396.0896 | -794196.2752 | -781081.4747 | -766983.0642 | -751827.2729 | -735534.7972 | -718020.3859 | -699192.3937 | -678952.3021 | -657194.2037 | -633804.2478 | -608660.0453 | -581630.0276 | -552572.7585 | -521336.1943 | -487756.8877 | -451659.1332 | -412854.047 | -371138.5795 | -326294.4518
Net Cash flow (£) | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249
NPV
Discount rate | 5%
NPV over 10 years | -4067483.5239
NPV over 15 years | -5467565.0538
NPV over 20 years | -6564565.5677
NPV over 25 years | -7424094.175
Minimum Debt Service Cover Ratio | 0.46898
Units from solar used at time of generation (kWh) | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500 | 328500
Units from wind used at time of generation (kWh) | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920 | 1024920
Units from solar available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units from wind available via storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Renewable energy available (kWh) | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420 | 1353420
Renewabe energy dependent upon storage (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Storage Capacity to handle available renewable energy (kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units generated by diesel (kWh) | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580 | 46580
Total units | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000 | 1400000
Average cost of fuel per kWh sent out | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 59.2369 | 58.3655 | 57.4288 | 56.4217 | 55.3392 | 54.1754 | 52.9244 | 51.5795 | 50.1338 | 48.5797 | 46.909 | 45.1129 | 43.1822 | 41.1067 | 38.8755 | 36.477 | 33.8986 | 31.1268 | 28.1471 | 24.944
Repayment of principal | 11.6189 | 12.4903 | 13.4271 | 14.4341 | 15.5166 | 16.6804 | 17.9314 | 19.2763 | 20.722 | 22.2761 | 23.9469 | 25.7429 | 27.6736 | 29.7491 | 31.9803 | 34.3788 | 36.9572 | 39.729 | 42.7087 | 45.9118
Operating Costs | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697 | 26.7697
| 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256 | 97.6256
Surplus/shortfall p/kWh | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256 | -37.6256
Tariff | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60

## 100% Solar Interest Calculation
Interest Calculation |  | 100% Solar & Storage
|  | Year: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Total asset cost |  | 11057563.9167
Debt |  | 100%
| Loan: | 11057563.9167
| Rate: | 7.5%
| Period of loan: | 25
| B/fwd |  | 11057563.9167 | 10894899.7246 | 10720035.7182 | 10532056.9113 | 10329979.6939 | 10112746.6852 | 9879221.2008 | 9628181.3051 | 9358313.4172 | 9068205.4377 | 8756339.3598 | 8421083.326 | 8060683.0896 | 7673252.8356 | 7256765.3125 | 6809041.2252 | 6327737.8313 | 5810336.6829 | 5254130.4483 | 4656208.7462 | 4013442.9163 | 3322469.6493 | 2579673.3872 | 1781167.4055 | 922773.4751
| Principal repaid |  | -162664.192 | -174864.0064 | -187978.8069 | -202077.2174 | -217233.0087 | -233525.4844 | -251039.8957 | -269867.8879 | -290107.9795 | -311866.0779 | -335256.0338 | -360400.2363 | -387430.254 | -416487.5231 | -447724.0873 | -481303.3939 | -517401.1484 | -556206.2346 | -597921.7021 | -642765.8298 | -690973.267 | -742796.2621 | -798505.9817 | -858393.9304 | -922773.4751
| Interest |  | -829317.2938 | -817117.4793 | -804002.6789 | -789904.2683 | -774748.477 | -758456.0014 | -740941.5901 | -722113.5979 | -701873.5063 | -680115.4078 | -656725.452 | -631581.2494 | -604551.2317 | -575493.9627 | -544257.3984 | -510678.0919 | -474580.3373 | -435775.2512 | -394059.7836 | -349215.656 | -301008.2187 | -249185.2237 | -193475.504 | -133587.5554 | -69208.0106
| C/fwd |  | 10894899.7246 | 10720035.7182 | 10532056.9113 | 10329979.6939 | 10112746.6852 | 9879221.2008 | 9628181.3051 | 9358313.4172 | 9068205.4377 | 8756339.3598 | 8421083.326 | 8060683.0896 | 7673252.8356 | 7256765.3125 | 6809041.2252 | 6327737.8313 | 5810336.6829 | 5254130.4483 | 4656208.7462 | 4013442.9163 | 3322469.6493 | 2579673.3872 | 1781167.4055 | 922773.4751 | -8.964e-09
|  |  | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858 | -991981.4858
|  |  | -162664.192 | 817117.4793 | 804002.6789 | 789904.2683 | 774748.477 | 758456.0014 | 740941.5901 | 722113.5979 | 701873.5063 | 680115.4078 | 656725.452 | 631581.2494

## 100% Solar Cash Flow
Cash flow | 100% Solar & Storage
Year
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Flow from operations
Revenue |  | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Fuel Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs |  | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392
EBITDA/Net cash flow from operations |  | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 21000000
Interest paid |  | -829317.2938 | -817117.4793 | -804002.6789 | -789904.2683 | -774748.477 | -758456.0014 | -740941.5901 | -722113.5979 | -701873.5063 | -680115.4078 | -656725.452 | -631581.2494 | -604551.2317 | -575493.9627 | -544257.3984 | -510678.0919 | -474580.3373 | -435775.2512 | -394059.7836 | -349215.656 | -301008.2187 | -249185.2237 | -193475.504 | -133587.5554 | -69208.0106 | -13741973.2276
Net cash flow pre |  | -364093.5329 | -351893.7185 | -338778.918 | -324680.5075 | -309524.7162 | -293232.2406 | -275717.8292 | -256889.837 | -236649.7455 | -214891.647 | -191501.6911 | -166357.4886 | -139327.4709 | -110270.2018 | -79033.6376 | -45454.3311 | -9356.5765 | 29448.5096 | 71163.9772 | 116008.1049 | 164215.5421 | 216038.5371 | 271748.2568 | 331636.2054 | 396015.7502 | 7258026.7724
Flow of Capital
Total start costs |  | -11057563.9167 | [24 empty] | -11057563.9167
Loan receipts |  | 11057563.9167 | [24 empty] | 11057563.9167
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayments of loans |  | -162664.192 | -174864.0064 | -187978.8069 | -202077.2174 | -217233.0087 | -233525.4844 | -251039.8957 | -269867.8879 | -290107.9795 | -311866.0779 | -335256.0338 | -360400.2363 | -387430.254 | -416487.5231 | -447724.0873 | -481303.3939 | -517401.1484 | -556206.2346 | -597921.7021 | -642765.8298 | -690973.267 | -742796.2621 | -798505.9817 | -858393.9304 | -922773.4751 | -11057563.9167
Net cash flow |  | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -526757.7249 | -3799537.1443
Cash Balance b/fwd |  |  | -526757.7249 | -1053515.4499 | -1580273.1748 | -2107030.8997 | -2633788.6247 | -3160546.3496 | -3687304.0746 | -4214061.7995 | -4740819.5244 | -5267577.2494 | -5794334.9743 | -6321092.6992 | -6847850.4242 | -7374608.1491 | -7901365.8741 | -8428123.599 | -8954881.3239 | -9481639.0489 | -10008396.7738 | -10535154.4987 | -11061912.2237 | -11588669.9486 | -12115427.6736 | -12642185.3985 | 0
Cash Balance c/fwd |  | -526757.7249 | -1053515.4499 | -1580273.1748 | -2107030.8997 | -2633788.6247 | -3160546.3496 | -3687304.0746 | -4214061.7995 | -4740819.5244 | -5267577.2494 | -5794334.9743 | -6321092.6992 | -6847850.4242 | -7374608.1491 | -7901365.8741 | -8428123.599 | -8954881.3239 | -9481639.0489 | -10008396.7738 | -10535154.4987 | -11061912.2237 | -11588669.9486 | -12115427.6736 | -12642185.3985 | -13168943.1234 | -3799537.1443
Debt Service Cover
Net operating income |  | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608
Debt Service |  | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858 | 991981.4858
Debt Service Cover Ratio |  | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898 | 0.46898
Inflation factors
General |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fuel |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Tariff |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 100% Solar Profit and Loss
Profit and Loss Account | 100% Solar & Storage
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | TOTAL
Revenue
Generation Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Other Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 840000 | 21000000
Operating Costs
Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Costs | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -9369405.9792
Total Operating Costs | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -374776.2392 | -9369405.9792
EBITDA | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 465223.7608 | 30369405.9792
| 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 55.38% | 144.6%
Depreciation | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -442302.5567 | -11057563.9167
EBIT | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 22921.2042 | 41426969.8958
Loan interest | -829317.2938 | -817117.4793 | -804002.6789 | -789904.2683 | -774748.477 | -758456.0014 | -740941.5901 | -722113.5979 | -701873.5063 | -680115.4078 | -656725.452 | -631581.2494 | -604551.2317 | -575493.9627 | -544257.3984 | -510678.0919 | -474580.3373 | -435775.2512 | -394059.7836 | -349215.656 | -301008.2187 | -249185.2237 | -193475.504 | -133587.5554 | -69208.0106 | -13741973.2276
Earnings Before Tax | -806396.0896 | -794196.2752 | -781081.4747 | -766983.0642 | -751827.2729 | -735534.7972 | -718020.3859 | -699192.3937 | -678952.3021 | -657194.2037 | -633804.2478 | -608660.0453 | -581630.0276 | -552572.7585 | -521336.1943 | -487756.8877 | -451659.1332 | -412854.047 | -371138.5795 | -326294.4518 | -278087.0146 | -226264.0195 | -170554.2999 | -110666.3512 | -46286.8065 | 55168943.1234
| -26.8799 | -26.4732 | -26.036 | -25.5661 | -25.0609 | -24.5178 | -23.934 | -23.3064 | -22.6317 | -21.9065 | -21.1268 | -20.2887 | -19.3877 | -18.4191 | -17.3779 | -16.2586 | -15.0553 | -13.7618 | -12.3713 | -10.8765 | -9.2696 | -7.5421 | -5.6851 | -3.6889 | -1.5429

## Distribution Scenario BoQs
|  | Replace network Like for Like |  | Replace HV Network only |  | Replace entire network with redseign |  | Build complete LV only network
Materials
Underground Cable | Price | Quantity | Total | Quantity | Total | Quantity | Total | Quantity | Total
11kV 95mm2 cable (km) | 26500 | 11 | 291500 | 11 | 291500 | 7 | 185500 |  | 0
LV cables from existing S/S positions to services (km) | 15600 | 10.5 | 163800 | 0 | 0 | 10.5 | 163800 | 22 | 343200
LV cable hubs to exisitng S/S positions (km) | 15600 | 0 | 0 | 0 | 0 | 5 | 78000 | 0 | 0
Three phase service cable (km) | 4000 | 3 | 12000 | 0 | 0 | 3 | 12000 | 3 | 12000
Single phase service cable (km) | 2000 | 12 | 24000 | 0 | 0 | 12 | 24000 | 12 | 24000
70mm Earthing cable (km) | 2000 | 15 | 30000 | 0 | 0 | 15 | 30000 | 15 | 30000
Freight | 10% | 10% | 52130 |  | 29150 |  | 49330 |  | 40920
Sub Total |  |  | 573430 | 0 | 320650 |  | 542630 |  | 450120
Substations
Ring main Units Including Generation RMUs | 15000 | 29 | 435000 | 29 | 435000 | 9 | 135000 |  | 0
315kVA pad mount transformers | 12173 | 10 | 121730 | 10 | 121730 | 6 | 73038 |  | 0
100kVA pad mount transformers | 9200 | 16 | 147200 | 16 | 147200 | 2 | 18400 |  | 0
LV pillars | 5000 | 0 | 0 | 0 | 0 | 20 | 100000 | 26 | 130000
Freight | 10% |  | 70393 |  | 70393 |  | 32643.8 |  | 13000
Sub Total |  |  | 774323 | 0 | 774323 |  | 359081.8 |  | 143000
Service Terminations
Three phase service terminations 100A | 70 | 95 | 6650 | 0 | 0 | 95 | 6650 | 95 | 6650
Single phase service terminations 100A | 65 | 401 | 26065 | 0 | 0 | 401 | 26065 | 401 | 26065
Three phase meters | 240 | 95 | 22800 | 0 | 0 | 95 | 22800 | 95 | 22800
Single phase meters | 160 | 401 | 64160 | 0 | 0 | 401 | 64160 | 401 | 64160
Single Phase Earth Leakage Trips | 100 | 401 | 40100 | 0 | 0 | 401 | 40100 | 401 | 40100
Three Phase Earth Leakage Trips | 200 | 95 | 19000 | 0 | 0 | 95 | 19000 | 95 | 19000
Freight | 10% |  | 17877.5 |  | 0 |  | 17877.5 |  | 17877.5
Sub Total |  |  | 196652.5 |  | 0 |  | 196652.5 |  | 196652.5
Misc
11kV joints (no.) | 300 | 88 | 26400 | 88 | 26400 | 30 | 9000 | 0 | 0
11kV Cable Terminations (no.) | 300 | 116 | 34800 | 116 | 34800 | 36 | 10800 | 0 | 0
LV joints (no.) | 300 | 50 | 15000 | 0 | 0 | 50 | 15000 | 50 | 15000
LV Pillar Cable terminations (no.) | 300 | 52 | 15600 | 0 | 0 | 52 | 15600 | 52 | 15600
Earth pins (no.) | 5 | 100 | 500 | 50 | 250 | 100 | 500 | 100 | 500
LV Fuses * 52 ways (no.) | 27 | 156 | 4212 | 0 | 0 | 156 | 4212 | 156 | 4212
125mm Internal/150mm Ridgiducts (units) | 40 | 1166.6667 | 46666.6667 | 1166.6667 | 46666.6667 | 1166.6667 | 46666.6667 | 0 | 0
Cable Warning Tape £20 per 365m (no.) | 20 | 55 | 1100 | 20 | 400 | 55 | 1100 | 35 | 700
Freight | 10% |  | 14427.8667 |  | 0 |  | 10287.8667 |  | 3601.2
Sub Total |  |  | 158706.5333 | 0 | 108516.6667 |  | 113166.5333 |  | 39613.2
0
Civil Works |  |  |  | 0
Bases for 11kV Switchgear | 4000 | 29 | 116000 | 29 | 116000 | 8 | 32000 | 0 | 0
Pad Mount Base | 4000 | 29 | 116000 | 29 | 116000 | 6 | 24000 | 0 | 0
LV Pillar Bases | 4000 | 0 | 0 | 0 | 0 | 20 | 80000 | 0 | 0
HV Cable laying (estimated 50m/day, 2 men +digger, island resource) | 672 | 220 | 147840 | 220 | 147840 | 140 | 94080 | 0 | 0
LV Cable laying (estimated 50m/day, 2 men +digger, island resource) | 672 | 210 | 141120 | 0 | 0 | 610 | 409920 | 440 | 295680
HV jointing | 600 | 87 | 52200 | 87 | 52200 | 59 | 35400 | 0 | 0
LV Cable routes jointing from Hubs to LV Pillars | 600 | 0 | 0 | 0 | 0 | 100 | 60000 | 0 | 0
LV Cable routes jointing from pillar to Services | 600 | 200 | 120000 | 0 | 0 | 200 | 120000 | 200 | 120000
Sub Total |  |  | 693160 | 0 | 432040 |  | 855400 |  | 415680
Project Management |  |  | 160000 | 0 | 160000 |  | 160000 |  | 150000
Total |  |  | 2556272.0333 | 0 | 1795529.6667 |  | 2226930.8333 |  | 1245065.7
Contingency | 10% |  | 255627.2033 |  | 179552.9667 |  | 222693.0833 |  | 124506.57
Complete replacement Network Costs |  |  | 2811899.2367 |  | 1975082.6333 |  | 2449623.9167 |  | 1369572.27