## Slide 1
1.5ton /18K
2ton/24K
（45*17-½*21）
2.5ton/30K
3ton/36K
4ton/48K
（49*21*21）
5ton/60K
（58*24-½*21）
Unit Dimensions

## Slide 2
Complete Product Line, High universality
Replace Market ACS with Bi Comm System | Product | 18K | 24K | 30K | 36K | 48K | 60K | Remark
 | AHU | Y | Y | Y | Y | Y | Y | Acoil Available
 | Regular SEER19 ODU | Y | Y | Y | Y | Y | Y | 
 | Hyper Heat ODU | Y | Y | Y | Y | Y | Coming Soon | 
“Y” mean new SKU
Notes: 2021.2.6：优化

## Slide 3
Dip Switch Setting
ON
1 2 3 4
ON
AHU SW1
1 2 3 4
ON
1 2 3 4
ODU SW
ON
1 2 3 4
ON
1 2 3 4
ON
1 2 3 4
ON
1 2 3 4
ON
1 2 3 4
Communication
Traditional
Factory
Default Setting
Other Brand
ODU
Other Brand
AHU
Notes: 2021.2.6：优化

## Slide 4
Remark:
T1--room temp. T2---evaporator temp.
T2B--evaporator out temp. Ts--setting temp.
T3--condenser temp. T4--outdoor temp.
T5– compressor discharge temp.
T2A and T2B –evaporator temp,control the EEV open(coil sensor)
Suction Sensor—detect the suction Sensor(Calculate the indoor demand
Pressure Sensor—Calculate the indoor demand
Ref.Temp Sensor—avoid the refrigerant heat sink have sweat issue
T1,T2
T3,T4,T5
EXV,T2A,T2B
Pressure Sensor
Suction Sensor
Ref.Temp Sensor
AHU
ODU
IDU
Replace
24V+485
*When Y1 the system default demand coil temp
should be 9C and when Y2 the demand is 5C,
Suction sensor and pressure sensor will calculate
the coil temp CT,then CT-9 or 5=▲T,when the gap
▲T is bigger the compressor will running faster or
will slowly,the heat pump mode with same logic(49C
and 53C）
*different model have different parameter
When Call Y1(stage one)
CT--Coil Temp
CTT--Coil Target Temp
▲T=CTT-CT
When Call Y2(stage two)
CT--Coil Temp
CTT--Coil Target Temp
▲t-- enhance factor
▲T=CTT-CT-▲t
▲T
Fz
Y1
Y2
▲t+Y2
Replace Market Product line
Notes: 2021.2.6：优化

## Slide 5
Complete Product Line, High universality
Electric Heater | Power of Electric Heater | 1.5ton /18K | 2ton/24K | 2.5ton/30K | 3ton/36K | 4ton/48K | 5ton/60K
 | 3KW | Y |  |  |  |  | 
 | 5KW | Y | Y | Y | Y |  | 
 | 8KW | Y | Y | Y | Y | Y | 
 | 10KW | Y | Y | Y | Y | Y | Y
 | 15KW |  | Y | Y | Y | Y | Y
 | 20KW |  |  |  | Y | Y | Y
 | 25KW |  |  |  |  |  | Y
Top Priority:When auxiliary is energize,the AHU will running with Turbo fan speed
SW4 is combination DIP Switch,just available with 1~3,the setting just available with 000/001/010/011
The relative air flow identification is below
Notes: 2021.2.6：优化

## Slide 6
This Could be The Most
Compatible AHU system
Comprehensive Business Solution
Multi Position (up\down\left\right)
High Efficient up to SEER 20
Universal Product Connection.
Aluminium Coil
Constantly Air Flow system up to 0.80 In.W.G
Adaptive Control System
Easy Maintenance
Optional Auxiliary heat kit up to 25kW

## Slide 7
Quick Check and Engineer setting Window
Disconnect or Circuit Breaker Location
Controller and Blower&Heater Access Panel
Coil Access Panel
Fitting Panel
Filter Access Panel

## Slide 8
This Could be The Most
Compatible AHU system
Comprehensive Business Solution
Multi Position (up\down\left\right)
High Efficient up to SEER 20
Constantly Air Flow system up to 0.80 In.W.G
Universal Product Connection.
Aluminium Coil
Easy Maintenance
Optional Auxiliary heat kit up to 25kW

## Slide 9
24V Thermostat running identify（Set system or single IDU with Other ODU
Mode | Priority | G | Y1 | Y/Y2 | B | W | W1 | W2 | E/AUX | DH/DS/BK | Fan speed | Display
OFF | / | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | OFF | 00
FAN | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | AUTO | 01
FAN |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 
Cool Y1 | 6 | * | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Medium | 02
Cool Y2 |  | * | * | 1 | 0 | 0 | 0 | 0 | 0 | 1 | High | 03
Dehumidify 1 |  | * | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 04
Dehumidify 2 |  | * | * | 1 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 05
Heat Pump 1 | 5 | * | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | Medium | 06
Heat Pump 2 |  | * | * | 1 | 1 | 0 | 0 | 0 | 0 | 1 | High | 07
Heat W |  | * | * | * | * | 1 | 0 | 0 | 0 | 1 | High | 
Heater W1 | 3 | * | 0 | 0 | 0 | 0 | 1 | 0 | 0 | * | Turbo | 08
Heater W2 |  | * | 0 | 0 | 0 | 0 | 0 | 1 | 0 | * | Turbo | 
Heater W1+W2 |  | * | 0 | 0 | 0 | 0 | 1 | 1 | 0 | * | Turbo | 09
Heat Pump1 +W1 | 4 | * | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | Turbo | 10
Heat Pump1+W2 |  | * | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | Turbo | 
Heat Pump2 +W1 |  | * | * | 1 | 1 | 0 | 1 | 0 | 0 | 1 | Turbo | 
Heat Pump W +W1 |  | * | * | * | * | 1 | 1 | 0 | 0 | 1 | Turbo | 
Heat Pump2 +W2 |  | * | * | 1 | 1 | 0 | 0 | 1 | 0 | 1 | Turbo | 
Heat Pump W +W2 |  | * | * | * | * | 1 | 0 | 1 | 0 | 1 | Turbo | 
Heat Pump 1 +W1+W2 |  | * | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | Turbo | 11
Heat Pump 2 +W1+W2 |  | * | * | 1 | 1 | 0 | 1 | 1 | 0 | 1 | Turbo | 
Heat Pump W +W1+W2 |  | * | * | * | * | 1 | 1 | 1 | 0 | 1 | Turbo | 
AUX | 1 | * | * | * | * | * | * | * | 1 | * | Turbo | 12
Heating Zone Control | 2 | * | 1 | 0 | 1 | 0 | * | * | 0 | 0 | Low | 13
Heating Zone Control |  | * | * | 1 | 1 | 0 | * | * | 0 | 0 | Low | 
Heating Zone Control |  | * | * | * | * | 1 | * | * | 0 | 0 | low | 

## Slide 10
AHU 485 +24V Connect Guide
485
24V
L1
L2
S1
S2
CN7
CN13
CN14
X.Y.E
CN2
Power
To Midea Unit IDU 18K~60K AHU
No polarity 2 wires of Wire controller
WiFi port(connect smart port)
reserve with 4 wires wire controller
Central Control/BACnet(controller from third party)
Remote Control(default with jumper shorten)—output
To Midea’s ODU
Midea supply
L1
L2
R
C
L
G
Y1
Y/Y2
B
W
W1
W2
E/AUX
DH
Power
24 V HOT
24 V COMM
ODU Malfunction Indicator
(out put to Thermostat or identification )
Fan
HEAT/COOL STAGE 1
HEAT/COOL STAGE 2(High Demand)
Change 4 ways valve energized in heating
Heat pump
Heater Group 1
Heater Group 2
Auxiliary heater
Dehumidify(Low Frequency and Low Fan)
Universal Product Connection

## Slide 11
SW1
SW2
SW3
SW4
Check
Button
Display
Tube
485/Not Polarity
Wire Controller
Infrared
Receiver
IDU+ODU
Connect Port
WiFi Port
Group Control Port
S1,S2 Group ENC1
Control Address
S3 operate
Limit temp.ENC2
24V
Power
Remote
Control
S4
24V thermostat
Connection
Funcational Board Guide
Universal Product Connection

## Slide 12
CN 34
UV LED(Output)
CN9 To
Functional
Board
CN29 T2
CN23
WORK
To terminal
block
Fan
Motor
Grounded
Power to
Transformer
CN12
Heater
CN15
CN34
CN 20
S1&S2
to ODU
CN6 T2B
CN46 T1
CN33
ALARM
CN5
Water (input)
CN21
EXV
CN10
To IDU
ENC1
Universal Product Connection
Main Board Guide
WORK(dry contactor)—when unit is work the 2 pins energize,when unit have error or protection,2 pins disconnect
ALARM(dry contactor) )—when unit is work the 2 pins disconnect,when unit have error or protection,2 pins energize
Water (input)when need use this,take off the
J1 (jumper) ,then connect to water switch,the 2 pins not connect the units will stop running
jumper
24VAC for UVLED,when fan is running,will
Output 24V signal

## Slide 13
Heat
Pump +
Heater
Heat
Pump
Only
Heater
Only
24V Thermostat
AUX
W or
Y1+B or Y/Y2+B
Based on HP
W1-Heater Stage 1st
W2-Heater Stage 2nd
Heat Control Solution 1#
HP n/a
HP n/a
AHU Heat Function Guide
Thermostat control the AHU just running with Auto fan speed(based on the setting temp and the ambient temp to adjust fan speed)
Universal Product Connection

## Slide 14
Heat
Pump +
Heater
Heat
Pump
Only
Heater
Only
24V Thermostat
AUX
W or
Y1+B or Y/Y2+B
Based on HP
W1-Heater Stage 1st
W2-Heater Stage 2nd
Heat Control Solution 1#
HP n/a
HP n/a
AHU Heat Function Guide
When use the thermostat all of action based on the thermostat output directly,not delay (expect for W1 and W2 have 30 second different when have signal together)
Universal Product Connection

## Slide 15
SW2-1:off is 2℃ gap; on is 1 ℃
SW2-2:off is 2.5℃ gap; on is not delay
SW2-3:off is delay 15’; on is 30’
Heat
Pump +
Heater
Heat
Pump
Only
Heater
Only
Midea’s Wire Controller
AUX
Heat Control Solution 2#
HP n/a
HP n/a
AHU Heat Function Guide
When Coil temp reach to 54℃ the electrical heater will shut off immediately in Heat model (Heat Pump +Heater) and just running with heat pump
Midea Wired Controller available set
Auto\Turbo\Medium\Low Fan speed
Universal Product Connection

## Slide 16
Multi Control Ways
Compatible with Midea wireless remote controller, programmable wired controller, central controller,
Wi-Fi controller, Remote On/Off.
Remote Control
Wired Control
Avoid mislaying
Central Control
Professional for commercial user
Remote On/Off
Easy for commercial users
Wi-Fi Control
Operates your AC wherever you are
24V Thermostat Control
Compatible for common 24V thermostat controller

## Slide 17
Midea Wired Controller
Two options :
Current 120G 485 control wired controller：
New 2-wired non-polarity control 120X wired controller
 | 485 control | 2-wired non-polarity
Weekly Timer | Yes | Yes
Follow-Me | Yes | Yes
Remote Control Compatible | No | Yes
Dual Control | No | Yes
Group Control | No | Yes
Rotation & Back-up | No | Yes
Ducted/Cassette/Ceiling floor compatible | Yes | No
Midea Wired Controller available set Auto\Turbo\Medium\Low Fan speed
Benefit with Midea wire controller
Available to adjust fan speed(Low,Med,High,Turbo,Auto)
2 wire controller control one system(First floor and second Floor)
Remote control the wire controller
Display the ERROR code on screen
Comfort and Energy saving adjust
Wire controller with WiFi dongle(coming soon)

## Slide 18
All DIP SWITCH default setting is OFF(except for S4)
SW1-1 | Communication solution （IDU controller select）
 | OFF not for 24V(it is 485)
 | ON for 24V comm.
SW1-2 | Anti cold setting(T2 to control fan start running) （BI controller work）
 | OFF for anti cold(Fan stop)
 | ON for not anti cold(fan not stop)
SW1-3 | Function setting（Set system and single IDU work）
 | OFF for HP
 | ON for Cooling Only
SW1-4 | Installation Request
 | OFF for Midea set system
 | ON for pair with third party ODU
Function setting
AHU DIP SWITCH Guide
SW1-1 setting mean we just available choose one communication even IDU and ODU from Midea,
If IDU or ODU not come from Midea have to use the 24V control
485 just available control with Midea’s wire controller /WiFi/Remote
24V just available control with 24V thermostat(not communication solution)

## Slide 19
SW2-1 | For W1 turn on condition(W1 and W2 have 30” delay even set not temp.delay)
 | OFF is 2℃ gap(setting temp and ambient temp)
 | ON is 1 ℃
SW2-2 | For W1 turn on condition(SW2-2 with ON then will delay with 2.5℃ and SW2-1 not available, SW3-3 decide 15’ or 30’, SW2-2 with OFF then will SW2-1 avaiable and SW3-3 not available）
 | OFF is not delay （when SW2-2 is OFF,the SW2-1 will be available or will use 2.5 ℃)
 | ON is 2.5℃ gap(setting temp and ambient temp)
SW2-3 | For energy saving(operate with heat pump priority,even have request with W1,when temp.not reach set point,the heater delay energize
 | OFF is delay 15’
 | ON is 30’
S3 | It is 16 digitals for Temp.protection -20 to 8 ℃,1 digital 2 ℃,work with SW2-4, Select 0 mean not temp limit for heater or compressor,1-F mean the temp from -20 to 8℃
Heater Mode Setting
Heat Source Limit Select(just for heater or compressor)
AHU DIP SWITCH Guide
All DIP SWITCH default setting is OFF
Here just for 485 communication(with
Midea’s wire controller)
SW2-4 | For energy saving or some code request OFF is for heater energize highest limit Temp.(need to set ENC2) ON is for the compressor energize lowest limit Temp.(need to set ENC2)
Note: When E/AUX controls electric heating, there is no temperature difference, and it starts directly

## Slide 20
SW3-1 | Increase or decrease 1 ℃ for temp.not satisfy when Heat or Cool （Just for 24V thermostat,when indoor unit and outdoor unit from Midea）
 | OFF for 1.5 hours
 | ON for 0.5 hour
SW3-2 | Adjust the set Y/Y2 Temp
 | OFF for 2 ℃
 | ON for 1 ℃
SW3-3 | Adjust the set W2 Temp
 | OFF for 3 ℃
 | ON for 2 ℃
AHU DIP SWITCH Guide
All DIP SWITCH default setting is OFF
Here just for 485 communication(with
Midea’s wire controller)
S4-1 | Default ON
 | OFF for 2 ℃
 | ON for 1 ℃
S4-2 | Default ON
 | OFF for DH is off by default
 | ON for DH on

## Slide 21
display CS is success display CF is fault | F1 | Auto restart
 |  | OFF for available
 |  | ON is not available
 | F2 | Heat compensation
 |  | Heat compensation -6℃~6℃,default is 0
 | F3 | Anti-cold setting(T2 trige
 |  | 1 for intelligent anti-cold setting (17℃~21℃)
 |  | 2 for normal anti cold fan stop temp(8℃~28℃)
 | F4 | Fan motor running when temp satisfy(1~4)
 |  | 1 for stop
 |  | 2 for lowest fan speed
 |  | 3 running setting fan speed（factory default setting)
 |  | 4 for termal mode
 | F7 | Cooling compensation
 |  | Cooling compensation -2℃~2℃,default is 0
Remote
setting with
engineering
Mode
AHU DIP SWITCH Guide
All DIP SWITCH default setting is OFF
Here just for 485 communication(with
Midea’s wire controller),all engineer
Mode just available for set system,but inquiry function is available for set system and single indoor unit
Central Control Address | S2 is 16 digital
 | S1 have 2,total S1 and S2 available for Max. 64 units
ENC1 | Capacity identification adjustment

## Slide 22
This Could be The Most
Compatible system
Comprehensive Business Solution
Normal and Hyper 2 Optional
Universal Product Connection.
Adaptive Control System
Easy Maintenance

## Slide 23
ODU 485 + 24V Connect Guide
Power
L1
L2
S1
S2
L1
L2
R
C
Y1
Y2
B
W
D
L
To Midea Unit IDU
AHU /18K~60K
Power
24 V HOT
24 V COMM
HEAT/COOL STAGE 1
HEAT/COOL STAGE 2(High Demand)
Changeover valve energized in heating
Heat pump
Defrost（out put , back to AHU/Furnace）
ODU Malfunction Indicator
(out put to Thermostat or identification )
Thermostat
Thermostat
or IDU
485
24V

## Slide 24
ODU Connect Guide
Check Button
Display Tube
Power Terminal
Communication Terminal
DIP SWITCH
SW-1 | Reserve
SW-2 | ON for 24V communication protocol and OFF for 485 communication protocol
SW-3 | ON for activing with enhance cool/heat,off for not activing enhance cool/heat
SW-4 | Reserve
Dip switch

## Slide 25
Accessory
Product line | Capacity | Model | Flare and Welding pipe | 
24V+485 AHU | 18K | MVC-18HWFN1-M | 3/4" size 15123000012887 | 3/8" size 15123000012948
 | 24K | MVC-24HWFN1-M |  | 
 | 30K | MVC-30HWFN1-M |  | 
 | 36K | MVC-36HWFN1-M |  | 
 | 48K | MVC-48HWFN1-M |  | 
 | 60K | MVC-60HWFN1-M | 7/8"size 15123100000608 | 
Product line | Capacity | Model | Flare and Welding pipe | 
24V+485 Regular ODU | 18K | MOX330U-18HFN1-MR0 | flare 5/8' to welding 3/4' 15123000013007 | 3/8" size 15123000012948
 | 24K | MOX430U-24HFN1-MR0 |  | 
 | 30K | MOD30U-30HFN1-MR0 | 3/4" size 15123000012887 | 
 | 36K | MOD30U-36HFN1-MR0 |  | 
 | 48K | MOE30U-48HFN1-MR0 |  | 
 | 60K | MOE30U-60HFN1-MR0 | 7/8"size 15123100000608 | 
24V+485 Hyper ODU | 18K | MOX430U-18HFN1-M | flare 5/8' to welding 3/4' 15123000013007 | 3/8" size 15123000012948
 | 24K | MOD30-24HFN1-MW |  | 
 | 30K | MOD30U-30HFN1-MR0(X) | 3/4" size 15123000012887 | 
 | 36K | MOE31U-36HFN1-M |  | 
 | 48K | MOE30U-48HFN1-M-[X1] |  | 
Notes: 2021.2.6：优化

## Slide 26
AHU Function Connection
Input
Dry Contact
Dry Contact

## Slide 27
AHU Function Connection
1.If we use the Y/Y2 (state 2) then the unit will concern the demand is big,so the fan motor will running with high fan
2.Request a connection diagram for different scenario
3.Ask if we have manual button for checking the 4 ways valve,we don‘t have this manual button，but we can use the 24V signal to check,connection terminal B
4.How to access into the engineer mode,please check the attached of file(just have the function that we show in the PPT,the other function not available still)
5.For heat pump it is available with Turbo fan speed with Midea’s wire controller
6.When auxiliary is energize,the AHU will running with Turbo fan speed
7.The Auxiliary turbo fan speed available adjust (4 speeds optional)
8.Two water base pan have 2 drain pipe connections,both available for normal drain water,the higher one
Also available for water most of the time
9.When call DH（the dehumidify function),the unit will running with low frequency and low fan,we can use in zone control,but we need to concern that the output is low,we suggest use the return duct bypass the air low,the capacity output is around 30%

## Slide 28
AHU Function Connection
10.When we want to set the DIP SWITCH,we have to power off then after we already done the setting,then
power on，because the setting just keep the setting after power on