## AHU
Series |  |  | Regular | Regular | Regular | Regular
|  |  | 24K | 36K | 48K | 60K
Factory Code |  |  | 22023110000427 | 22023110000428 | 22023110000449 | 22023110000429
Factory Indoor code |  |  | 22023111000250 | 22023111000251 | 22023111000272 | 22023111000252
Factory outdoor code |  |  | 22023116000081 | 22023116000082 | 22023116000103 | 22023116000083
Journey Indoor unit model |  |  | RGV18AHU24 | RGV18AHU36 | RGV18AHU48 | RGV18AHU60
Journey Outdoor unit model |  |  | RGV18ODU24 | RGV18ODU36 | RGV18ODU48 | RGV18ODU60
Customer Indoor unit model |  |  | RGV18AHU24 | RGV18AHU36 | RGV18AHU48 | RGV18AHU60
Customer Outdoor unit model |  |  | RGV18ODU24 | RGV18ODU36 | RGV18ODU48 | RGV18ODU60
Power supply | Rated | V, Ph, Hz | 208/230, 1, 60 | 208/230, 1, 60 | 208/230, 1, 60 | 208/230, 1, 60
| Voltage range | V | 187-253 | 187-253 | 187-253 | 187-253
Cooling | Rated Capacity (range) | Btu/h | 24000(7500~26000) | 36000(7700~38900) | 47000(10500~48000) | 57000(4395~60200)
| Input power | W | 2120 | 3750 | 5046 | 5644
| Rated current | A | 9.7 | 15.82 | 21.9 | 23.8
| EER | Btu/w | 11.3 | 10.4 | 9.3 | 10.3
| SEER | Btu/w | 19.4 | 18 | 17.3 | 18
Heating at 47℉ | Rated Capacity (range) | Btu/h | 26000(5600~30000) | 36000(6000~36400) | 55000(11700~57000) | 60000(11400~63100)
| Input power | W | 2150 | 3496 | 5373 | 4959
| Rated current | A | 9.8 | 16.12 | 23.3 | 20.9
| COP | W/W | 3.54 | 3.02 | 3.00 | 3.55
| HSPF4 | Btu/w | 11.3 | 9.1 | 10 | 9.2
| HSPF5 | Btu/w | 9.2 | 7.1 | 8.2 | 7.6
Heating at 5℉ (-15℃) | Capacity | Btu/h | 17000 | 18600 | 27000 | 29000
| COP | W/W | 1.75 | 1.80 | 1.75 | 1.80
The Rated Input Current of The Power Conversion Equipment |  | A | 3 | 3.5 | 3.5 | 5
MINIMUM CIRCUIT AMPACITY (Indoor unit) |  | A | 4 | 4.5 | 4.5 | 7
MAX. FUSE (Indoor unit) |  | A | 15 | 15 | 15 | 15
Indoor fan motor | Model |  | ZKFD-250-8-1 | ZKFD-375-8-1 | ZKFD-560-8-1 | ZKFD-750-8-1
| Qty. |  | 1 | 1 | 1 | 1
| Input power | W | 67.8 | 168 | 235 | 286.5
| Output power | W | 250 | 375 | 560 | 750
|  | HP | 1/3 | 1/2 | 3/4 | 1
| Fan motor load current (RLA) | A | - | - | - | -
| Speed(Hi/Mi/Lo) | r/min | - | - | - | -
Indoor air flow (Hi/Mi/Lo) |  | m3/h | 1290/1180/1070 | 1840/1650/1470 | 2180/1860/1540 | 2690/2310/1930
Indoor air flow (Hi/Mi/Lo) |  | CFM | 758.82/694.12/629.41 | 1082.35/970.59/864.71 | 1282.35/1094.12/905.88 | 1582.35/1358.82/1135.29
Indoor noise level (Hi/Mi/Lo) |  | dB(A) | 43/40.5/35 | 46.8/44/41.3 | 53/50/46 | 52.5/49/44
Eeternal Static Pressure (ESP) | Rated | Pa | 25 | 37 | 50 | 50
|  | In. wc. | 0.1 | 0.15 | 0.2 | 0.2
| Range | Pa | 0-200 | 0-200 | 0-200 | 0-200
| Range | In. wc. | 0-0.8 | 0-0.8 | 0-0.8 | 0-0.8
Throttle type |  |  | EEV for Cooling | EEV for Cooling | EEV for Cooling | EEV for Cooling
Evaporator | Number of rows | / | 3 | 3 | 3 | 3
| Tube outside dia | mm | Φ7 | Φ7 | Φ7 | Φ7
| Tube outside type | / | Inner groove tube | Inner groove tube | Inner groove tube | Inner groove tube
| Tube pitch(a)x row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37 | 21x13.37
| Fin spacing | mm | 1.6 | 1.6 | 1.6 | 1.3
| Fin type (code) | / | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum
| Coil length x height x width | mm | 415*426*53.48*2 | 415*426*53.48*2 | 415*426*53.48*2 | 415*336*40.11
| Number of circuits | / | 4 | 4 | 4 | 3
Indoor unit | Dimension (W×D×H) | mm | 534x445x1143 | 534x534x1245 | 534x534x1245 | 534x622x1346
|  | inch | 21.02x17.52x45.00 | 21.02x21.02x49.02 | 21.02x21.02x49.02 | 21.02x24.49x52.99
| Packing (W×D×H) | mm | 640x530x1280 | 640x620x1380 | 640x620x1380 | 640x705x1480
|  | inch | 25.20x20.87x50.39 | 25.20x24.41x54.33 | 25.20x24.41x54.33 | 25.20x27.76x58.27
| Net/Gross weight | kg | 47.9/57.8 | 58.6/70.6 | 59.2/70.9 | 73.8/86.5
|  | lbs. | 105.60/127.43 | 129.19/155.64 | 130.51/156.31 | 162.70/190.70
Refrigerant piping | Liquid side/Gas side | mm | 9.52/15.9 | 9.52/15.9 | 9.52/15.9 | 9.52/22
|  | inch | 3/8" / 3/4" | 3/8" / 3/4" | 3/8" / 3/4" | 3/8" / 7/8"
Drainage water pipe diameter |  | inch | 3/4 | 3/4 | 3/4 | 3/4
Connection wiring |  |  | 16AWG*2 Stranded, shielded | 16AWG*2 Stranded, shielded | 16AWG*2 Stranded, shielded | 16AWG*2 Stranded, shielded
Communication protocol between IDU and ODU |  |  | RS485+24V | RS485+24V | RS485+24V | RS485+24V
Thermostat type | Wireless remote controller |  | Standard | Standard | Standard | Standard
| Wired Controller |  | n/a | n/a | n/a | n/a
| Programmable wired Controller |  | Standard | Standard | Standard | Standard
| WiFi |  | Optional | Optional | Optional | Optional
Room temperature | Cooling | ℃ | 16～32 | 16～32 | 16～32 | 16～32
|  | ℉ | 60～90 | 60～90 | 60～90 | 60～90
| Heating | ℃ | 0～30 | 0～30 | 0～30 | 0～30
|  | ℉ | 32～86 | 32～86 | 32～86 | 32～86
Application area (cooling Standard) |  | m2 | 32～47 | 48～70 | 64～94 | 76～111
|  | sq.ft | 344.44～505.90 | 516.67～753.47 | 688.89～1011.81 | 818.06～1194.79
Qty. per 20’/40’/40' HQ | Indoor unit |  | 39/82/154 | 27/57/57 | 27/57/57 | 27/54/54
Certification | Performance | AHRI | Yes | Yes | Yes | Yes
|  | E*Star | - | - | - | -
|  | NEEP | Yes | Yes | Yes | Yes
| Safety | UL | Yes | Yes | Yes | Yes
|  | ETL | - | - | - | -
|  | CSA | - | - | - | -
Note on C39: 邱珍: 1in.wg.=249.0889Pa
Note on C41: 邱珍: 1in.wg.=249.0889Pa

## AHU 24K
AHU Heat Pump System
Approval: ________________________________
Location: __________________________________ |  |  | Date: ___________________________________
Engineer: __________________________________ |  |  | Construction: _____________________________
Submitted to: _______________________________ |  |  | Unit #: __________________________________
Submitted by: _______________________________ |  |  | Drawing #: ________________________________
Reference: _________________________________
Set Code | 22023110000427
Indoor unit code | 22023111000250
Outdoor unit code | 22023116000081
Set Model
Indoor unit model | RGV18AHU24
Outdoor unit model | RGV18ODU24
Ceritified | AHRI
UL
SYSTEM PERFORMANCE DATA |  |  | INDOOR UNIT DATA
Power supply |  |  | Indoor fan motor
Normal Operational Voltage | (V, Ph, Hz) | 208/230, 1, 60 | Type |  | Centrifugal
Voltage Range | (V) | 187-253 | Model |  | ZKFD-250-8-1
|  |  | Qty |  | 1
Electrical |  |  | Input | (W) | 67.8
Minimum circuit ampacity | (A) | 19 | RLA | (A) | ---
Max.fuse | (A) | 30 | LRA | (A) | ---
Connection wiring |  | 16AWG*2 Stranded, shielded | Winding Resistance | (Ω) | ---
|  |  | Capacitor | (uF) | ---
Cooling |  |  | Speed(Hi/Mi/Lo) | (r/min) | -
Rated Capacity | (Btu/h) | 24000 | Air flow & Noise level
Capacity Range | (Btu/h) | 7500~26000 | Indoor air flow (Hi/Med/Lo) (No duct) | (CFM) | 758.82/694.12/629.41
Powrer Input | (W) | 2120 | Indoor noise level (Hi/Med/Lo) | [dB(A)] | 43/40.5/35
Rated current | (A) | 9.7 | Dehumidification | (Pint/H) | ---
SEER | (Btu/W) | 19.4 | Indoor unit
EER | (Btu/W) | 11.3 | Dimension (WxDxH) | (inch) | 21.02x17.52x45.00
Heating at 47F |  |  |  | (mm) | 534x445x1143
Rated Capacity | (Btu/h) | 26000 | Packing(WxDxH) | (inch) | 25.20x20.87x50.39
Capacity Range | (Btu/h) | 5600~30000 |  | (mm) | 640x530x1280
Powrer Input | (W) | 2150 | Net/Gross weight | (lbs.) | 47.9/57.8
Rated current | (A) | 9.8 |  | (kg) | 105.60/127.43
HSPF4 | (Btu/W) | 11.3
HSPF5 | (Btu/W) | 9.2 | OUTDOOR UNIT DATA
COP | W/W | 3.54 | Compressor
|  |  | Type |  | Twin-ROTARY
|  |  | Model |  | KTM240D57UMT
REFRIGERANT PIPE DATA |  |  | Brand |  | GMCC
Throttle type | Indoor unit | EEV for cooling | Capacity | (Btu/h) | 24686
| Outdoor unit | EEV for heating | Input | (W) | 1945
Design pressure | (PSIG) | 550/340 | Rated current (RLA) | (A) | -
Refrigerant Type | (Oz) | R410A/74.08 | Refrigerant oil/oil charge | (ml) | VG74/670
Refrigerant precharge | (ft) | 25
| (m) | 7.5 | Outdoor fan motor
Additional charge for each ft | (oz/ft) | 0.69 | Model |  | ZKFN-80-8-3
| (g/m) | 65 | Qty |  | 1
Liquid side/ Gas side | (inch) | 3/8" / 3/4" | Input | (W) | 88
| (mm) | 9.52/19 | RLA | (A) | --
Max. pipe length | (ft) | 164 | Speed | (r/min) | 810/720
| (m) | 50 | Air flow & Noise level
Max. difference in level | (ft) | 82 | Outdoor air flow (Max.) | (CFM) | 1764.71
| (m) | 25 | Outdoor noise level | [dB(A)] | 56.5
Connection method |  | Flared | Outdoor unit
|  |  | Dimension (W×D×H) | (inch) | 35.04x13.46x26.50
Indoor(cooling/ heating) | (Deg. ℉) | 60～90/32～86 |  | (mm) | 890x342x673
| (Deg. °C) | 16～32/0～30 | Packing (W×D×H) | (inch) | 39.17x15.67x29.13
Outdoor(cooling/heating) | (Deg. ℉) | 5~122/5~75 |  | (mm) | 995x398x740
| (Deg. °C) | -15～50/ -15～24 | Net/ Gross weight | (lbs.) | 102.29/109.13
Application area | (sq.ft) | 344.44～505.90 |  | (kg) | 46.4/49.5
| (m2) | 32～47
Indoor unit dimension
Outdoor unit dimension
Fan performance
SUBMITTAL DATA SHEET

## AHU 36K
AHU Heat Pump System
Approval: ________________________________
Location: __________________________________ |  |  | Date: ___________________________________
Engineer: __________________________________ |  |  | Construction: _____________________________
Submitted to: _______________________________ |  |  | Unit #: __________________________________
Submitted by: _______________________________ |  |  | Drawing #: ________________________________
Reference: _________________________________
Set Code | 22023110000428
Indoor unit code | 22023111000251
Outdoor unit code | 22023116000082
Set Model
Indoor unit model | RGV18AHU36
Outdoor unit model | RGV18ODU36
Ceritified | AHRI
UL
SYSTEM PERFORMANCE DATA |  |  | INDOOR UNIT DATA
Power supply |  |  | Indoor fan motor
Normal Operational Voltage | (V, Ph, Hz) | 208/230, 1, 60 | Type |  | Centrifugal
Voltage Range | (V) | 187-253 | Model |  | ZKFD-375-8-1
|  |  | Qty |  | 1
Electrical |  |  | Input | (W) | 168
Minimum circuit ampacity | (A) | 24 | RLA | (A) | ---
Max.fuse | (A) | 40 | LRA | (A) | ---
Connection wiring |  | 16AWG*2 Stranded, shielded | Winding Resistance | (Ω) | ---
|  |  | Capacitor | (uF) | ---
Cooling |  |  | Speed(Hi/Mi/Lo) | (r/min) | -
Rated Capacity | (Btu/h) | 36000 | Air flow & Noise level
Capacity Range | (Btu/h) | 7700~38900 | Indoor air flow (Hi/Med/Lo) (No duct) | (CFM) | 1082.35/970.59/864.71
Powrer Input | (W) | 3750 | Indoor noise level (Hi/Med/Lo) | [dB(A)] | 46.8/44/41.3
Rated current | (A) | 15.82 | Dehumidification | (Pint/H) | ---
SEER | (Btu/W) | 18 | Indoor unit
EER | (Btu/W) | 10.4 | Dimension (WxDxH) | (inch) | 21.02x21.02x49.02
Heating at 47F |  |  |  | (mm) | 534x534x1245
Rated Capacity | (Btu/h) | 36000 | Packing(WxDxH) | (inch) | 25.20x24.41x54.33
Capacity Range | (Btu/h) | 6000~36400 |  | (mm) | 640x620x1380
Powrer Input | (W) | 3496 | Net/Gross weight | (lbs.) | 58.6/70.6
Rated current | (A) | 16.12 |  | (kg) | 129.19/155.64
HSPF4 | (Btu/W) | 9.1
HSPF5 | (Btu/W) | 7.1 | OUTDOOR UNIT DATA
COP | W/W | 3.02 | Compressor
|  |  | Type |  | ROTARY
|  |  | Model |  | KTF250D22UMT
REFRIGERANT PIPE DATA |  |  | Brand |  | GMCC
Throttle type | Indoor unit | EEV for cooling | Capacity | (Btu/h) | 26084.74
| Outdoor unit | EEV for heating | Input | (W) | 2080
Design pressure | (PSIG) | 550/340 | Rated current (RLA) | (A) | -
Refrigerant Type | (Oz) | R410A/130.51 | Refrigerant oil/oil charge | (ml) | VG74/670
Refrigerant precharge | (ft) | 25
| (m) | 7.5 | Outdoor fan motor
Additional charge for each ft | (oz/ft) | 0.69 | Model |  | ZKFN-120-8-2
| (g/m) | 65 | Qty |  | 1
Liquid side/ Gas side | (inch) | 3/8" / 3/4" | Input | (W) | 150.0
| (mm) | 9.52/19 | RLA | (A) | --
Max. pipe length | (ft) | 213 | Speed | (r/min) | 1150/1050/900/850
| (m) | 65 | Air flow & Noise level
Max. difference in level | (ft) | 98 | Outdoor air flow (Max.) | (CFM) | 2235.29
| (m) | 30 | Outdoor noise level | [dB(A)] | 61
Connection method |  | Flared | Outdoor unit
|  |  | Dimension (W×D×H) | (inch) | 37.24x16.14x31.89
Indoor(cooling/ heating) | (Deg. ℉) | 60～90/32～86 |  | (mm) | 946x410x810
| (Deg. °C) | 16～32/0～30 | Packing (W×D×H) | (inch) | 42.91x19.69x34.84
Outdoor(cooling/heating) | (Deg. ℉) | 5~122/5~75 |  | (mm) | 1090x500x885
| (Deg. °C) | -15～50/ -15～24 | Net/ Gross weight | (lbs.) | 151.68/161.16
Application area | (sq.ft) | 516.67～753.47 |  | (kg) | 68.8/73.1
| (m2) | 48～70
Indoor unit dimension
Outdoor unit dimension
Fan performance
SUBMITTAL DATA SHEET

## AHU 48K
AHU Heat Pump System
Approval: ________________________________
Location: __________________________________ |  |  | Date: ___________________________________
Engineer: __________________________________ |  |  | Construction: _____________________________
Submitted to: _______________________________ |  |  | Unit #: __________________________________
Submitted by: _______________________________ |  |  | Drawing #: ________________________________
Reference: _________________________________
Set Code | 22023110000449
Indoor unit code | 22023111000272
Outdoor unit code | 22023116000103
Set Model
Indoor unit model | RGV18AHU48
Outdoor unit model | RGV18ODU48
Ceritified | AHRI
UL
SYSTEM PERFORMANCE DATA |  |  | INDOOR UNIT DATA
Power supply |  |  | Indoor fan motor
Normal Operational Voltage | (V, Ph, Hz) | 208/230, 1, 60 | Type |  | Centrifugal
Voltage Range | (V) | 187-253 | Model |  | ZKFD-560-8-1
|  |  | Qty |  | 1
Electrical |  |  | Input | (W) | 235
Minimum circuit ampacity | (A) | 34 | RLA | (A) | ---
Max.fuse | (A) | 50 | LRA | (A) | ---
Connection wiring |  | 16AWG*2 Stranded, shielded | Winding Resistance | (Ω) | ---
|  |  | Capacitor | (uF) | ---
Cooling |  |  | Speed(Hi/Mi/Lo) | (r/min) | -
Rated Capacity | (Btu/h) | 47000 | Air flow & Noise level
Capacity Range | (Btu/h) | 10500~48000 | Indoor air flow (Hi/Med/Lo) (No duct) | (CFM) | 1282.35/1094.12/905.88
Powrer Input | (W) | 5046 | Indoor noise level (Hi/Med/Lo) | [dB(A)] | 53/50/46
Rated current | (A) | 21.9 | Dehumidification | (Pint/H) | ---
SEER | (Btu/W) | 17.3 | Indoor unit
EER | (Btu/W) | 9.3 | Dimension (WxDxH) | (inch) | 21.02x21.02x49.02
Heating at 47F |  |  |  | (mm) | 534x534x1245
Rated Capacity | (Btu/h) | 55000 | Packing(WxDxH) | (inch) | 25.20x24.41x54.33
Capacity Range | (Btu/h) | 11700~57000 |  | (mm) | 640x620x1380
Powrer Input | (W) | 5373 | Net/Gross weight | (lbs.) | 59.2/70.9
Rated current | (A) | 23.3 |  | (kg) | 130.51/156.31
HSPF4 | (Btu/W) | 10
HSPF5 | (Btu/W) | 8.2 | OUTDOOR UNIT DATA
COP | W/W | 3.00 | Compressor
|  |  | Type |  | ROTARY
|  |  | Model |  | KTQ420D1UMU
REFRIGERANT PIPE DATA |  |  | Brand |  | GMCC
Throttle type | Indoor unit | EEV for cooling | Capacity | (Btu/h) | 44697
| Outdoor unit | EEV for heating | Input | (W) | 3420
Design pressure | (PSIG) | 550/340 | Rated current (RLA) | (A) | -
Refrigerant Type | (Oz) | R410A/165.79 | Refrigerant oil/oil charge | (ml) | VG74/1400
Refrigerant precharge | (ft) | 25
| (m) | 7.5 | Outdoor fan motor
Additional charge for each ft | (oz/ft) | 0.69 | Model |  | ZKFN-85-8-22-5
| (g/m) | 65 | Qty |  | 2
Liquid side/ Gas side | (inch) | 3/8" / 3/4" | Input | (W) | 126.0
| (mm) | 9.52/19 | RLA | (A) | --
Max. pipe length | (ft) | 213 | Speed | (r/min) | 850/750/650
| (m) | 65 | Air flow & Noise level
Max. difference in level | (ft) | 98 | Outdoor air flow (Max.) | (CFM) | 4500.00
| (m) | 30 | Outdoor noise level | [dB(A)] | 59
Connection method |  | Flared | Outdoor unit
|  |  | Dimension (W×D×H) | (inch) | 37.48x16.34x52.48
Indoor(cooling/ heating) | (Deg. ℉) | 60～90/32～86 |  | (mm) | 952x415x1333
| (Deg. °C) | 16～32/0～30 | Packing (W×D×H) | (inch) | 43.11x19.49x58.27
Outdoor(cooling/heating) | (Deg. ℉) | 5~122/5~75 |  | (mm) | 1095x495x1480
| (Deg. °C) | -15～50/ -15～24 | Net/ Gross weight | (lbs.) | 217.59/248.68
Application area | (sq.ft) | 688.89～1011.81 |  | (kg) | 98.7/112.8
| (m2) | 64～94
Indoor unit dimension
Outdoor unit dimension
Fan performance
SUBMITTAL DATA SHEET

## AHU 60K
AHU Heat Pump System
Approval: ________________________________
Location: __________________________________ |  |  | Date: ___________________________________
Engineer: __________________________________ |  |  | Construction: _____________________________
Submitted to: _______________________________ |  |  | Unit #: __________________________________
Submitted by: _______________________________ |  |  | Drawing #: ________________________________
Reference: _________________________________
Set Code | 22023110000429
Indoor unit code | 22023111000252
Outdoor unit code | 22023116000083
Set Model
Indoor unit model | RGV18AHU60
Outdoor unit model | RGV18ODU60
Ceritified | AHRI
UL
SYSTEM PERFORMANCE DATA |  |  | INDOOR UNIT DATA
Power supply |  |  | Indoor fan motor
Normal Operational Voltage | (V, Ph, Hz) | 208/230, 1, 60 | Type |  | Centrifugal
Voltage Range | (V) | 187-253 | Model |  | ZKFD-750-8-1
|  |  | Qty |  | 1
Electrical |  |  | Input | (W) | 286.5
Minimum circuit ampacity | (A) | 34 | RLA | (A) | ---
Max.fuse | (A) | 60 | LRA | (A) | ---
Connection wiring |  | 16AWG*2 Stranded, shielded | Winding Resistance | (Ω) | ---
|  |  | Capacitor | (uF) | ---
Cooling |  |  | Speed(Hi/Mi/Lo) | (r/min) | -
Rated Capacity | (Btu/h) | 57000 | Air flow & Noise level
Capacity Range | (Btu/h) | 4395~60200 | Indoor air flow (Hi/Med/Lo) (No duct) | (CFM) | 1582.35/1358.82/1135.29
Powrer Input | (W) | 5644 | Indoor noise level (Hi/Med/Lo) | [dB(A)] | 52.5/49/44
Rated current | (A) | 23.8 | Dehumidification | (Pint/H) | ---
SEER | (Btu/W) | 18 | Indoor unit
EER | (Btu/W) | 10.3 | Dimension (WxDxH) | (inch) | 21.02x24.49x52.99
Heating at 47F |  |  |  | (mm) | 534x622x1346
Rated Capacity | (Btu/h) | 60000 | Packing(WxDxH) | (inch) | 25.20x27.76x58.27
Capacity Range | (Btu/h) | 11400~63100 |  | (mm) | 640x705x1480
Powrer Input | (W) | 4959 | Net/Gross weight | (lbs.) | 73.8/86.5
Rated current | (A) | 20.9 |  | (kg) | 162.70/190.70
HSPF4 | (Btu/W) | 9.2
HSPF5 | (Btu/W) | 7.6 | OUTDOOR UNIT DATA
COP | W/W | 3.55 | Compressor
|  |  | Type |  | ROTARY
|  |  | Model |  | KTQ420D1UMU
REFRIGERANT PIPE DATA |  |  | Brand |  | GMCC
Throttle type | Indoor unit | EEV for cooling | Capacity | (Btu/h) | 44697
| Outdoor unit | EEV for heating | Input | (W) | 3420
Design pressure | (PSIG) | 550/340 | Rated current (RLA) | (A) | -
Refrigerant Type | (Oz) | R410A/172.84 | Refrigerant oil/oil charge | (ml) | VG74/1400
Refrigerant precharge | (ft) | 25
| (m) | 7.5 | Outdoor fan motor
Additional charge for each ft | (oz/ft) | 0.69 | Model |  | ZKFN-85-8-22-5
| (g/m) | 65 | Qty |  | 2
Liquid side/ Gas side | (inch) | 3/8" / 7/8" | Input | (W) | 126.0
| (mm) | 9.52/22 | RLA | (A) | --
Max. pipe length | (ft) | 213 | Speed | (r/min) | 900/850/650
| (m) | 65 | Air flow & Noise level
Max. difference in level | (ft) | 98 | Outdoor air flow (Max.) | (CFM) | 4411.76
| (m) | 30 | Outdoor noise level | [dB(A)] | 61
Connection method |  | Flared | Outdoor unit
|  |  | Dimension (W×D×H) | (inch) | 37.48x16.34x52.48
Indoor(cooling/ heating) | (Deg. ℉) | 60～90/32～86 |  | (mm) | 952x415x1333
| (Deg. °C) | 16～32/0～30 | Packing (W×D×H) | (inch) | 43.11x19.49x58.27
Outdoor(cooling/heating) | (Deg. ℉) | 5~122/5~75 |  | (mm) | 1095x495x1480
| (Deg. °C) | -15～50/ -15～24 | Net/ Gross weight | (lbs.) | 217.15/248.46
Application area | (sq.ft) | 818.06～1194.79 |  | (kg) | 98.5/112.7
| (m2) | 76～111
Indoor unit dimension
Outdoor unit dimension
Fan performance
SUBMITTAL DATA SHEET