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REQUEST FOR PROPOSALS (RFP)
Propane Fueling Station
Project # 2017-0041 / P17

KEY DATES
Request for Proposals Issued:			10/05/2026
Walk-Thru Visit					10/13/26 Between 1:00 PM – 3:00 PM EST
Deadline for Questions to be Submitted: 		10/15/2026 at 4:00 PM EST
Due Date for the Proposal: 				10/27/2026 at 4:00 PM EST
Project completion deadline: 			 04/01/2027



This Request for Proposal packet contains the following components:
Scope of Work…………………………………………………………   2-11
Instructions to Vendors…………………………………………………12
Proposal Submission Requirements…………………………..12-14
Cost Proposal………………………………………………………………15
Photos of the Work Area………………………………………………..16

Attachments:
Federal Contract Clauses for Construction More than $350K (Form 3163)
Davis-Bacon wages for Delta County, MI.
Third Party Contract (Form 5634)
Certification of Build America, Buy America (BABA) Compliance (Form 1083)

Delta Area Transit Authority (Hereinafter referred to as “DATA”) issues this Request for Proposals for equipment and facilities (hereinafter referred to as "the Work") to be supplied and installed by Vendor at DATA in Escanaba, Michigan location at 2901 27th Avenue N. 

The Work will generally consist of facilities for the storage and distribution of liquid propane. The Work shall generally conform to this Proposal, which was developed from information provided by DATA. Vendor’s Proposal shall be developed on a material, engineering, installation, and supervision basis, the whole to cover a completely integrated / turn-key operating unit as described herein. All equipment supplied by Vendor is to be new.

 DESIGN CONDITIONS 

The work consists of providing and installing one (1) new 18,000-gallon tank (minimum) on piers, one (1) truck unloading station, and one (1) two-hose motor fueling stations. The vendor’s scope of work does NOT include any extraordinary requirements mandated by the authorities having jurisdiction, or your insurance underwriters, such as firewalls, sprinkler systems, deluge spray systems, diking, etc. 

The Work will conform to the requirements of NFPA 58: Liquefied Petroleum Gas Code, NFPA 54: National Fuel Gas Code, NFPA 70: National Electrical Code, and the State of Michigan.

GENERAL FLOW DESCRIPTION 

Liquid Propane 
The installation provides for delivery of propane to the site by tank truck transport which can then use the unloading facility for transfer of the liquid contents for storage. 

Propane Pumping System 
For delivery of liquid propane to the filling system, Vendor will supply one (1) HD 30-35 GPM new motor-driven pump package. The pump needs to maintain the required flow while two buses are fueling, including the pressure losses through the piping, valves, filters, hoses, dispensers, and vehicle fill valves.

Package includes: 
Pump 
Motor 
Inlet strainer 
Differential bypass valve 
Appropriate fittings and valves 

The system will be designed to fuel vehicles. Filling operations will be from the propane station via the fill pumps.

GENERAL EQUIPMENT DESCRIPTION 

STORAGE TANK  –  VENDOR TO SUPPLY AND INSTALL ONE (1) NEW 18,000-GALLON  
                                        TANK. (MINIMUM VOLUME)



PNEUMATIC TANK TRIM 

One  (1)  -  Internal valve with pneumatic actuator: Vapor Transfer. 
One  (1)  -  Internal valve with pneumatic actuator: Liquid-In.
One  (1)  -   Internal Valve with pneumatic actuator: Liquid-out. 
Two  (2)  -  Relief valves with risers and rain caps. 
One  (1)  -  8” magnetic, direct reading variable liquid level gauge. 
One  (1 ) -  Rotary liquid level gauge. 
One  (1)  - Thermometer

TANK TRANSPORT UNLOADING STATION 

Vendor will provide a tank transport unloading station which shall include:

	One 
	(1) 
	Steel protective support. 

	One 
	(1) 
	1-1/4” 300# emergency shutoff valve with remote actuator, thermal link, and breakaway system: Vapor transfer. 

	One 
	(1) 
	2” 300# Ball valve: Liquid-in.

	One 
	(1) 
	2” 300# screwed flow indicator with check valve: Liquid-in.

	One 
	(1) 
	3-1/4” Acme hose connector with protective cap: Liquid-in. 

	One 
	(1) 
	1-3/4” Acme hose connector with protective cap: Vapor transfer. 

	Two 
	(2) 
	Vent valves. 



Necessary hydrostatic relief valves, pipe, and fittings to provide for the assembly of these components.
 
AUTO FUELING STATIONS 

Vendor will provide one (1) two-hose auto fueling dispenser as follows:

	One 
	(1) 
	Parafour (or equal) fuel dispenser 

	Two 
	(2) 
	Elaflex (or equal) Euro Nozzles 

	Two 
	(2) 
	Hose supports with pull-away protection 



In addition:  all valves, connectors, hoses, pipe, and fittings to assemble these components.
PROPANE DISPENSER – FUEL MANAGEMENT SYSTEM INTEGRATION
The propane dispensing system shall be fully compatible with and capable of integration into the Owner’s fuel management and/or fleet management system. The system shall provide electronic tracking and reporting of individual fueling transactions.
At a minimum, the system shall be capable of recording and associating the following information with each fueling transaction:
· Vehicle number or fleet identification number.
· Driver name and/or driver identification number.
· Date and time of fueling.
· Gallons of propane dispensed.
· Fueling location and dispenser identification.
· Vehicle and/or equipment identification.
· Total transaction amount, when applicable.
Must have the capabilities to program it to collect or record other information such odometer, engine hours, etc.
The dispenser and fuel management system shall provide the capability to restrict or authorize fueling based on vehicle and/or driver identification. The system shall maintain an electronic record of each transaction and provide reporting capabilities for management, accounting, fuel usage, and fleet monitoring.
The proposed system shall not require the Agency to pay annual, monthly, or other recurring fees, subscriptions, licensing charges, or service-contract fees in order to maintain basic system functionality and operation.
The Vendor shall be responsible for configuring and testing the complete system to ensure that fueling transactions are accurately captured and transmitted to the fuel management system. All required programming, setup, integration, and commissioning shall be included in the Vendor’s proposal.
The completed system shall be demonstrated to the Owner prior to final acceptance. The Vendor shall provide training to designated Owner personnel on the operation, transaction reporting, user administration, and maintenance of the system. The Vendor and DATA, or its designated representative, shall jointly sign off on the pressure test confirming that the system has maintained the required pressure for the specified test period. The Vendor shall be responsible for correcting, at no additional cost to DATA, any leaks identified following the pressure test that are attributable to the Vendor’s installation, workmanship, or supplied equipment during the applicable warranty period.  
The Vendor shall provide on-demand technical support to designated Owner personnel at no additional cost for the duration of the applicable warranty period following final acceptance of the system. Technical support may be provided by telephone, email, remote/digital access, or in-person service when reasonably necessary. Support shall include assistance with system operation, transaction reporting, user administration, troubleshooting, and routine maintenance.
The Vendor shall provide a designated technical support contact and procedures for requesting assistance. Technical support related to defects, malfunctions, or other issues attributable to Vendor-supplied equipment, software, installation, or workmanship shall be provided at no additional cost to DATA during the applicable warranty period.
 EMERGENCY SHUTDOWN SYSTEM 

Vendor will furnish and install an emergency shutdown system to close all pneumatic valves at the storage tank and truck unloading station. The system will be operated by a self-contained nitrogen system. Vendor will provide the required initial nitrogen. The system must be manually actuated at a remote emergency shutoff device located in accordance with NFPA 58.

LIQUID PROPANE PUMP PACKAGE 

For delivery of liquid propane to the dispensers, Vendor will supply and install (1) - one new motor-driven pump package. The pump will be installed on the concrete fuel island. 




The equipment will generally include:

	One
	(1) 
	Liquid propane pump Blackmer (or equal), complete with Class 1, Group 2, 7.5-10HP/3 PH motor. 

	One 
	(1) 
	Bypass control valve. 

	One 
	(1) 
	300# strainer with 40 mesh basket (pump inlet). 

	Two
	(2) 
	300# valves (pump inlet and outlet) 




And all interconnecting piping, fittings, and hydrostatic relief valves to make a complete package. 

INSTALLATION
 
· Furnish all labor, materials, equipment, and supervision necessary for complete installation. 
· Install propane tanks, pumps, dispensers, piping, electrical systems, controls, and related equipment. 
· Coordinate installation with all trades and approved project drawings. 
· Follow manufacturer installation requirements and applicable Michigan, NFPA, OSHA, and local codes. 
· Properly install and connect all utilities, controls, grounding, and safety systems. 
· Provide required foundations, pads, fencing, guard posts, gravel, drainage, and site improvements. 
· Protect existing facilities and utilities during construction. 
· Perform required testing, inspections, startup, and commissioning. 
· Correct deficiencies identified during inspections or testing. 
· Provide operating manuals, warranties, certifications, and as-built drawings. 
· Clean the site and remove construction debris. 
· Provide final demonstration to the Owner and obtain required approvals before final acceptance.

DRAWINGS 

Vendor will provide engineering, design specifications and drawings necessary for execution of the Work. 
The actual installation and engineering details may vary from this Proposal, subject to written approval by 
DATA. The installed system will conform to approved engineering drawings. 

PROFESSIONAL ENGINEER STAMP 

When required by Vendor, or by state or local authorities for permitting purposes, Vendor will have required drawings prepared, reviewed, and stamped by a Professional Engineer. 

PERMITS 

Vendor will obtain permits required for trade work, such as plumbing and electrical, to be performed by Vendor on the project. 

Vendor is responsible for obtaining all required use permits for the facility, including building, zoning, environmental, others needed for approval of the site for the system at the Vendors expense, all applicable 
permits and licenses. 




FOUNDATIONS

Vendor shall:
· Furnish and install engineered concrete foundation pads and piers for propane tanks and fueling equipment. 
· Excavate, prepare, and compact subgrade as required. 
· Provide reinforcing steel and concrete as specified by the structural plans. 
· Design foundations for equipment weight, vehicle loads, wind, snow, and site/soil conditions. 
· Provide anchor bolts, embedded items, and equipment connections. 
· Coordinate dimensions and anchor locations with equipment manufacturers. 
· Foundations shall be level, properly finished, and adequately cured before equipment installation. 
· Provide required inspections and testing. 
· Restore surrounding areas after construction. 
· Final foundation dimensions and reinforcement shall be based on the approved engineering drawings and manufacturer's equipment requirements.

EQUIPMENT SETTING 

Vendor will furnish crane and other equipment required to transport and set the tank and the concrete foundations. Vendor shall be responsible for setting the tank. 

INTERCONNECTING PIPING (ABOVE GROUND) 

Vendor will supply and install all pipes and fittings to manifold the tank and connect from the unloading station to the tank as specified below: 

From Truck Unloading Station to Tank 
                                                                                        2” Liquid-in --------------------------------------------------- 30’ 
        1 ¼” Vapor transfer ------------------------------------------ 30’ 

From Tank to Fueling Dispenser  (#1)    --  1 ¼” Liquid-out ----------------------------------------------- 35’ 
From Tank to Fueling Dispenser  (#2)         --1 ¼” Liquid-out -----------------------------------------------65’

All underground piping will be coated and wrapped, cathodically protected, trenched, and backfilled with existing soil. If existing soil is deemed unsuitable for backfilling, sand or imported soil will be furnished on a time and material cost-plus basis. Liquid propane piping will be protected by hydrostatic relief valves as required. 

Piping distances are subject to final system layout. Vendor’s price should be based on the piping distances specified above. The increase in cost due to the piping distance increase will be charged, as an extra, prior
 to installing any piping. 

TESTING 

Piping will be tested using air or nitrogen at appropriate pressures for the service. Vendor and DATA or its assigned representative will both sign off on pressure test indicating that the system held the required pressure. The Vendor shall be responsible for correcting, at no additional cost to DATA, any leaks identified following the pressure test that are attributable to the Vendor’s installation, workmanship, or supplied equipment during the applicable warranty period.
ELECTRICAL APPARATUS & WIRING 

 The Vendor shall furnish all labor, supervision, materials, equipment, wiring, conduit, fittings, devices, controls, testing, permits, inspections, and incidental work necessary to provide a complete and operational electrical system for the propane fueling facility.

The Vendor shall coordinate all electrical work with the propane equipment manufacturer, civil contractor, structural contractor, fueling-system contractor, Owner, and Engineer.

All electrical work shall comply with the latest editions legally adopted and applicable to the project, including:
· Michigan Electrical Code.
· 2023 National Electrical Code (NFPA 70), as adopted and amended by the State of Michigan.
· NFPA 58, Liquefied Petroleum Gas Code.
· Applicable requirements of NFPA 30A where applicable.
· Applicable OSHA requirements.
· Local electrical and building authority requirements.
· Requirements of the serving electrical utility.
· Manufacturer's installation requirements.
· All applicable federal, state, and local codes and regulations.
CONCRETE/TRENCHING 
The Vendor is responsible for providing:
· Site excavation, grading, and preparation. 
· Trenching for electrical, propane, communications, and drainage. 
· Proper bedding, backfill, and compaction. 
· Reinforced concrete fueling pad. 
· Concrete foundations for propane tank, pump, and dispenser. 
· Equipment pads and protective bollards. 
· Proper site drainage. 
· Concrete designed for transit-bus and service-vehicle loads. 
· Utility locating and protection. 
· Required inspections and compaction testing. 
· Restoration of asphalt, concrete, gravel, and landscaping. 
· Final as-built drawings showing underground utilities and foundations. 
· All work must comply with Michigan codes, OSHA, applicable NFPA
 	   requirements, and project engineering drawings 

PAINTING 

Equipment to be fabricated and supplied by Vendor will be painted with primer and finish coat before or after shipment. Vendor shall be responsible for painting the entire project. Finish coat to be a standard grayscale color approved by DATA. 


FENCING/GRAVEL 
 The Vendor shall furnish and install all fencing, gates, posts, hardware, gravel, aggregate base, grading, compaction, and related work required for the propane fueling facility.
The Vendor shall provide plans identifying the proposed fencing layout and shall submit those plans to DATA for review and written approval prior to installation. Fencing shall be installed in accordance with the approved Vendor-prepared plans and shall provide secure protection around the propane equipment and fueling area. Fence materials shall be corrosion-resistant and suitable for outdoor exposure. Lockable vehicle and maintenance gates shall be provided by the Vendor as required.
Fence locations shall be coordinated with propane tank, fueling equipment, electrical equipment, required clearances, emergency access, and maintenance access.
The Vendor shall determine the required gravel thickness, aggregate material, grading, and compaction requirements based on site conditions and applicable design standards and shall include these details in the plans submitted by the Vendor for DATA’s review and approval. Gravel areas shall be properly graded and compacted and shall provide a stable surface for vehicles and equipment. Gravel surfaces shall be graded to provide positive drainage and prevent standing water.
The Vendor shall maintain required access for fueling operations, maintenance, emergency vehicles, and snow removal.
All disturbed areas shall be restored upon completion. Final fencing and gravel installation shall be secure, properly graded, compacted, and free of hazards.
PROPANE FUELING & CANOPY INSTALLATION
· Furnish and install a complete engineered canopy over the propane fueling area. 
· Canopy will completely cover the propane transfer area while maintaining all required clearances.  
· Minimum dimensions shall be:   Width -30 ft – Length – 40 ft – clear height – 16 ft.
· Provide structural steel framing, roof system, columns, foundations, and required connections. 
· Design for local snow, wind, ice, and weather loads. 
· Coordinate canopy dimensions and location with propane tanks, dispensers, vehicles, and required clearances. 
· Provide proper drainage, gutters, and downspouts where required. 
· Provide canopy lighting and electrical connections as specified. Lighting shall incorporate both motion-sensor activation and dusk-to-dawn operation. Fixtures shall automatically operate from dusk to dawn as required for security and general site illumination, with motion sensors providing increased illumination when personnel or vehicles are detected. 
· Coordinate all electrical work with the hazardous/classified-area requirements. 
· Protect propane equipment and fueling operations during construction. 
· Provide corrosion-resistant exterior finishes suitable for Upper Michigan weather. 
· Obtain required permits and inspections. 
· Provide engineered drawings and manufacturer's installation information. 
· Complete final inspection, cleanup, and touch-up before acceptance.


GUARD POSTS 
The Vendor shall furnish and install heavy-duty steel guard posts/bollards to protect propane tanks, dispensers, pumps, electrical equipment, and other equipment from vehicle impact. The Vendor shall submit the proposed locations and installation detailed plan to DATA for review and approval prior to installation.
Guard posts shall be securely anchored in reinforced concrete foundations and shall be designed to withstand anticipated vehicle impact. Posts shall be corrosion-resistant and suitable for outdoor exposure.
Locations shall be coordinated with propane equipment, required safety clearances, fueling operations, maintenance access, emergency access, and snow removal.
Guard posts shall receive a durable, high-visibility safety coating or finish approved by the Owner. Damaged coatings shall be repaired prior to final acceptance.
FIRE EXTINGUISHERS & "NO SMOKING" SIGNS 

Vendor will supply (2) 20 lb. BC-rated dry chemical fire extinguishers & (4) “No Smoking” signs for the system.

OPERATION & MAINTENANCE MANUAL 

Vendor will submit to DATA, one (1) Operation and Maintenance manual, including one (1) set of drawings, vendor equipment brochures, description of system, sufficient training for employees identified by DATA of system operation, including software training, and startup & shutdown instructions, adjusting and troubleshooting procedures. Training timeline and duration to be identified once vendor selection occurs. 

FIRE SAFETY ANALYSIS 

A fire safety analysis is required by NFPA 58. Vendor will prepare a written Fire Safety Analysis for the system prior to initial operation. This analysis is to be tailored to specific needs of the system. 

ACCEPTANCE
The Work shall not be considered complete until all Work described in the Contract Documents has been completed and approved by DATA. Payment will be made after Unit is operational, passes all required inspections and tests, and has been accepted by DATA. Items identified during inspection, testing, or acceptance that are subject to correction or warranty shall be corrected by the Vendor, at no additional cost to DATA, in accordance with the applicable warranty requirements.
WARRANTY
The Vendor shall warrant all labor, materials, equipment, workmanship, and installation provided under this Contract to be free from defects and suitable for their intended purpose.
The Vendor shall provide a minimum one (1) year warranty from the date of final acceptance of the completed project, unless a longer warranty period is required by the manufacturer, plans, specifications, or Contract documents. Vendor must include detail in provided bid.
The warranty shall include, but not be limited to:
· Propane tanks and associated equipment.
· Pumps and dispensers.
· Propane piping and fittings.
· Electrical equipment and wiring.
· Fuel management and control systems.
· Concrete foundations, pads, and piers.
· Fueling canopy and structural components.
· Roofing and drainage components.
· Fencing, gates, and guard posts.
· Site improvements and related installation work.
The Vendor shall provide all manufacturer's warranties and shall assign or transfer such warranties to the Owner where permitted.
During the warranty period, the Vendor shall, at no additional cost to the Owner, repair or replace defective materials, equipment, components, or workmanship. Repairs shall include all labor, materials, transportation, removal, replacement, testing, and related costs necessary to restore the affected system to proper operating condition.
Warranty repairs shall be performed promptly after notification by the Owner. Emergency or safety-related deficiencies affecting the operation of the propane fueling facility shall receive immediate attention.
Any repaired or replaced component shall be warranted for the remainder of the original warranty period or for a minimum of one (1) year from the date of repair or replacement, whichever is longer.
The Vendor shall provide the Owner with written warranty certificates, manufacturer's warranties, operating manuals, maintenance information, and contact information for warranty service prior to final acceptance.
The warranty shall not relieve the Vendor of responsibility for defects resulting from improper installation, defective materials, failure to follow manufacturer's requirements, or failure to comply with the Contract documents.
Warranty obligations shall remain in effect not withstanding final payment or final acceptance of the project.
TERMS AND CONDITIONS 

This Proposal is subject to the following Terms and Conditions unless otherwise specified within the body of the Proposal, in which case that section or paragraph only would be superseded.

No deviations from or changes to these Terms and Conditions will be honored or recognized without prior negotiation and agreement between Vendor and the DATA. 

DATA reserves the right to award a vendor other than the lowest bidder that demonstrates the best value.




BUILD AMERICA, BUY AMERICA 
This project is subject to adhere to Build America, Buy America (BABA) requirements for all bids $500,000 and over in value. Documentation of how BABA will be monitored and reported must be included in bid, if applicable. Vendor must provide certification that all iron, steel, manufactured products, and construction materials incorporated into this project are in full compliance with the BABA requirements, which must be provided at time of each billing, using the appropriate Contractor form or the MDOT Certification of BABA Compliance form (MDOT Form 1083).
WAGE REQUIREMENTS FOR LABOR PERFORMED
This project is subject to the Davis-Bacon Act (40 U.S.C. §3141 et seq.), as applicable, and all related federal regulations.
The vendor and all subcontractors shall pay laborers and mechanics employed on the project wages and fringe benefits at rates not less than those prevailing on similar construction in the locality, as determined by the U.S. Department of Labor. Rates provided in Davis-Bacon Wages attachment.
The Vendor shall:
· Comply with all Davis-Bacon Act requirements
· Submit certified payrolls as required
· Ensure compliance by all subcontractors
Failure to comply with prevailing wage requirements may result in contract termination or other penalties as provided by law.
7. INSURANCE AND LICENSING REQUIREMENTS
Proposals must include proof of insurance to the following requirements, at a minimum. Each policy and Certificate of Insurance must be acceptable to DATA. Nothing contained in these insurance requirements is to be construed as limiting the extent of the Vendor's responsibility for payment of damages resulting from his operations under this contract. The Vendor shall maintain insurances in force at all times during the term of this agreement. All coverage shall be with insurance companies licensed and admitted to do business in the State of Michigan. All coverages shall be with insurance carriers that have a Best Company’s Insurance Reports Rating of A or A-(Excellent).
The Vendor shall be responsible for the maintaining all required licenses. Additionally, the Vendor shall comply with all Federal, State, and local ordinances, rules, and regulations in the performance of this project.
8. COMPLETION TIMELINE REQUIREMENTS
The entire project must be completed no later than April 1st, 2027 therefore, the proposer must also show capability and attest it can complete the job within that schedule.



INSTRUCTIONS TO VENDORS
PROPOSAL SUBMISSION PACKET REQUIREMENTS:
1. Company Information and Experience:
A. State the legal name under which the Vendor carries out business, the year the company was established, and the size of the company in terms of total employees and annual revenues.
B. Identify the office's location from which work described will be managed and the year that office was established if it differs from above.
C. Provide the contact information (name, title, telephone number, and email) for the Bidder’s representative submitting the proposal.
D. Documentation showing the Vendor is not debarred in SAM.gov federal system. To fulfill this requirement, submit a screenshot showing a search, or searches, for Vendor official name(s), selecting “all words” and search results that should show either (1) “No matches found” or (2) a green “Entity” indicator box at the top of the Vendor entry in SAM.gov, both of which indicates the Vendor is not on the federal debarred or suspended list.
E. Provide information for a minimum of 3 similar projects that were completed by Vendor, including associated contact information for reference checks.
2. Contract Agreement and Costs:
A. Completed Federal Contract Clauses for Construction More than $350,000 (MDOT Form 3163).
B. Completed Cost Proposal document. Must be signed in ink by the Vendor representative.
C. Review the Third-Party Contract (MDOT Form 5634), which does not need to be filled out by Vendor, but will be expected to be signed by selected Vendor at contract award.
D. Davis-Bacon Wages must be reviewed and utilized (included attachment).
E. For bids $500,000 and larger: Documentation of how Build America, Buy America (BABA) will be monitored and reported, if applicable. Included BABA attachment can be utilized for reporting, or a similar Vendor-supplied form.
3. Project timeline.
4. Warranty and ongoing support information.
5. Proof of Insurance Coverage.


PROPOSAL SUBMISSION INSTRUCTIONS AND QUESTIONS:
Proposal packets must be received by 4:00 PM EST on 10/27/26 Late submissions will not be accepted.
Vendors may email a copy of their proposal packet with the subject line PROPANE FUELING STATION to director@sctransit.org 
OR

Vendors may mail or deliver a hardcopy proposal packet in an envelope marked: PROPANE FUELING STATION to:
Delta Area Transit Authority
John Stapleton, Director
2901 27 Avenue N.
Escanaba, MI  49829


Proposals must remain valid for 120 days after the proposal’s due date.
Questions on the RFP are due by 4:00 PM EST on 10/15/26 and should be submitted to John Stapleton, Director, at director@sctransit.org with the subject line – “PROPANE FUELING STATION - Inquiry”.
DATA will compile and review all questions received from all vendors and post the responses to DATA’s website at databus.org as an RFP clarification. Written questions and responses will also be
sent to all firms that submitted an RFP or contacted DATA’s Director, John Stapleton, in writing with a question. Verbal comments, such as those via phone calls, will not be accepted and are not part of the official question and answer responses.
Proposals may be withdrawn in writing at any time prior to the due date and time. A proposal may also be withdrawn in person by a proposing firm, provided the withdrawal is made prior to the due date and time. The proposing firm must sign a receipt of withdrawal. No proposal may be withdrawn after the due date unless there is a material error in the proposal. Withdrawn proposals may be resubmitted, with or without modifications, up to the due date and time.
PROPOSAL EVALUATION:
During the evaluation process, DATA reserves the right to request additional information or clarifications from the Vendor or to allow corrections of errors or omissions. In evaluating proposals and awarding contracts, DATA will use the following evaluation criteria, in order of importance:
· Experience and qualifications (40%)
· Quality and reliability of proposed equipment (25%)
· Warranty and support services (20%)
· Price (15%). Proposed prices will be scored using the formula: lowest proposal price divided by the price of the proposal being evaluated x allotted points.
The selection panel members will include DATA’s Executive Director, Office Manager, and Operations Manager.
Any submitter falling within a competitive range as determined by the selection panel may be asked to present the submitter's abilities and qualifications to the selection panel and to answer any questions about the submitted qualifications. The original scoring of evaluation criteria may be modified based on the interview results. DATA reserves the right to award the RFP based on qualifications that provide the best value to DATA and to award a Vendor other than the lowest price proposal. The award will only be given to a responsive and responsible firm.
EVALUATION PROTESTS:

All protests shall be addressed in writing to DATA via e-mail at director@sctransit.org or mailed to 

Delta Area Transit Authority
John Stapleton, Director
2901 27 Avenue N.
          Escanaba, MI  49829

Protests about RFP specifications must be received ten (10) days before the proposal due date. Post award protests may be received no later than five (5) business days after notification to all proposers of the contract award decision. DATA will review and respond in writing within ten (10) days of receiving the protest. DATA is the final arbitrator on any question or dispute pertaining to proposals, proposal forms, and awards. This "disputes" clause does not preclude consideration of questions of law in connection with decisions provided for above; provided that nothing in this contract shall be construed as making final the decision of any administrative official, representative, or board on a question of law.

Proposal protests shall contain:
1. The name and address of the protester.
2. Identification of the project.
3. A statement of the grounds for the protest and any supporting documentation. The grounds for protest shall be fully supported to the extent feasible. Additional materials in support of an initial protest may be permitted only at the sole discretion of DATA.
4. The relief desired from DATA.
CONTRACT AWARD AND PAYMENT TERMS:
The award will be a firm-fixed-price contract with a lump sum single payment. The prime Vendor will complete the project AND submit an invoice to the Delta Area Transit Authority at 2901 27th Avenue N, Escanaba, MI  49829 to guarantee payment. No payment will be submitted to the State of Michigan for reimbursement until DATA verifies that the project meets the bid specifications and an acceptable inspection of the finished project has been completed by DATA. Upon acceptance, DATA will submit a request to the State of Michigan which will take up to thirty (30) days to be processed. No payment will be made by DATA until the reimbursement check is received from MDOT. All invoices shall be itemized.
Award, if made, will be to the responsible Vendor whose proposal is determined to be the most advantageous to DATA, considering evaluation criteria listed, and will need to be approved by the Michigan Department of Transportation. Notification letters will be sent to each Vendor who submitted a proposal.

DATA reserves the right to cancel the solicitation or reject all proposals for sound, documentable, business reasons. DATA also reserves the right to accept the proposal or any part thereof that it determines best to serve DATA’s needs and waive any informalities or irregularities in the proposals.
This RFP does not commit DATA to award a contract or to pay any costs incurred in the preparation of a proposal.

DATA is not liable for any cost incurred by any party prior to signing a contract with that party and then only upon written authorization from DATA to proceed with the project. The Michigan Department of Transportation (MDOT) must approve of the award prior to the start of the project.

The selected Vendor must comply with all applicable federal, state, and local laws, ordinances, rules, and regulations. This Agreement shall be governed by and construed in accordance with the laws of the State of Michigan. All applicable laws, ordinances, and the rules and regulations of all authorities having jurisdiction over construction of the project shall apply to the contract.

DATA is exempt from Federal, State, and local taxes. DATA will not be responsible for any taxes levied on the respondent as a result of the contract resulting from this RFP.



DELTA AREA TRANSIT AUTHORITY
Cost Proposal
Direct Any Questions and Submit To:  Delta Area Transit Authority, John Stapleton, Director at    director@sctransit.org.    

Please direct questions by 4:00 PM EST on 10/15/26   

Questions and answers will be posted at databus.org by 10/20/2026

RFP Issue Date: 10/05/2026
   
RFP Bids Due: 4:00 PM EST on 10/27/26

Once completed, the following cost table shall establish the pricing to be charged unless otherwise negotiated and agreed upon in writing.

	PROJECT TASKS
	NOT TO EXCEED COST

	MATERIALS AND SUPPLIES
	$

	INSTALLATION AND LABOR
	$

	TRAINING
	$

	OPTIONAL OR RECURRING COSTS
	$



Certification
The bid shall be firm for a minimum of 120 days from the RFP submittal deadline and signed by the following individual authorized to certify pricing and enter into agreements. The undersigned certifies that he/she offers to complete project and furnish materials in strict accordance with the requirements of this bid including the specifications and Terms and Conditions that are attached; that prices quoted are correct.


	Vendor Name: 
	

	Vendor Address: 
	

	City, State, Zip: 
	

	E-mail address:
	

	Authorized Representative Name (Print):
	

	Authorized Representative Position Title:
	

	Authorized Representative Signature:
	

	Date of Signature:
	



  
Photos of the Work Area
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