| 600 Volts or Less - Arc Flash Matrix Working on equipment: | Hard Hat | Safety Glasses | Standard Face Shield | Leather Work Gloves | CAT 2 Arc Suit* | Insulated Mat or Platform** | 2nd Man Recommened | 4’ Approach Boundary | 10’ Approach Boundary |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage less than 120v | X | X |  | X |  |  |  |  |  |
| 120v device (outlet, switch) | X | X |  | X |  |  |  |  |  |
| 120v circuit testing | X | X |  | X |  |  |  |  |  |
| 120v control equipment | X | X |  | X |  |  |  |  |  |
| 120v light Fixture | X | X |  | X |  |  |  |  |  |
| 120v “J” boxes | X | X |  | X |  |  |  |  |  |
| 208volt device | X | X | X | X |  |  |  | X |  |
| 208v disconnect less than 60A | X | X | X | X |  |  |  | X |  |
| 208v disconnect more than 60A | X | X | X | X |  |  |  | X |  |
| 208v panel less than 60A | X | X | X | X |  |  |  | X |  |
| 208v panel more than 60A | X | X | X | X |  |  |  | X |  |
| 208v panel testing | X | X | X | X |  |  |  | X |  |
| 208v control equip. less than 60A | X | X | X | X |  |  |  | X |  |
| 208v control equip. more than 60A | X | X | X | X |  |  |  | X |  |
| 208v light fixture | X | X | X | X |  |  |  | X |  |
| 208v “J” boxes | X | X | X | X |  |  |  | X |  |
| 240v or less motor control center | X | X | X | X |  |  |  | X |  |
| 240v or more motor control center |  | X |  |  | X | X |  |  | X |
| 277v device** |  | X |  |  | X | X |  |  | X |
| 277v circuit testing** |  | X |  |  | X | X |  |  | X |
| 277v control equipment** |  | X |  |  | X | X |  |  | X |
| 277v light fixture** |  | X |  |  | X | X |  |  | X |
| 277v “J” boxes** |  | X |  |  | X | X |  |  | X |
| 480v disconnect** |  | X |  |  | X | X | X |  | X |
| 480v panel work** |  | X |  |  | X | X | X |  | X |
| 480v panel testing** |  | X |  |  | X | X | X |  | X |
| 480v control equipment** |  | X |  |  | X | X | X |  | X |
| 480v light fixture** |  | X |  |  | X | X | X |  | X |
| 480v “J” boxes** |  | X |  |  | X | X | X |  | X |

Note:   	Any suspect equipment that is being worked on must be treated with caution and all protective equipment must be worn.  Required PPE is based on exposure hazard and not the primary job to be completed.

The matrix shown on the left is the minimum requirement.  Job planning, open communication and consulting between all personnel will aid in creating a atmosphere free from recognized hazards.

Long sleeve shirt or flash suit jacket required for 208 and above.

*CAT 2 Arc Suit includes:  Low voltage hard hat, 8 cal. Face shield w/safety glasses, CAT 2 FR Rated suit, hearing protection, 1000 Volt Rated Gloves.  The whole suit is required if indicated.

Transformers and Switch Gear must be reviewed on a case by case basis.  This equipment and other energized situations may have a fault to ground that exceeds 600Volts or less and the protection outlined in this matrix above may not be adequate for protection.

If you have a doubt – STAY OUT– ASK!

**NEC 430.133 Guards for Attendants.  Where live parts of motor controls operating at over 150 volts to ground are guarded against accidental contact only by location…and where adjustment or other attendance may be necessary during the operation of the apparatus, suitable insulating mats or platforms shall be provided so that the attendant cannot readily touch live parts unless standing on the mat(s) or platforms.