## Sheet1
Wire to Water Energy Calculator
REQUIRED DATA | PUMP 1 |  |  | PUMP 2
Pump Operation - Hours / Day | 8 |  |  | 8
Pump Operation - Days / Year | 365 |  |  | 365
Pump Flow - GPM | 1000 |  |  | 1000
Pump Head - Feet | 100 |  |  | 100
Pump Efficiency - % | 82% |  |  | 75%
Motor Efficiency - % | 95% |  |  | 90%
Energy Cost in $/KWH | 0.1 |  |  | 0.1
RESULTS
BHP At Design Point | 30.7958 |  |  | 33.67
Wire to Water Efficiency - % | 77.9% |  |  | 67.5%
Annual Energy Cost | 7061.3711 | 24.1828 | 27.9087 | 8149.3453
KW Per 1000 Gallons Pumped | 0.40305 | 1 | 1 | 0.46515
Cost Per 1000 Gallons Pumped | 0.040305 |  |  | 0.046515
PAYBACK
Annual Savings - $$ | 1087.9742 |  |  | Note: When comparing two pumps, place the lower
Annual Savings - % | 13.35% |  |  | efficiency pump/motor in the Pump 2 column.
Cost of Pump 1 | 7000
Cost of Pump 2 | 5000
Payback - Years | 1.8383