## SUMMARY
Monte Cristi Project
Summary
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
Fixed |  |  | Domes |  |  | Tracked
System Size | 11990 | kWp DC | System Size | 11990 | kWp DC | System Size | 11990 | kWp DC
| 9000 | kW AC |  | 9000 | kW AC |  | 9000 | kW AC
System Yield | 18296.74 | GWh per year | System Yield | 17961.02 | GWh per year | System Yield | 21294.24 | GWh per year
Capex (raw, no margin included) | 8021515.4942 |  | Capex (raw, no margin included) | 8342718.4942 |  | Capex (raw, no margin included) | 8607618.4942
| 669.0171 | /kWp |  | 695.8064 | /kWp |  | 717.8998 | /kWp
Att PPA rate of | 0.1 | /kWh | Att PPA rate of | 0.1 | /kWh | Att PPA rate of | 0.1 | /kWh
IRR 25 years | 20.9% |  | IRR 25 years | 19.68% |  | IRR 25 years | 24.36%
NPV 25 years | 12330029.7953 |  | NPV 25 years | 11854234.7957 |  | NPV 25 years | 15985468.4545
Simple Payback at | 5.6509 | years | Simple Payback at | 5.922 | years | Simple Payback at | 5.0235 | years
Block Size | 93750 | m2 | Block Size | 70000 | m2 | Block Size | 115000 | m2

## Sizing
Monte Cristi Project
Sizing
|  |  | FIXED TABLES | [8 empty] | DOME SHEDS | [8 empty] | ACTIVE TRACKERS
|  |  | Orientation parameters | [8 empty] | Orientation parameters | [8 empty] | Orientation parameters
|  |  | Field type: Fixed Tables | [8 empty] | Field type: Several orientations | [8 empty] | Field type: Trackers
|  |  | Tilt/azim = 20°/0° | [8 empty] | 2 orientations: Tilt/azim = 5°/-90°, 5°/90° | [8 empty] | Orientations: Azimut = 0°
[21 empty] | Tracking (with back-tracking) |  |  | 60 to -60 degrees
|  |  | Block Size |  | 9MW(ac) | [6 empty] | Block Size |  | 9MW(ac) | [6 empty] | Block Size |  | 9MW(ac)
[5 empty] | 12 MWp | [8 empty] | 12 MWp | [8 empty] | 12 MWp
|  |  | Fixed Field |  | Length | 375 | m |  |  |  |  | Dome Field |  | Length | 350 | m |  |  |  |  | Tracked Field |  | Length | 575 | m
[5 empty] | Width | 250 | m | [6 empty] | Width | 200 | m | [6 empty] | Width | 200 | m
[6 empty] | 93750 | m2 | [7 empty] | 70000 | m2 | [7 empty] | 115000 | m2
[5 empty] | Circumvent | 1250 | m | [6 empty] | Circumvent | 1100 | m | [6 empty] | Circumvent | 1550 | m
|  | 18296.74 | MWH/year |  | 1526 | kWh/kWp/year |  |  |  |  | 17961.02 | MWH/year |  | 1498 | kWh/kWp/year |  |  |  |  | 21294.24 | MWH/year |  | 1776 | kWh/kWp/year
[8 empty] | Perf.Ratio | 76.37 | [7 empty] | Perf.Ratio | 78.04 | [7 empty] | Perf.Ratio | 75.79
|  |  |  | Modules | 18171 | units |  | Inverters | 30 |  |  |  | Modules | 18171 | units |  | Inverters | 30 |  |  |  | Modules | 18171 | units |  | Inverters | 30
|  |  |  | Nominal Power | 11990 | kWp |  | AC Power | 9000 |  |  |  | Nominal Power | 11990 | kWp |  | AC Power | 9000 |  |  |  | Nominal Power | 11990 | kWp |  | AC Power | 9000
[8 empty] | PR | 1.33 | [7 empty] | PR | 1.33 | [7 empty] | PR | 1.33
|  |  |  | Total Size | 19 | Blocks | [5 empty] | Total Size | 25 | Blocks | [6 empty] | Total Size | 13 | Blocks
|  |  |  | Capacity | 227.981 | MWp | [5 empty] | Capacity | 299.975 | MWp | [6 empty] | Capacity | 155.987 | MWp
|  |  |  | Yield | 347.6381 | GWh/year | [5 empty] | Yield | 449.0255 | GWh/year | [6 empty] | Yield | 276.8251 | GWh/year
| Index (yield/capex) |  |  | 2.281 | [5 empty] | Index (yield/capex) |  |  | 2.1529 | [5 empty] | Index (yield/capex) |  |  | 2.4739

## Costing (Fixed)
Monte Cristi Project
FIXED DESIGN
Costing
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
[6 empty] | Subtotal | % | $/Wp | Confidence
Components | Amount | Unit | Quote/unit | Total
Solar module | [5 empty] | 3661818.9113 | 45.65% | 0.30541
Risen 660Wp | 11990 | kWp | 0.285 | 3417150 |  |  |  |  | 90%
Module amount | 18166.6667
Shipping | 30.5836 | containers | 8000 | 244668.9113 |  |  |  |  | 50%
Inverters | [5 empty] | 306650 | 3.823% | 0.025575
Huawei 300 | 30 | set | 9775 | 293250 |  |  |  |  | 75%
SmartACU2000D-D-03 | 1 | unit | 5400 | 5400
Shipping | 1 | containers | 8000 | 8000 |  |  |  |  | 50%
Transformer Packages | [5 empty] | 233000 | 2.905% | 0.019433
Jupiter 900 | 1 | unit | 200000 | 200000 |  |  |  |  | 75%
Shipping | 1 | containers | 8000 | 8000 |  |  |  |  | 50%
Installation and Commissioning |  |  |  | 25000 |  |  |  |  | 50%
Interconnection | [5 empty] | 50000 | 0.6233% | 0.0041701
TBD | 1 | set |  | 50000 |  |  |  |  | 0%
Measuring and Monitoring | [5 empty] | 5856.84 | 0.07301% | 0.00048848
RainWise PVmet 330 Complete Weather Station | 2 | set | 2928.42 | 5856.84 |  |  |  |  | 90%
Mounting System | [5 empty] | 1038797 | 12.95% | 0.086639
Grace Structures | 11990 | kWp | 0.0803 | 962797 |  |  |  |  | 90%
Grounding for structure commercial | 24 | sets | 500 | 12000 |  |  |  |  | 75%
Shipping | 8 | containers | 8000 | 64000 |  |  |  |  | 50%
Grounding & Lightning Protection | [5 empty] | 68280 | 0.8512% | 0.0056947
Grounding Pits | 30 | sets | 1000 | 30000 |  |  |  |  | 50%
Complete Masts | 30 | sets | 1276 | 38280 |  |  |  |  | 90%
Cables & Conduits | [5 empty] | 666112.7429 | 8.304% | 0.055556
DC side
1x4 mm2 (PV Cable to Combiners) | 400 | Rolls (500 mtr) | 556.336 | 222534.4 |  |  |  |  | 75%
1x6 mm2 (PV Cable to Inverter) | 400 | Rolls (500 mtr) | 673.728 | 269491.2 |  |  |  |  | 75%
AC side
NYY 4x35mm2 (Inverters to AC Combiner) | 2000 | meter | 14.7429 | 29485.7143 |  |  |  |  | 50%
NYY 4x240mm2 (AC combiner to transformer to BLPC) | 2000 | meter | 59.8007 | 119601.4286 |  |  |  |  | 50%
PVC Pipe + Fittings for Outdoor | 1 | budget | 0 | 25000 |  |  |  |  | 33%
PVC Cable duct for Indoor | 0 | budget | 0 | 0 |  |  |  |  | 50%
Switch Gear | [5 empty] | 0 | 0% | 0
11KV Switchgear Panel | 0 | budget | 15000 | 0
800V Inverter Combiner Panel | 0 | budget | 30000 | 0
DC Combiners | 0 | sets | 500 | 0 |  |  |  |  | 50%
Isolator | 0 | sets | 7500 | 0 |  |  |  |  | 90%
Installation | [5 empty] | 1400000 | 17.45% | 0.11676
Installation Contractor (to be quoted) | 1 | lumpsum | 0 | 900000 |  |  |  |  | 25%
Electrical Subcontractor | 1 | lumpsum | 0 | 500000 |  |  |  |  | 25%
Engineering and test-commissioning | [5 empty] | 75000 | 0.935% | 0.0062552
Engineering design | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Project management | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Commissioning | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Miscellaneous | [5 empty] | 516000 | 6.433% | 0.043036
Fences | 1250 | meter | 100 | 125000 |  |  |  |  | 50%
Gates | 2 | sets | 3000 | 6000 |  |  |  |  | 50%
Green Screens/planting/roadworks | 1 | budget | 100000 | 100000 |  |  |  |  | 25%
Netting | 0 | m2 | 5 | 0
CCTV | 1 | set | 50000 | 50000 |  |  |  |  | 50%
Local transportation | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Equipment transport | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Safety Equipment | 1 | budget | 10000 | 10000 |  |  |  |  | 50%
Machinery (Forklif, crane, etc) | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Insurance | 1 | set | 50000 | 25000 |  |  |  |  | 50%
Unforeseen | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Check
Total |  |  |  | 8021515.4942 |  | 8021515.4942 | 100% | 0.66902
Total/kWp |  |  | 0 | 669.0171 | /kWp
|  |  |  | 0.66902 | /Wp
| PLUS (safety margin for Financials) |  | 10% | 735.9189 | /kWp
| CAPEX |  |  | 8823667.0436

## Financials (Fixed)
Monte Cristi Project
Calculation sheet for grid-tied PV systems
FIXED DESIGN
DASHBOARD
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
Inputs
Location | [5 empty] | Outputs
Customer | [5 empty] | Internal Rate of Return (IRR) |  |  |  |  | Cost per kWh
[7 empty] | 20 years | 25 years | 30 years |  |  | 20 years | 25 years | 30 years
Technical inputs | [10 empty] | USD | 0.040898 | 0.039226 | 0.033012
Capacity | 11990 | kWp |  |  |  | After inflation | 20.54% | 20.9% | 21.03%
Produced energy (Pvsyst) | 17961.02 | MWh/year |  |  |  | After inflation and tax | 20.54% | 20.9% | 21.03%
Degradation / year | 0.4% | [9 empty] | Revenue after inflation
[6 empty] | Net Present Value (NPV) in USD x 1,000 | [5 empty] | 20 years | 25 years | 30 years
Economical inputs | [6 empty] | 20 years | 25 years | 30 years
Capex per kWp (USD) | 735.9189 | [9 empty] | USD x 1,000 | 34589.2135 | 42811.8941 | 50871.4315
[6 empty] | After inflation | 10077.4718 | 12330.0298 | 14053.2357
FIT Rate | 0.1 | US$/kWh |  |  |  | After inflation and tax | 10077.4718 | 12330.0298 | 14053.2357
MWh produced
Discount rate (for NPV) | 5% |  |  |  |  | Payback period (years) | [5 empty] | 20 years | 25 years | 30 years
Depreciation | 10 | years | [8 empty] | MWh produced | 345892.135 | 428118.9414 | 508714.3153
Depreciation method | 1 | (1 = double decling, 0 = straight line) |  |  |  | After inflation | 5.6509 | years
Corporate tax rate | 0% |  |  |  |  | After inflation and tax | 5.6509 | years
Inflation (for O&M) | 2% | per year
O&M | 3% | per year
1. O&M costs assumed at zero by using idle land or rooftop space and weekly rainfall for cleaning
2. Replacement of inverters assumed in year 12
CALCULATIONS
Cash flows
Year | Total 20 years | Total 25 years | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Electricity production (kWh) | 345892135.0322 | 428118941.3649 | 17961020 | 17889175.92 | 17817619.2163 | 17746348.7395 | 17675363.3445 | 17604661.8911 | 17534243.2436 | 17464106.2706 | 17394249.8455 | 17324672.8461 | 17255374.1547 | 17186352.6581 | 17117607.2475 | 17049136.8185 | 16980940.2712 | 16913016.5101 | 16845364.4441 | 16777982.9863 | 16710871.0544 | 16644027.5702 | 16577451.4599 | 16511141.654 | 16445097.0874 | 16379316.6991 | 16313799.4323 | 16248544.2345 | 16183550.0576 | 16118815.8574 | 16054340.5939 | 15990123.2316
O&M |  | -7941300.3393 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113
Outgoing | USD | -16793507.3716 | -8823667.0436 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -557960.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113 | -264710.0113
Income before inflation | USD | 50871431.534 | 1796102 | 1788917.592 | 1781761.9216 | 1774634.8739 | 1767536.3344 | 1760466.1891 | 1753424.3244 | 1746410.6271 | 1739424.9845 | 1732467.2846 | 1725537.4155 | 1718635.2658 | 1711760.7247 | 1704913.6818 | 1698094.0271 | 1691301.651 | 1684536.4444 | 1677798.2986 | 1671087.1054 | 1664402.757 | 1657745.146 | 1651114.1654 | 1644509.7087 | 1637931.6699 | 1631379.9432 | 1624854.4235 | 1618355.0058 | 1611881.5857 | 1605434.0594 | 1599012.3232
Inflation
Income after inflation | USD | 50871431.534 | 1796102 | 1788917.592 | 1781761.9216 | 1774634.8739 | 1767536.3344 | 1760466.1891 | 1753424.3244 | 1746410.6271 | 1739424.9845 | 1732467.2846 | 1725537.4155 | 1718635.2658 | 1711760.7247 | 1704913.6818 | 1698094.0271 | 1691301.651 | 1684536.4444 | 1677798.2986 | 1671087.1054 | 1664402.757 | 1657745.146 | 1651114.1654 | 1644509.7087 | 1637931.6699 | 1631379.9432 | 1624854.4235 | 1618355.0058 | 1611881.5857 | 1605434.0594 | 1599012.3232
Total cash flow before inflation | USD | 34077924.1624 | -7027565.0436 | 1524207.5807 | 1517051.9103 | 1509924.8626 | 1502826.3231 | 1495756.1778 | 1488714.313 | 1481700.6157 | 1474714.9732 | 1467757.2733 | 1460827.4042 | 1160675.2545 | 1447050.7134 | 1440203.6705 | 1433384.0158 | 1426591.6397 | 1419826.4331 | 1413088.2873 | 1406377.0941 | 1399692.7457 | 1393035.1347 | 1386404.1541 | 1379799.6974 | 1373221.6586 | 1366669.9319 | 1360144.4121 | 1353644.9945 | 1347171.5744 | 1340724.0481 | 1334302.3118
Total cash flow after inflation | USD | 34077924.1624 | -7027565.0436 | 1524207.5807 | 1517051.9103 | 1509924.8626 | 1502826.3231 | 1495756.1778 | 1488714.313 | 1481700.6157 | 1474714.9732 | 1467757.2733 | 1460827.4042 | 1160675.2545 | 1447050.7134 | 1440203.6705 | 1433384.0158 | 1426591.6397 | 1419826.4331 | 1413088.2873 | 1406377.0941 | 1399692.7457 | 1393035.1347 | 1386404.1541 | 1379799.6974 | 1373221.6586 | 1366669.9319 | 1360144.4121 | 1353644.9945 | 1347171.5744 | 1340724.0481 | 1334302.3118
Accumulated cash flow before inflation | USD |  | -7027565.0436 | -5503357.4629 | -3986305.5526 | -2476380.69 | -973554.3668 | 522201.811 | 2010916.124 | 3492616.7398 | 4967331.713 | 6435088.9863 | 7895916.3905 | 9056591.645 | 10503642.3584 | 11943846.029 | 13377230.0448 | 14803821.6845 | 16223648.1176 | 17636736.4049 | 19043113.499 | 20442806.2448 | 21835841.3794 | 23222245.5335 | 24602045.231 | 25975266.8896 | 27341936.8215 | 28702081.2336 | 30055726.2281 | 31402897.8025 | 32743621.8506 | 34077924.1624
Accumulated cash flow after inflation | USD |  | -7027565.0436 | -5503357.4629 | -3986305.5526 | -2476380.69 | -973554.3668 | 522201.811 | 2010916.124 | 3492616.7398 | 4967331.713 | 6435088.9863 | 7895916.3905 | 9056591.645 | 10503642.3584 | 11943846.029 | 13377230.0448 | 14803821.6845 | 16223648.1176 | 17636736.4049 | 19043113.499 | 20442806.2448 | 21835841.3794 | 23222245.5335 | 24602045.231 | 25975266.8896 | 27341936.8215 | 28702081.2336 | 30055726.2281 | 31402897.8025 | 32743621.8506 | 34077924.1624
Payback period before inflation | 5.6509 | years | 0 | 0 | 0 | 0 | 5.6509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Payback period after inflation | 5.6509 | years | 0 | 0 | 0 | 0 | 5.6509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation (straight-line) | 10 | years | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | -882366.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opening Balance |  | 8823667.0436 | 7941300.3393 | 7058933.6349 | 6176566.9305 | 5294200.2262 | 4411833.5218 | 3529466.8174 | 2647100.1131 | 1764733.4087 | 882366.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation (double declining) | 10 | years | -1764733.4087 | -1411786.727 | -1129429.3816 | -903543.5053 | -722834.8042 | -578267.8434 | -462614.2747 | -370091.4198 | -296073.1358 | -1184292.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opening Balance |  | 8823667.0436 | 7058933.6349 | 5647146.9079 | 4517717.5263 | 3614174.0211 | 2891339.2169 | 2313071.3735 | 1850457.0988 | 1480365.679 | 1184292.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes paid on cost saving | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes saved on depreciation (straight line) | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes saved on depreciation (double-declining) | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total tax cash flows | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total cash flow after inflation and tax | USD | 34077924.1624 | -7027565.0436 | 1524207.5807 | 1517051.9103 | 1509924.8626 | 1502826.3231 | 1495756.1778 | 1488714.313 | 1481700.6157 | 1474714.9732 | 1467757.2733 | 1460827.4042 | 1160675.2545 | 1447050.7134 | 1440203.6705 | 1433384.0158 | 1426591.6397 | 1419826.4331 | 1413088.2873 | 1406377.0941 | 1399692.7457 | 1393035.1347 | 1386404.1541 | 1379799.6974 | 1373221.6586 | 1366669.9319 | 1360144.4121 | 1353644.9945 | 1347171.5744 | 1340724.0481 | 1334302.3118
Accumulated cash flow after inflation and tax |  |  | -7027565.0436 | -5503357.4629 | -3986305.5526 | -2476380.69 | -973554.3668 | 522201.811 | 2010916.124 | 3492616.7398 | 4967331.713 | 6435088.9863 | 7895916.3905 | 9056591.645 | 10503642.3584 | 11943846.029 | 13377230.0448 | 14803821.6845 | 16223648.1176 | 17636736.4049 | 19043113.499 | 20442806.2448 | 21835841.3794 | 23222245.5335 | 24602045.231 | 25975266.8896 | 27341936.8215 | 28702081.2336 | 30055726.2281 | 31402897.8025 | 32743621.8506 | 34077924.1624
Payback period after inflation and tax | 5.6509 | years | 0 | 0 | 0 | 0 | 5.6509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on B20: t.b.d. ======
Note on O42: ====== ID#AAAAWe47BUQ tc={7095523A-2010-F042-A398-D15ACDA4DCBA} (2022-03-05 14:50:14) [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New Inverters

## Costing (Domes)
Monte Cristi Project
DOMES DESIGN
Costing
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
[6 empty] | Subtotal | % | $/Wp | Confidence
Components | Amount | Unit | Quote/unit | Total
Solar module | [5 empty] | 3661818.9113 | 43.89% | 0.30541
Risen 660Wp | 11990 | kWp | 0.285 | 3417150 |  |  |  |  | 90%
Module amount | 18166.6667
Shipping | 30.5836 | containers | 8000 | 244668.9113 |  |  |  |  | 50%
Inverters | [5 empty] | 306650 | 3.676% | 0.025575
Huawei 300 | 30 | set | 9775 | 293250 |  |  |  |  | 75%
SmartACU2000D-D-03 | 1 | unit | 5400 | 5400
Shipping | 1 | containers | 8000 | 8000 |  |  |  |  | 50%
Transformer Packages | [5 empty] | 233000 | 2.793% | 0.019433
Jupiter 900 | 1 | unit | 200000 | 200000 |  |  |  |  | 75%
Shipping | 1 | containers | 8000 | 8000 |  |  |  |  | 50%
Installation and Commissioning |  |  |  | 25000 |  |  |  |  | 50%
Interconnection | [5 empty] | 50000 | 0.5993% | 0.0041701
TBD | 1 | set |  | 50000 |  |  |  |  | 0%
Measuring and Monitoring | [5 empty] | 5856.84 | 0.0702% | 0.00048848
RainWise PVmet 330 Complete Weather Station | 2 | set | 2928.42 | 5856.84 |  |  |  |  | 90%
Mounting System | [5 empty] | 1275000 | 15.28% | 0.10634
Grace Structures | 11990 | kWp | 0.1 | 1199000 |  |  |  |  | 90%
Grounding for structure commercial | 24 | sets | 500 | 12000 |  |  |  |  | 75%
Shipping | 8 | containers | 8000 | 64000 |  |  |  |  | 50%
Grounding & Lightning Protection | [5 empty] | 68280 | 0.8184% | 0.0056947
Grounding Pits | 30 | sets | 1000 | 30000 |  |  |  |  | 50%
Complete Masts | 30 | sets | 1276 | 38280 |  |  |  |  | 90%
Cables & Conduits | [5 empty] | 666112.7429 | 7.984% | 0.055556
DC side
1x4 mm2 (PV Cable to Combiners) | 400 | Rolls (500 mtr) | 556.336 | 222534.4 |  |  |  |  | 75%
1x6 mm2 (PV Cable to Inverter) | 400 | Rolls (500 mtr) | 673.728 | 269491.2 |  |  |  |  | 75%
AC side
NYY 4x35mm2 (Inverters to AC Combiner) | 2000 | meter | 14.7429 | 29485.7143 |  |  |  |  | 50%
NYY 4x240mm2 (AC combiner to transformer to BLPC) | 2000 | meter | 59.8007 | 119601.4286 |  |  |  |  | 50%
PVC Pipe + Fittings for Outdoor | 1 | budget | 0 | 25000 |  |  |  |  | 33%
PVC Cable duct for Indoor | 0 | budget | 0 | 0 |  |  |  |  | 50%
Switch Gear | [5 empty] | 0 | 0% | 0
11KV Switchgear Panel | 0 | budget | 15000 | 0
800V Inverter Combiner Panel | 0 | budget | 30000 | 0
DC Combiners | 0 | sets | 500 | 0 |  |  |  |  | 50%
Isolator | 0 | sets | 7500 | 0 |  |  |  |  | 90%
Installation | [5 empty] | 1500000 | 17.98% | 0.1251
Installation Contractor (to be quoted) | 1 | lumpsum | 0 | 1000000 |  |  |  |  | 25%
Electrical Subcontractor | 1 | lumpsum | 0 | 500000 |  |  |  |  | 25%
Engineering and test-commissioning | [5 empty] | 75000 | 0.899% | 0.0062552
Engineering design | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Project management | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Commissioning | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Miscellaneous | [5 empty] | 501000 | 6.005% | 0.041785
Fences | 1100 | meter | 100 | 110000 |  |  |  |  | 50%
Gates | 2 | sets | 3000 | 6000 |  |  |  |  | 50%
Green Screens/planting/roadworks | 1 | budget | 100000 | 100000 |  |  |  |  | 25%
Netting | 0 | m2 | 5 | 0
CCTV | 1 | set | 50000 | 50000 |  |  |  |  | 50%
Local transportation | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Equipment transport | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Safety Equipment | 1 | budget | 10000 | 10000 |  |  |  |  | 50%
Machinery (Forklif, crane, etc) | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Insurance | 1 | set | 50000 | 25000 |  |  |  |  | 50%
Unforeseen | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Check
Total |  |  |  | 8342718.4942 |  | 8342718.4942 | 100% | 0.69581
Total/kWp |  |  | 0 | 695.8064 | /kWp
|  |  |  | 0.69581 | /Wp
| PLUS (safety margin for Financials) |  | 10% | 765.387 | /kWp
| CAPEX |  |  | 9176990.3436

## Financials (Domes)
Monte Cristi Project
Calculation sheet for grid-tied PV systems
DOMES DESIGN
DASHBOARD
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
Inputs
Location | [5 empty] | Outputs
Customer | [5 empty] | Internal Rate of Return (IRR) |  |  |  |  | Cost per kWh
[7 empty] | 20 years | 25 years | 30 years |  |  | 20 years | 25 years | 30 years
Technical inputs | [10 empty] | USD | 0.042502 | 0.04077 | 0.03431
Capacity | 11990 | kWp |  |  |  | After inflation | 19.26% | 19.68% | 19.83%
Produced energy (Pvsyst) | 17961.02 | MWh/year |  |  |  | After inflation and tax | 19.26% | 19.68% | 19.83%
Degradation / year | 0.4% | [9 empty] | Revenue after inflation
[6 empty] | Net Present Value (NPV) in USD x 1,000 | [5 empty] | 20 years | 25 years | 30 years
Economical inputs | [6 empty] | 20 years | 25 years | 30 years
Capex per kWp (USD) | 765.387 | [9 empty] | USD x 1,000 | 34589.2135 | 42811.8941 | 50871.4315
[6 empty] | After inflation | 9618.9727 | 11854.2348 | 13563.8889
FIT Rate | 0.1 | US$/kWh |  |  |  | After inflation and tax | 9618.9727 | 11854.2348 | 13563.8889
MWh produced
Discount rate (for NPV) | 5% |  |  |  |  | Payback period (years) | [5 empty] | 20 years | 25 years | 30 years
Depreciation | 10 | years | [8 empty] | MWh produced | 345892.135 | 428118.9414 | 508714.3153
Depreciation method | 1 | (1 = double decling, 0 = straight line) |  |  |  | After inflation | 5.922 | years
Corporate tax rate | 0% |  |  |  |  | After inflation and tax | 5.922 | years
Inflation (for O&M) | 2% | per year
O&M | 3% | per year
1. O&M costs assumed at zero by using idle land or rooftop space and weekly rainfall for cleaning
2. Replacement of inverters assumed in year 12
CALCULATIONS
Cash flows
Year | Total 20 years | Total 25 years | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Electricity production (kWh) | 345892135.0322 | 428118941.3649 | 17961020 | 17889175.92 | 17817619.2163 | 17746348.7395 | 17675363.3445 | 17604661.8911 | 17534243.2436 | 17464106.2706 | 17394249.8455 | 17324672.8461 | 17255374.1547 | 17186352.6581 | 17117607.2475 | 17049136.8185 | 16980940.2712 | 16913016.5101 | 16845364.4441 | 16777982.9863 | 16710871.0544 | 16644027.5702 | 16577451.4599 | 16511141.654 | 16445097.0874 | 16379316.6991 | 16313799.4323 | 16248544.2345 | 16183550.0576 | 16118815.8574 | 16054340.5939 | 15990123.2316
O&M |  | -8259291.3093 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103
Outgoing | USD | -17454221.9426 | -9176990.3436 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -568559.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103 | -275309.7103
Income before inflation | USD | 50871431.534 | 1796102 | 1788917.592 | 1781761.9216 | 1774634.8739 | 1767536.3344 | 1760466.1891 | 1753424.3244 | 1746410.6271 | 1739424.9845 | 1732467.2846 | 1725537.4155 | 1718635.2658 | 1711760.7247 | 1704913.6818 | 1698094.0271 | 1691301.651 | 1684536.4444 | 1677798.2986 | 1671087.1054 | 1664402.757 | 1657745.146 | 1651114.1654 | 1644509.7087 | 1637931.6699 | 1631379.9432 | 1624854.4235 | 1618355.0058 | 1611881.5857 | 1605434.0594 | 1599012.3232
Inflation
Income after inflation | USD | 50871431.534 | 1796102 | 1788917.592 | 1781761.9216 | 1774634.8739 | 1767536.3344 | 1760466.1891 | 1753424.3244 | 1746410.6271 | 1739424.9845 | 1732467.2846 | 1725537.4155 | 1718635.2658 | 1711760.7247 | 1704913.6818 | 1698094.0271 | 1691301.651 | 1684536.4444 | 1677798.2986 | 1671087.1054 | 1664402.757 | 1657745.146 | 1651114.1654 | 1644509.7087 | 1637931.6699 | 1631379.9432 | 1624854.4235 | 1618355.0058 | 1611881.5857 | 1605434.0594 | 1599012.3232
Total cash flow before inflation | USD | 33417209.5914 | -7380888.3436 | 1513607.8817 | 1506452.2113 | 1499325.1636 | 1492226.6241 | 1485156.4788 | 1478114.614 | 1471100.9167 | 1464115.2742 | 1457157.5743 | 1450227.7052 | 1150075.5555 | 1436451.0144 | 1429603.9715 | 1422784.3168 | 1415991.9407 | 1409226.7341 | 1402488.5883 | 1395777.3951 | 1389093.0467 | 1382435.4357 | 1375804.4551 | 1369199.9984 | 1362621.9596 | 1356070.2329 | 1349544.7131 | 1343045.2955 | 1336571.8754 | 1330124.3491 | 1323702.6128
Total cash flow after inflation | USD | 33417209.5914 | -7380888.3436 | 1513607.8817 | 1506452.2113 | 1499325.1636 | 1492226.6241 | 1485156.4788 | 1478114.614 | 1471100.9167 | 1464115.2742 | 1457157.5743 | 1450227.7052 | 1150075.5555 | 1436451.0144 | 1429603.9715 | 1422784.3168 | 1415991.9407 | 1409226.7341 | 1402488.5883 | 1395777.3951 | 1389093.0467 | 1382435.4357 | 1375804.4551 | 1369199.9984 | 1362621.9596 | 1356070.2329 | 1349544.7131 | 1343045.2955 | 1336571.8754 | 1330124.3491 | 1323702.6128
Accumulated cash flow before inflation | USD |  | -7380888.3436 | -5867280.4619 | -4360828.2506 | -2861503.087 | -1369276.4628 | 115880.016 | 1593994.63 | 3065095.5468 | 4529210.821 | 5986368.3953 | 7436596.1005 | 8586671.656 | 10023122.6704 | 11452726.642 | 12875510.9588 | 14291502.8995 | 15700729.6336 | 17103218.2219 | 18498995.617 | 19888088.6638 | 21270524.0994 | 22646328.5545 | 24015528.553 | 25378150.5126 | 26734220.7455 | 28083765.4586 | 29426810.7541 | 30763382.6295 | 32093506.9786 | 33417209.5914
Accumulated cash flow after inflation | USD |  | -7380888.3436 | -5867280.4619 | -4360828.2506 | -2861503.087 | -1369276.4628 | 115880.016 | 1593994.63 | 3065095.5468 | 4529210.821 | 5986368.3953 | 7436596.1005 | 8586671.656 | 10023122.6704 | 11452726.642 | 12875510.9588 | 14291502.8995 | 15700729.6336 | 17103218.2219 | 18498995.617 | 19888088.6638 | 21270524.0994 | 22646328.5545 | 24015528.553 | 25378150.5126 | 26734220.7455 | 28083765.4586 | 29426810.7541 | 30763382.6295 | 32093506.9786 | 33417209.5914
Payback period before inflation | 5.922 | years | 0 | 0 | 0 | 0 | 5.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Payback period after inflation | 5.922 | years | 0 | 0 | 0 | 0 | 5.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation (straight-line) | 10 | years | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | -917699.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opening Balance |  | 9176990.3436 | 8259291.3093 | 7341592.2749 | 6423893.2405 | 5506194.2062 | 4588495.1718 | 3670796.1374 | 2753097.1031 | 1835398.0687 | 917699.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation (double declining) | 10 | years | -1835398.0687 | -1468318.455 | -1174654.764 | -939723.8112 | -751779.0489 | -601423.2392 | -481138.5913 | -384910.8731 | -307928.6984 | -1231714.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opening Balance |  | 9176990.3436 | 7341592.2749 | 5873273.8199 | 4698619.0559 | 3758895.2447 | 3007116.1958 | 2405692.9566 | 1924554.3653 | 1539643.4922 | 1231714.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes paid on cost saving | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes saved on depreciation (straight line) | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes saved on depreciation (double-declining) | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total tax cash flows | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total cash flow after inflation and tax | USD | 33417209.5914 | -7380888.3436 | 1513607.8817 | 1506452.2113 | 1499325.1636 | 1492226.6241 | 1485156.4788 | 1478114.614 | 1471100.9167 | 1464115.2742 | 1457157.5743 | 1450227.7052 | 1150075.5555 | 1436451.0144 | 1429603.9715 | 1422784.3168 | 1415991.9407 | 1409226.7341 | 1402488.5883 | 1395777.3951 | 1389093.0467 | 1382435.4357 | 1375804.4551 | 1369199.9984 | 1362621.9596 | 1356070.2329 | 1349544.7131 | 1343045.2955 | 1336571.8754 | 1330124.3491 | 1323702.6128
Accumulated cash flow after inflation and tax |  |  | -7380888.3436 | -5867280.4619 | -4360828.2506 | -2861503.087 | -1369276.4628 | 115880.016 | 1593994.63 | 3065095.5468 | 4529210.821 | 5986368.3953 | 7436596.1005 | 8586671.656 | 10023122.6704 | 11452726.642 | 12875510.9588 | 14291502.8995 | 15700729.6336 | 17103218.2219 | 18498995.617 | 19888088.6638 | 21270524.0994 | 22646328.5545 | 24015528.553 | 25378150.5126 | 26734220.7455 | 28083765.4586 | 29426810.7541 | 30763382.6295 | 32093506.9786 | 33417209.5914
Payback period after inflation and tax | 5.922 | years | 0 | 0 | 0 | 0 | 5.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on B20: t.b.d. ======
Note on O42: ====== ID#AAAAWe47BUQ tc={7095523A-2010-F042-A398-D15ACDA4DCBA} (2022-03-05 14:50:14) [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New Inverters

## Costing (Tracked)
Monte Cristi Project
TRACKED DESIGN
Costing
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
[6 empty] | Subtotal | % | $/Wp | Confidence
Components | Amount | Unit | Quote/unit | Total
Solar module | [5 empty] | 3661818.9113 | 42.54% | 0.30541
Risen 660Wp | 11990 | kWp | 0.285 | 3417150 |  |  |  |  | 90%
Module amount | 18166.6667
Shipping | 30.5836 | containers | 8000 | 244668.9113 |  |  |  |  | 50%
Inverters | [5 empty] | 306650 | 3.563% | 0.025575
Huawei 300 | 30 | set | 9775 | 293250 |  |  |  |  | 75%
SmartACU2000D-D-03 | 1 | unit | 5400 | 5400
Shipping | 1 | containers | 8000 | 8000 |  |  |  |  | 50%
Transformer Packages | [5 empty] | 233000 | 2.707% | 0.019433
Jupiter 900 | 1 | unit | 200000 | 200000 |  |  |  |  | 75%
Shipping | 1 | containers | 8000 | 8000 |  |  |  |  | 50%
Installation and Commissioning |  |  |  | 25000 |  |  |  |  | 50%
Interconnection | [5 empty] | 50000 | 0.5809% | 0.0041701
TBD | 1 | set |  | 50000 |  |  |  |  | 0%
Measuring and Monitoring | [5 empty] | 5856.84 | 0.06804% | 0.00048848
RainWise PVmet 330 Complete Weather Station | 2 | set | 2928.42 | 5856.84 |  |  |  |  | 90%
Mounting System | [5 empty] | 1394900 | 16.21% | 0.11634
Grace Structures | 11990 | kWp | 0.11 | 1318900 |  |  |  |  | 90%
Grounding for structure commercial | 24 | sets | 500 | 12000 |  |  |  |  | 75%
Shipping | 8 | containers | 8000 | 64000 |  |  |  |  | 50%
Grounding & Lightning Protection | [5 empty] | 68280 | 0.7933% | 0.0056947
Grounding Pits | 30 | sets | 1000 | 30000 |  |  |  |  | 50%
Complete Masts | 30 | sets | 1276 | 38280 |  |  |  |  | 90%
Cables & Conduits | [5 empty] | 666112.7429 | 7.739% | 0.055556
DC side
1x4 mm2 (PV Cable to Combiners) | 400 | Rolls (500 mtr) | 556.336 | 222534.4 |  |  |  |  | 75%
1x6 mm2 (PV Cable to Inverter) | 400 | Rolls (500 mtr) | 673.728 | 269491.2 |  |  |  |  | 75%
AC side
NYY 4x35mm2 (Inverters to AC Combiner) | 2000 | meter | 14.7429 | 29485.7143 |  |  |  |  | 50%
NYY 4x240mm2 (AC combiner to transformer to BLPC) | 2000 | meter | 59.8007 | 119601.4286 |  |  |  |  | 50%
PVC Pipe + Fittings for Outdoor | 1 | budget | 0 | 25000 |  |  |  |  | 33%
PVC Cable duct for Indoor | 0 | budget | 0 | 0 |  |  |  |  | 50%
Switch Gear | [5 empty] | 0 | 0% | 0
11KV Switchgear Panel | 0 | budget | 15000 | 0
800V Inverter Combiner Panel | 0 | budget | 30000 | 0
DC Combiners | 0 | sets | 500 | 0 |  |  |  |  | 50%
Isolator | 0 | sets | 7500 | 0 |  |  |  |  | 90%
Installation | [5 empty] | 1600000 | 18.59% | 0.13344
Installation Contractor (to be quoted) | 1 | lumpsum | 0 | 1100000 |  |  |  |  | 25%
Electrical Subcontractor | 1 | lumpsum | 0 | 500000 |  |  |  |  | 25%
Engineering and test-commissioning | [5 empty] | 75000 | 0.8713% | 0.0062552
Engineering design | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Project management | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Commissioning | 1 | budget | 25000 | 25000 |  |  |  |  | 50%
Miscellaneous | [5 empty] | 546000 | 6.343% | 0.045538
Fences | 1550 | meter | 100 | 155000 |  |  |  |  | 50%
Gates | 2 | sets | 3000 | 6000 |  |  |  |  | 50%
Green Screens/planting/roadworks | 1 | budget | 100000 | 100000 |  |  |  |  | 25%
Netting | 0 | m2 | 5 | 0
CCTV | 1 | set | 50000 | 50000 |  |  |  |  | 50%
Local transportation | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Equipment transport | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Safety Equipment | 1 | budget | 10000 | 10000 |  |  |  |  | 50%
Machinery (Forklif, crane, etc) | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Insurance | 1 | set | 50000 | 25000 |  |  |  |  | 50%
Unforeseen | 1 | budget | 50000 | 50000 |  |  |  |  | 50%
Check
Total |  |  |  | 8607618.4942 |  | 8607618.4942 | 100% | 0.7179
Total/kWp |  |  | 0 | 717.8998 | /kWp
|  |  |  | 0.7179 | /Wp
| PLUS (safety margin for Financials) |  | 10% | 789.6898 | /kWp
| CAPEX |  |  | 9468380.3436

## Financials (Tracked)
Monte Cristi Project
Calculation sheet for grid-tied PV systems
TRACKED DESIGN
DASHBOARD
INSTRUCTION: CELLS IN GREEN ARE RESULTS FROM OTHER SHEETS. ONLY CHANGE THE BLUE ASSUMPTIONS, DON'T CHANGE OTHER CELLS
Inputs
Location | [5 empty] | Outputs
Customer | [5 empty] | Internal Rate of Return (IRR) |  |  |  |  | Cost per kWh
[7 empty] | 20 years | 25 years | 30 years |  |  | 20 years | 25 years | 30 years
Technical inputs | [10 empty] | USD | 0.036965 | 0.035461 | 0.029843
Capacity | 11990 | kWp |  |  |  | After inflation | 24.1% | 24.36% | 24.44%
Produced energy (Pvsyst) | 21294.24 | MWh/year |  |  |  | After inflation and tax | 24.1% | 24.36% | 24.44%
Degradation / year | 0.4% | [9 empty] | Revenue after inflation
[6 empty] | Net Present Value (NPV) in USD x 1,000 | [5 empty] | 20 years | 25 years | 30 years
Economical inputs | [6 empty] | 20 years | 25 years | 30 years
Capex per kWp (USD) | 789.6898 | [9 empty] | USD x 1,000 | 41008.3065 | 50756.9586 | 60312.1912
[6 empty] | After inflation | 13266.2799 | 15985.4685 | 18066.5469
FIT Rate | 0.1 | US$/kWh |  |  |  | After inflation and tax | 13266.2799 | 15985.4685 | 18066.5469
MWh produced
Discount rate (for NPV) | 5% |  |  |  |  | Payback period (years) | [5 empty] | 20 years | 25 years | 30 years
Depreciation | 10 | years | [8 empty] | MWh produced | 410083.0653 | 507569.586 | 603121.9119
Depreciation method | 1 | (1 = double decling, 0 = straight line) |  |  |  | After inflation | 5.0235 | years
Corporate tax rate | 0% |  |  |  |  | After inflation and tax | 5.0235 | years
Inflation (for O&M) | 2% | per year
O&M | 3% | per year
1. O&M costs assumed at zero by using idle land or rooftop space and weekly rainfall for cleaning
2. Replacement of inverters assumed in year 12
CALCULATIONS
Cash flows
Year | Total 20 years | Total 25 years | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Electricity production (kWh) | 410083065.2986 | 507569586.0241 | 21294240 | 21209063.04 | 21124226.7878 | 21039729.8807 | 20955570.9612 | 20871748.6773 | 20788261.6826 | 20705108.6359 | 20622288.2013 | 20539799.0485 | 20457639.8523 | 20375809.2929 | 20294306.0558 | 20213128.8315 | 20132276.3162 | 20051747.2109 | 19971540.2221 | 19891654.0612 | 19812087.445 | 19732839.0952 | 19653907.7388 | 19575292.1079 | 19496990.9394 | 19419002.9757 | 19341326.9638 | 19263961.6559 | 19186905.8093 | 19110158.186 | 19033717.5533 | 18957582.6831
O&M |  | -8521542.3093 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103
Outgoing | USD | -17999121.2426 | -9468380.3436 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -577301.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103 | -284051.4103
Income before inflation | USD | 60312191.1912 | 2129424 | 2120906.304 | 2112422.6788 | 2103972.9881 | 2095557.0961 | 2087174.8677 | 2078826.1683 | 2070510.8636 | 2062228.8201 | 2053979.9049 | 2045763.9852 | 2037580.9293 | 2029430.6056 | 2021312.8832 | 2013227.6316 | 2005174.7211 | 1997154.0222 | 1989165.4061 | 1981208.7445 | 1973283.9095 | 1965390.7739 | 1957529.2108 | 1949699.0939 | 1941900.2976 | 1934132.6964 | 1926396.1656 | 1918690.5809 | 1911015.8186 | 1903371.7553 | 1895758.2683
Inflation
Income after inflation | USD | 60312191.1912 | 2129424 | 2120906.304 | 2112422.6788 | 2103972.9881 | 2095557.0961 | 2087174.8677 | 2078826.1683 | 2070510.8636 | 2062228.8201 | 2053979.9049 | 2045763.9852 | 2037580.9293 | 2029430.6056 | 2021312.8832 | 2013227.6316 | 2005174.7211 | 1997154.0222 | 1989165.4061 | 1981208.7445 | 1973283.9095 | 1965390.7739 | 1957529.2108 | 1949699.0939 | 1941900.2976 | 1934132.6964 | 1926396.1656 | 1918690.5809 | 1911015.8186 | 1903371.7553 | 1895758.2683
Total cash flow before inflation | USD | 42313069.9486 | -7338956.3436 | 1836854.8937 | 1828371.2685 | 1819921.5778 | 1811505.6858 | 1803123.4574 | 1794774.758 | 1786459.4533 | 1778177.4098 | 1769928.4945 | 1761712.5749 | 1460279.519 | 1745379.1953 | 1737261.4728 | 1729176.2213 | 1721123.3108 | 1713102.6119 | 1705113.9958 | 1697157.3342 | 1689232.4992 | 1681339.3636 | 1673477.8005 | 1665647.6836 | 1657848.8873 | 1650081.2861 | 1642344.7553 | 1634639.1706 | 1626964.4083 | 1619320.345 | 1611706.858
Total cash flow after inflation | USD | 42313069.9486 | -7338956.3436 | 1836854.8937 | 1828371.2685 | 1819921.5778 | 1811505.6858 | 1803123.4574 | 1794774.758 | 1786459.4533 | 1778177.4098 | 1769928.4945 | 1761712.5749 | 1460279.519 | 1745379.1953 | 1737261.4728 | 1729176.2213 | 1721123.3108 | 1713102.6119 | 1705113.9958 | 1697157.3342 | 1689232.4992 | 1681339.3636 | 1673477.8005 | 1665647.6836 | 1657848.8873 | 1650081.2861 | 1642344.7553 | 1634639.1706 | 1626964.4083 | 1619320.345 | 1611706.858
Accumulated cash flow before inflation | USD |  | -7338956.3436 | -5502101.4499 | -3673730.1814 | -1853808.6037 | -42302.9179 | 1760820.5395 | 3555595.2975 | 5342054.7508 | 7120232.1606 | 8890160.6552 | 10651873.2301 | 12112152.7491 | 13857531.9443 | 15594793.4172 | 17323969.6385 | 19045092.9493 | 20758195.5612 | 22463309.557 | 24160466.8912 | 25849699.3904 | 27531038.754 | 29204516.5544 | 30870164.2381 | 32528013.1253 | 34178094.4114 | 35820439.1667 | 37455078.3373 | 39082042.7456 | 40701363.0906 | 42313069.9486
Accumulated cash flow after inflation | USD |  | -7338956.3436 | -5502101.4499 | -3673730.1814 | -1853808.6037 | -42302.9179 | 1760820.5395 | 3555595.2975 | 5342054.7508 | 7120232.1606 | 8890160.6552 | 10651873.2301 | 12112152.7491 | 13857531.9443 | 15594793.4172 | 17323969.6385 | 19045092.9493 | 20758195.5612 | 22463309.557 | 24160466.8912 | 25849699.3904 | 27531038.754 | 29204516.5544 | 30870164.2381 | 32528013.1253 | 34178094.4114 | 35820439.1667 | 37455078.3373 | 39082042.7456 | 40701363.0906 | 42313069.9486
Payback period before inflation | 5.0235 | years | 0 | 0 | 0 | 0 | 5.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Payback period after inflation | 5.0235 | years | 0 | 0 | 0 | 0 | 5.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation (straight-line) | 10 | years | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | -946838.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opening Balance |  | 9468380.3436 | 8521542.3093 | 7574704.2749 | 6627866.2405 | 5681028.2062 | 4734190.1718 | 3787352.1374 | 2840514.1031 | 1893676.0687 | 946838.0344 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10 | -9.3132e-10
Depreciation (double declining) | 10 | years | -1893676.0687 | -1514940.855 | -1211952.684 | -969562.1472 | -775649.7177 | -620519.7742 | -496415.8194 | -397132.6555 | -317706.1244 | -1270824.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opening Balance |  | 9468380.3436 | 7574704.2749 | 6059763.4199 | 4847810.7359 | 3878248.5887 | 3102598.871 | 2482079.0968 | 1985663.2774 | 1588530.6219 | 1270824.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes paid on cost saving | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes saved on depreciation (straight line) | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxes saved on depreciation (double-declining) | USD | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total tax cash flows | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total cash flow after inflation and tax | USD | 42313069.9486 | -7338956.3436 | 1836854.8937 | 1828371.2685 | 1819921.5778 | 1811505.6858 | 1803123.4574 | 1794774.758 | 1786459.4533 | 1778177.4098 | 1769928.4945 | 1761712.5749 | 1460279.519 | 1745379.1953 | 1737261.4728 | 1729176.2213 | 1721123.3108 | 1713102.6119 | 1705113.9958 | 1697157.3342 | 1689232.4992 | 1681339.3636 | 1673477.8005 | 1665647.6836 | 1657848.8873 | 1650081.2861 | 1642344.7553 | 1634639.1706 | 1626964.4083 | 1619320.345 | 1611706.858
Accumulated cash flow after inflation and tax |  |  | -7338956.3436 | -5502101.4499 | -3673730.1814 | -1853808.6037 | -42302.9179 | 1760820.5395 | 3555595.2975 | 5342054.7508 | 7120232.1606 | 8890160.6552 | 10651873.2301 | 12112152.7491 | 13857531.9443 | 15594793.4172 | 17323969.6385 | 19045092.9493 | 20758195.5612 | 22463309.557 | 24160466.8912 | 25849699.3904 | 27531038.754 | 29204516.5544 | 30870164.2381 | 32528013.1253 | 34178094.4114 | 35820439.1667 | 37455078.3373 | 39082042.7456 | 40701363.0906 | 42313069.9486
Payback period after inflation and tax | 5.0235 | years | 0 | 0 | 0 | 0 | 5.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on B20: t.b.d. ======
Note on O42: ====== ID#AAAAWe47BUQ tc={7095523A-2010-F042-A398-D15ACDA4DCBA} (2022-03-05 14:50:14) [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New Inverters

## Sheet6
rigs | power | energy/day | energy/mnth | energy/year
|  | MWh | MWh | MWh | 17961 | MWh/yr
1 | 3000 | 0.072 | 2.16 | 788.4 | 49208.2192 | kWh/day | 32805.4795
[5 empty] | 683.4475 | rigs | 2050.3425 | 32805.4795 | 24604109.589
36906164.3836
Modules |  |  |  |  | 49208.2192
20000 | 600 | 12000
Energy/Bitcoin |  | Cost of Energy
830.21 | KWH/BTC | 0.15 | per KWh | 124.5315
BTC Value
18247.1

## Prices
|  | USD/IDR | 14000
| General Price List 2021 | EUR/USD | 1.16
|  | GBP/USD | 1.36
PV Modules
| Model | Quote ($) | Transport +TAX | Cost | Capacity | $/Wp |  | Notes/Source
| Risen bifacial 645/650W | 0.281 | 10% | 0.3091 |  | 0.3091 |  | Q2/22, Huawei Europe, Bruce Tang, tangyj@risenenergy.com
| Risen monofacial 395/400Wp | 0 | 10% | 0 |  | 0 |  | Q2/22, Huawei Europe, Bruce Tang, tangyj@risenenergy.com
| Risen 600 (New Zealand) | 0 | 10% | 0 |  | 0 | 0.185 | GBP0.185/Watt peak CIF Europe
| Ja Solar Panels 380W 400W 450W 550W Tier 1 Perc Solar Panel Mono 36V | 0 | 10% | 0 |  | 0 |  | https://pnsolarpv.en.made-in-china.com/product/fOXtBrHGvQcm/China-Ja-Solar-Panels-380W-400W-450W-550W-Tier-1-Perc-Solar-Panel-Mono-36V.html
| PNG Hot Sell Half Cell PV Module Mono 400W 410W 430W 450W Solar Panel 5bb 9bb | 0 | 10% | 0 |  | 0 |  | https://pnsolarpv.en.made-in-china.com/product/mdRntFeDgzhH/China-PNG-Hot-Sell-Half-Cell-PV-Module-Mono-400W-410W-430W-450W-Solar-Panel-5bb-9bb.html
Inverters
| Model | Quote ($) | Transport +TAX | Cost | kW | $/W |  | Notes/Source
| HUAWEI SUN2000-215 KTL-M1 | 7000 | 15% | 8050 | 215 | 0.037442 |  | https://pnsolarpv.en.made-in-china.com/product/AFgxTIrGqtWZ/China-Huawei-Sun2000-215ktl-H0-Solar-Inverter-200kw-for-Solar-Energy-System.html
| HUAWEI SUN2000-315 KTL-M1 | 8500 | 15% | 9775 | 300 | 0.032583 |  | https://pnsolarpv.en.made-in-china.com/product/AFgxTIrGqtWZ/China-Huawei-Sun2000-215ktl-H0-Solar-Inverter-200kw-for-Solar-Energy-System.html
| Huawai 185kW | 7736.04 | 10% | 8509.644 | 185 | 0.045998 | 6669 | https://www.europe-solarstore.com/solar-inverters/huawei/huawei-sun2000-185-ktl-h1.html
| HUAWEI SUN2000-100 KTL-M1 | 6525 | 10% | 7177.5 | 100 | 0.071775 | 5625 | https://www.europe-solarstore.com/solar-inverters/huawei/huawei-smart-string-commercial-inverters/huawei-sun2000-100-ktl-m1.html
| HUAWEI SUN2000-60 KTL-M1 | 4650.44 | 10% | 5115.484 | 100 | 0.051155 | 4009 | https://www.europe-solarstore.com/solar-inverters/huawei/huawei-smart-string-commercial-inverters/huawei-sun2000-100-ktl-m1.html
| Sungrow SG110CX Multi-MPPT String Inverter | 5405.6 | 10% | 5946.16 | 110 | 0.054056 | 4660 | https://www.europe-solarstore.com/solar-inverters/sungrow/sungrow-commercial-3-phase/sungrow-sg110cx-multi-mppt-string-inverter.html
| Sungrow SG250HX-V112 Multi-MPPT String Inverter for 1500 Vdc System | 9993.4 | 10% | 10992.74 | 250 | 0.043971 | 8615 | https://www.europe-solarstore.com/solar-inverters/sungrow/sungrow-highvoltage/sungrow-sg250hx-v112-multi-mppt-string-inverter-for-1500-vdc-system.html
| SMA Sunny Highpower Peak3 SHP 150-20 | 8350.84 | 10% | 9185.924 | 150 | 0.061239 | 7199 | https://www.europe-solarstore.com/solar-inverters/sma/sma-sunny-highpower/sma-sunny-highpower-peak3-shp-150-20.html
| Delta M88H_121 ST | 5305.84 | 10% | 5836.424 | 88 | 0.066323 | 4574 | https://www.europe-solarstore.com/solar-inverters/delta/delta-solar-inverters/delta-m88h-121-st.html
Goodwe HT 1500V Series (225/250kW)
| GoodWe GW80KBF-MT Solar Inverter | 3874.4 | 10% | 4261.84 | 80 | 0.053273 | 3340 | https://www.europe-solarstore.com/solar-inverters/goodwe/goodwe-gw80kbf-mt-solar-inverter.html
| Growatt MAX 185/253 | [6 empty] | https://www.ginverter.com/Large-Commercial-Utility-Inver/42-642.html
Hybrid Inverters
| Model | Quote ($) | Transport +TAX | Cost | kW | $/W |  | Notes/Source
| ICASolar SNV-GH5041 5kW/48V | 487.1429 | 20% | 584.5714 | 5 |  | 6820000 | https://www.icasolar.com/product/icasolar-snv-gh5041-5kw48v
ESS
| Model | Quote ($) | Transport +TAX | Cost | kWh | $/Wh |  | Notes/Source
| BYD Battery-Box Premium HVS module ((2.56 kWh, 102.4 V, 38 kg) | 1342.12 | 10% | 1476.332 | 2.56 | 0.52427 | 1157 | https://www.europe-solarstore.com/byd-battery-box-premium-hvs-module.html
| BYD Battery-Box Premium HVM module (2.76 kWh, 51.2 V, 38 kg) | 1334 | 10% | 1467.4 | 2.76 | 0.48333 | 1150 | https://www.europe-solarstore.com/byd-battery-box-premium-hvm-module.html
| ICAL LIP48100LF (9.6 kWh) | 1200 | 15% | 1380 | 9.6 | 0.125 | 1200
Transformer/Inverter packages
| Model | Quote ($) | Transport +TAX | Cost | kW | $/W |  | Notes/Source
| Huawei STS6000 Smart Transformer Package | 0 | 10% | 0 |  |  | 0
| Huawei STS3000 Smart Transformer Package | 0 | 10% | 0 |  |  | 0
| INGECON SUN 1665TL B640 (6) + INGECON SUN FSK 4995 B Series (2) | 566845.6 | 10% | 623530.16 | 10000 | 0.062353 | 488660
Monitoring
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
| HUAWEI Smart Logger 3000A03 | 1734.2 | 10% | 1907.62 |  |  | 1495 | https://www.europe-solarstore.com/accessories/monitoring/huawei/huawei-smart-logger-3000a03.html
| RainWise PVmet 330 Complete Weather Station | 2662.2 | 10% | 2928.42 |  |  | 2295 | https://www.fondriest.com/rainwise-pvmet-330-complete-weather-station.htm
Mounting System
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
| Grace Solar - NZ Tables | 0.079333 | 20% | 0.0952 |  | 0.0952 | 35 | Frame system allow GBP32-34/panel CIF
| NZ Trackers | 0.102 | 20% | 0.1224 |  | 0.1224 | 45 | Trackers Gbp45/module
| Grounding for Structure Commercial |  |  | 0
Cables & Conduits
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
| HIKRA Plus 1x4mm² - [500 meters red, black, yellow, blue] | 505.76 | 10% | 556.336 |  |  | 436 | https://www.europe-solarstore.com/hikra-plus-1x4mm-500-meters-red.html
| HIKRA Plus 1x6mm² - [500 meters red, black, yellow, blue] | 612.48 | 10% | 673.728 |  |  | 528 | https://www.europe-solarstore.com/hikra-plus-1x6mm-500-meters-red.html
| NYY 1X16 mm² | 1.4025 | 20% | 1.683 |  |  | 19635
| NYY 1X25 mm² | 2.1525 | 20% | 2.583 |  |  | 30135
| NYY 1X35 mm² | 2.925 | 20% | 3.51 |  |  | 40950
| NYY 1X50 mm² | 3.9 | 20% | 4.68 |  |  | 54600
| NYY 1X70 mm² | 5.61 | 20% | 6.732 |  |  | 78540
| NYY 1X95 mm² | 7.7175 | 20% | 9.261 |  |  | 108045
| NYY 1X120 mm² | 9.675 | 20% | 11.61 |  |  | 135450
| NYY 1X150 mm² | 11.925 | 20% | 14.31 |  |  | 166950
| NYY 2X1.5 mm² | 0.5 | 20% | 0.6 |  |  | 7000
| NYY 2X2.5 mm² | 0.6875 | 20% | 0.825 |  |  | 9625
| NYY 2X4 mm² | 1.0625 | 20% | 1.275 |  |  | 14875
| NYY 2X6 mm² | 1.4375 | 20% | 1.725 |  |  | 20125
| NYY 2X10 mm² | 2.25 | 20% | 2.7 |  |  | 31500
| NYY 2X16 mm² | 3 | 20% | 3.6 |  |  | 42000
| NYY 2X25 mm² | 4.6071 | 20% | 5.5286 |  |  | 64500
| NYY 2X35 mm² | 6.1429 | 20% | 7.3714 |  |  | 86000
| NYY 2X50 mm² | 8.2857 | 20% | 9.9429 |  |  | 116000
| NYY 2X70 mm² | 11.6429 | 20% | 13.9714 |  |  | 163000
| NYY 2X95 mm² | 15.9643 | 20% | 19.1571 |  |  | 223500
| NYY 2X120 mm² | 19.9286 | 20% | 23.9143 |  |  | 279000
| NYY 3X1.5 mm² | 0.625 | 20% | 0.75 |  |  | 8750
| NYY 3X2.5 mm² | 0.9375 | 20% | 1.125 |  |  | 13125
| NYY 3X4 mm² | 1.4375 | 20% | 1.725 |  |  | 20125
| NYY 3X6 mm² | 2 | 20% | 2.4 |  |  | 28000
| NYY 3X10 mm² | 3.25 | 20% | 3.9 |  |  | 45500
| NYY 3X16 mm² | 4.6071 | 20% | 5.5286 |  |  | 64500
| NYY 3X25 mm² | 7.0643 | 20% | 8.4771 |  |  | 98900
| NYY 3X35 mm² | 9.5214 | 20% | 11.4257 |  |  | 133300
| NYY 3X50 mm² | 12.4393 | 20% | 14.9271 |  |  | 174150
| NYY 4X1.5 mm² | 0.99821 | 20% | 1.1979 |  |  | 13975
| NYY 4X2.5 mm² | 1.5357 | 20% | 1.8429 |  |  | 21500
| NYY 4X4 mm² | 2.3036 | 20% | 2.7643 |  |  | 32250
| NYY 4X6 mm² | 3.225 | 20% | 3.87 |  |  | 45150
| NYY 4X10 mm² | 5.1446 | 20% | 6.1736 |  |  | 72025
| NYY 4X16 mm² | 5.8357 | 20% | 7.0029 |  |  | 81700
| NYY 4X25 mm² | 9.0607 | 20% | 10.8729 |  |  | 126850
| NYY 4X35 mm² | 12.2857 | 20% | 14.7429 |  |  | 172000
| NYY 4X50 mm² | 16.4321 | 20% | 19.7186 |  |  | 230050
| NYY 4X70 mm² | 23.3429 | 20% | 28.0114 |  |  | 326800
| NYY 4X95 mm² | 32.1732 | 20% | 38.6079 |  |  | 450425
| NYY 4X120 mm² | 40.4661 | 20% | 48.5593 |  |  | 566525
| NYY 4X150 mm² | 49.8339 | 20% | 59.8007 |  |  | 697675
| NYY 5X4 mm² | 5.3571 | 20% | 6.4286 |  |  | 75000
| NYY 5X6 mm² | 7.5 | 20% | 9 |  |  | 105000
| NYY 5X10 mm² | 10 | 20% | 12 |  |  | 140000
| NYY 5X16 mm² | 10.3571 | 20% | 12.4286 |  |  | 145000
| NYYHY 2X0.75 mm² | 0 | 20% | 0
| NYYHY 2X4 mm² | 1.5625 | 20% | 1.875 |  |  | 21875
| NYYHY 2X6 mm² | 2.125 | 20% | 2.55 |  |  | 29750
| NYYHY 2X10 mm² | 3.5625 | 20% | 4.275 |  |  | 49875
| NYYHY 1X16 mm² | 0 | 20% | 0
| NYYHY 1X25 mm² | 0 | 20% | 0
| NYYHY 1X35 mm² | 0 | 20% | 0
| NYYHY 1X50 mm² | 0 | 20% | 0
| NYYHY 3X1.5 mm² | 0.78129 | 20% | 0.93754 |  |  | 10938
| NYYHY 3X2.5 mm² | 1.1875 | 20% | 1.425 |  |  | 16625
| NYYHY 3X4 mm² | 2.125 | 20% | 2.55 |  |  | 29750
| NYYHY 3X6 mm² | 3 | 20% | 3.6 |  |  | 42000
| NYYHY 3X10 mm² | 5 | 20% | 6 |  |  | 70000
| NYYHY 3X16 mm² | 0 | 20% | 0
| NYYHY 3X25 mm² | 0 | 20% | 0
| NYYHY 3X35 mm² | 0 | 20% | 0
| NYYHY 3X50 mm² | 0 | 20% | 0
| NYYHY 4X1.5 mm² | 1 | 20% | 1.2 |  |  | 14000
| NYYHY 4X2.5 mm² | 1.5625 | 20% | 1.875 |  |  | 21875
| NYYHY 4X4 mm² | 2.75 | 20% | 3.3 |  |  | 38500
| NYYHY 4X6 mm² | 3.875 | 20% | 4.65 |  |  | 54250
| NYYHY 4X10 mm² | 6.5 | 20% | 7.8 |  |  | 91000
| NYYHY 4X16 mm² | 0 | 20% | 0
| NYYHY 4X25 mm² | 0 | 20% | 0
| NYYHY 4X35 mm² | 0 | 20% | 0
| NYYHY 4X50 mm² | 0 | 20% | 0
| MC4 Kit Combiner 2 to 1 pair |  | 20% | 0 |  |  | 9
| MC4 Kit Combiner 3 to 1 pair |  | 20% | 0 |  |  | 24
| PVC Pipe+Fittings for outdoors |  | 20% | 0 |  |  | 3 | price per meter
| PVC Cable Duct for Indoors |  | 20% | 0 |  |  | 10 | price per meter
| Electroplating Cable Tray 200x100mm+Cover |  | 20% | 0 |  |  | 15 | price per meter
| ABB AC-TRUNK-BUS 1.05m |  | 20% | 0 |  |  | 97.5
| ABB AC-TRUNK-BUS 1.70m |  | 20% | 0 |  |  | 114.4
| ABB AC-TRUNK-BUS 2.05m |  | 20% | 0 |  |  | 130
Lightning Protection
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
| Dehn Telecopic 800 cm | 1160 | 10% | 1276 |  |  | 1000 | https://www.dehn-international.com/store/f/10808750/Artikelnummer_PDF/103121.pdf
Switch Gear
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
| DC Box IP 65 800X600 | 250 | 20% | 300 |  |  | 3500000
| DC Box IP 65 500X400 | 121.4286 | 20% | 145.7143 |  |  | 1700000
| AC Combiner IP 65 800X600 | 250 | 20% | 300 |  |  | 3500000
| AC Combiner IP 65 500X400 | 121.4286 | 20% | 145.7143 |  |  | 1700000
| ABB DC Isolator 32A 1000VDC | 0.0032143 | 50% | 0.0048214 |  |  | 45
| MCB 2 Pole | 9.6429 | 20% | 11.5714 |  |  | 135000
| MCB 3 Pole | 15.8571 | 20% | 19.0286 |  |  | 222000
| SPD 500VDC | 15 | 20% | 18 |  |  | 15
| SPD 1000VDC | 20 | 20% | 24 |  |  | 20
| PV Fuse + Fuse Holder | 4 | 20% | 4.8 |  |  | 4
| Prewiring and components | 60 | 20% | 72 |  |  | 60
| Socomec Energy Meter+CT | 350 | 20% | 420 |  |  | 350
| Main Breaker MCCB 125A | 100 | 20% | 120 |  |  | 100
| UV Release | 50 | 20% | 60 |  |  | 50
| MCB Box | 0 | 20% | 0
Engineering and test-commissioning
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
| Engineering design | 0 | 10% | 0
| Project management & site supervision | 0 | 10% | 0
| Commissioning | 0 | 10% | 0
Miscellaneous
| Model | Quote ($) | Transport +TAX | Cost |  |  |  | Notes/Source
Local transportation
Training and Documentation Residential
Training and Documentation Commercial