## Sheet1
DRY PIPE SYSTEM TEST RECORDS
Name/ Location: _________________________________________________
Notes: __________________________________________________________
Person to Contact Prior to Testing:
Telephone Number
● A main drain test should be conducted any time that a control valve has been closed and re-opened.
● Check dry pipe valve enclosure temperature and low point drains daily during cold weather.
Date | Weekly* |  | Quarterly |  |  | Once Each Year |  |  |  | Once Every 3 Years | [5 empty] | Quarterly
| Normal |  | Alarm Test | Main Drain Resid., PSI | Water Column Test Yes or No | DPV Test, Partial |  |  |  | DPV Test, Full Flow |  |  |  | Water to Insp. Test Seconds |  | QOD Test |  |  |  | By
| Static Water Press., PSI | Air Press., PSI |  |  |  | Trip Press., PSI | Trip Time, Seconds | Grade |  | Trip Press., PSI | Trip Time, Seconds | Grade |  |  | Valve reset yes or no | Trip Press., PSI | Trip Time, Seconds | Grade
|  |  | Loc. Rem |  |  |  |  | Pass | Fail |  |  | Pass | Fail |  |  |  |  | Pass | Fail
Disclaimer: This is a sample only, reference the most current edition of NFPA 25 (Standard for the inspection, testing and maintenance of waterbased fire protection systems) for full details and procedures.
*Monthly if equipped with low air or nitrogen pressure alarms.
Notify any off-premises alarm receiving station before conducting any tests. Contact them after testing to verify receipt of alarms and advise that the tests are concluded.
Main drain tests are conducted to ensure:
● | main control valves are open
● | no major obstructions exist in supply piping
● | drain valves are operational
Main Drain Test Procedures:
Ensure the discharge area is clear and water will drain away safely.
Ensure that fire pumps and other water supplies remain in operation during all testing.
Open the main drain fully and keep it open until the pressure stabilizes.
Record residual pressure in column marked "RES"
Close the main drain slowly to avoid water hammer.
Record static pressure in column marked "STAT".
Alarm tests are conducted to ensure:
● | water flow detecting devices are operational
● | local alarms are operational
● | a signal is received by off-premises station, if provided
Alarm Test Procedures:
Ensure the drain is clear and it will discharge to a safe place.
Open the alarm test valve at the Dry Pipe Valve.
Record a "yes" in the box for satifsactory results or "no" for unsatisfactory results.
Preffered results are:
| ● | local mechanical alarm operates within 3 minutes after waterflow begins
| ● | electrically operated alarm operates within 90 seconds
| ● | off-premises alarm is received within 90 seconds
Water column tests (Priming Water tests) are conducted to confirm that excess water has not accumulated above the dry pipe valve. This condition can cause:
● | improper operation of supervisory air or nitrogen pressure maintenance devices
● | dry pipe valve failure to trip due to weight of water column
● | potential freezing of water outside of heated dry pipe valve enclosure
Water Column Test Procedures:
Slowly open the priming level test valve.
If water flows, drain it.
Close the valve when water stops flowing and air discharges.
If only air discharges when the valve is opened, the priming water level may be too low. To add priming water, refer to manufacture's instructions.
Dry Pipe Valve Test:
Use on form for each dry pipe valve. This will allow evaluation of each valve over a period of time.
A partial flow trip test is done with the control valve mostly closed and relieving system air pressure by opening the priming level test valve.
Little or no water enters the system piping.
A full flow trip test is done with the control valve fully open and relieving system air pressure by opening the end test or inspector's test connection.
Water flows through the system piping.
During full flow testing, water should reach the inspectors test connection within 60 seconds. If it does not a Quick Opening Device or system flushing may be required.
Refer to NFPA 25 - Water-Based Fire Protection Systems for more details on these testing procedures.