Fire pump start and stop settings from 2019 NFPA 20, A-14-2.6.

*    *    *    *    *

Fire Pump Settings. The fire pump system, when started by pressure drop, should be arranged as follows:

(1) The jockey pump stop point should equal the pump churn pressure plus the minimum static supply pressure.

(2) The jockey pump start point should be at least 10 psi (0.68-bar) less than the jockey pump stop point.

(3) The fire pump start point should be 5 psi (0.34 bar) less than the jockey pump start point. Use 10-psi (0.68-bar) increments for each additional pump.  (Also note that NFPA 20, section 10.5.2.5 also has a provision for multiple pumps.  The second pump must start 5-10 seconds behind the primary pump starting to prevent water hammer.)

(4) Where minimum run times are provided, the pump will continue to operate after attaining these pressures. The final pressures should not exceed the pressure rating of the system.

(5) Where the operating differential of pressure switches does not permit these settings, the settings should be as close as equipment will permit. Pressures observed on test gauges should establish the settings.

*   *   *   *   *

Example:

Pump: 1000-gpm, 100-psi pump with churn pressure of 115 psi.

Suction Supply: 50 psi from city — minimum static.   60 psi from city — maximum static.

Jockey pump stop = 115 + 50 = 165 psi.

Jockey pump start = 165 - 10 = 155 psi.

Fire pump stop = 115 + 50 = 165 psi.

Fire pump start = 155 - 5 = 150 psi.

Fire pump maximum churn = 115 + 60 = 175 psi.

Disclaimer:  This is a sample only, reference the most current edition of NFPA 20 (Standard for the Installation of Stationary Pumps for Fire Protection) for full details and procedures.