## Sheet1
Weekly Diesel Fire/Booster Pump Inspection and Testing
Name/Location
Person To Contact Prior to Testing |  |  | Telephone Number
Notes:
Fire/booster pumps are normally used to:
● | Take suction from private water supply storage tanks or reservoirs to supply water for fire protection
needs at proper volume and pressure.
● | Boost (increase) inadequate (low) water pressures to proper levels
Fire pumps are a vital part of your fire protection system. It is essential that they are operational at all times.
Regular inspections and tests ensure this.
WEEKLY INSPECTION - Inspect these items prior to beginning any tests. Complete date accomplished at top
of column. Indicate Y for yes, N for no, NA for not applicable, or provide information requested in the boxes
below the date.
Date
Pump House
1. Heat maintained at not less than 40 degrees Fahrenheit
2. Outside air intake louvers free to operate
Piping System
3. Valves fully open
4. No leaks in piping
5. Suction line pressure gauge reading
6. System line pressure gauge reading
7. Suction reservoir full
8. Oil level in vertical motor sight glass normal
Controller
9. Pilot light (power on) illuminated
10. Controller selector switch in AUTO position
11. Voltage readings normal on batteries
12. Charging current readings normal on batteries
13. Battery pilot lights illuminated or battery failure pilot lights are off
14. All alarm pilot lights are off
Diesel Engine System
15. Fuel tank at least 2/3 full
16. Engine running time meter reading - hours
17. Oil level in right angle gear drive normal
18. Crankcase oil level normal
19. Engine coolant level normal
20. Electrolyte level in batteries normal
21. Battery terminals free from corrosion
22. Water jacket heater operating
Disclaimer: This is a sample only, reference the most current edition of NFPA 25 (Standard for the inspection, testing and maintenance of waterbased fire protection systems) for full details and procedures.
WEEKLY CHURN TESTING - This ensures automatic or manual starting upon demand and continuous delivery of
required system output. Start pumps by pressure drop using the inspector's test connection. Indicate Y for yes,
N for no, NA for not applicable, or provide information requested in the boxes below the date.
Flow a small amount of water by partially opening inspector's test connection or use a separate small petcock connection to
initiate pressure drop for only starting pressure maintenance pump. This will also allow pressure maintenance pump to
accomplish a shutoff sequence.
Date
Jockey - Pressure Maintenance Pump
23. Record actual pump starting pressure - psi
24. Record actual pump shutoff pressure - psi
Churn Test Procedure Use inspector's test connection to initiate pressure drop in system so fire pump starting sequence can be evaluated.
25. Record actual pump starting pressure - psi
26. Record system suction pressure while pump is running -psi
27. Record system discharge pressure while pump is running - psi
28. Packing glands should have slight discharge of water,
adjust as needed.
29. Packing boxes, bearings, or casings should not be overheating
Observe these indicators periodically while engine is running and record the indicator values just before shutting off engine.
30. Observe time for engine to crank - seconds
31. Observe time for engine to reach running speed - seconds
32. Run engine for at least 30 minutes
33. Engine oil pressure - psi
34. Speed indicator - rpm
35. Water temperature - degrees Fahrenheit
36. Oil temperature -degrees Fahrenheit
37. Check that cooling water is flowing to heat exchanger and
is discharging properly
Comments: (Clarify all "no" entries)
Disclaimer: This is a sample only, reference the most current edition of NFPA 25 (Standard for the inspection, testing and maintenance of waterbased fire protection systems) for full details and procedures.