## Sheet1
Weekly & Monthly Electric Fire/Booster Pump Inspection and Testing
Name/Location
Person To Contact Prior to Testing |  |  | Telephone Number
Notes:
Fire/booster pumps are normally used to:
● | Take suction from private water supply storage tanks or reservoirs to supply water for fire protection
needs at proper volume and pressure.
● | Boost (increase) inadequate (low) water pressures to proper levels
Fire pumps are a vital part of your fire protection system. It is essential that they are operational at all times.
Regular inspections and tests ensure this.
WEEKLY INSPECTION - Inspect these items prior to beginning any tests. Complete date accomplished at top
of column. Indicate Y for yes, N for no, NA for not applicable, or provide information requested in the boxes
below the date.
Date
Pump House
1. Heat maintained at not less than 40 degrees Fahrenheit
2. Outside air intake louvers free to operate
Piping System
3. Valves fully open
4. No leaks in piping
5. Normal suction line pressure gauge reading ___________
6. Normal system line pressure gauge reading ___________
7. Suction reservoir full
8. Oil level in vertical motor sight glass normal
Controller
9. Pilot light (power on) illuminated
10. Transfer switch normal pilot light illuminated
11. Isolating switch closed (standby source)
12. Reverse phase alarm pilot light off or normal phase rotation
pilot light illuminated
Information on this form is based on NFPA 25 - Water Based Fire Protection Systems
Monthly CHURN TESTING - This ensures automatic or manual starting upon demand and continuous delivery of
required system output. Start pumps by pressure drop using the inspector's test connection. Indicate Y for yes,
N for no, NA for not applicable, or provide information requested in the boxes below the date.
Flow a small amount of water by partially opening inspector's test connection or use a separate small petcock connection to
initiate pressure drop for only starting pressure maintenance pump. This will also allow pressure maintenance pump to
accomplish a shutoff sequence.
Date
Jockey - Pressure Maintenance Pump
13. Record actual pump starting pressure - psi
14. Record actual pump shutoff pressure - psi
Churn Test Procedure Use inspector's test connection to initiate pressure drop in system so fire pump starting sequence can be evaluated.
15. Record actual pump starting pressure - psi
16. Record system suction pressure while pump is running -psi
17. Record system discharge pressure while pump is running - psi
18. Packing glands should have slight discharge of water,
adjust as needed.
19. Packing boxes, bearings, or casings should not be overheating
20. Run pump for at least 10 minutes
21. Record time for motor to accelerate to speed -seconds
22. Record time controller is on first step (for reduced voltage
or reduced current starting) -seconds
23. Record time pump runs after starting (for automatic stop
controllers) - minutes
Comments: (Clarify all "no" entries)