## Sheet1
Wet Pipe System Inspector's and Main Drain Test Results
Name/ Location: ________________________________________________________________________________________________________________________________________________________________________________________________________
Notes: ______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________
Person to Contact Prior to Testing:
Telephone Number ( )
● A main drain test should be conducted any time that a control valve has been closed and re-opened.
Date/ BY | / |  |  |  | / |  |  |  | / |  |  |  | / |  |  |  | / |  |  |  | /
System No., Etc | Alarm |  | Drain |  | Alarm |  | Drain |  | Alarm |  | Drain |  | Alarm |  | Drain |  | Alarm |  | Drain |  | Alarm |  | Drain
| LOC. | REM. | STAT. | RES. | LOC. | REM. | STAT. | RES. | LOC. | REM. | STAT. | RES. | LOC. | REM. | STAT. | RES. | LOC. | REM. | STAT. | RES. | LOC. | REM. | STAT. | RES.
Disclaimer: This is a sample only, reference the most current edition of NFPA 25 (Standard for the inspection, testing and maintenance of waterbased fire protection systems) for full details and procedures.
INSPECTOR'S AND MAIN DRAIN TESTS - Reference the most current NFPA 25 standard for inspecting and testing additional items
Notify proper authorities before conducting any tests. There is a possibility that alarms may be activated.
Inspector's tests (Alarm Tests) are conducted to ensure:
| ● | water flow detecting devices are operational
| ● | alarms are operational
| ● | a signal is sent and received by off-premises station, if so connected.
Main drain tests are conducted to ensure:
| ● | main control valves are open
| ● | no obstruction exists in piping
| ● | drain valves are operational.
INSPECTOR'S TEST PROCEDURES - Conduct these tests quarterly (* semi-annually where vane-type and pressure-type waterflow devices are utilized) .
Ensure the discharge area is clear and water will drain away safely.
Ensure the discharge orifice is of proper size.
Ensure that fire pumps and other water supplies remain in operation during all testing.
Open the inspector's test valve fully.
For satisfactory results:
| ● | Local mechanical devices recommended to operate within 3 minutes after waterflow begins.
| ● | Electrically operated devices recommeneded to operate within 90 seconds
| ● | A local alarm is always required.
If results are satisfactory, record "yes" in:
| ● | column marked "LOC" for local alarms, or
| ● | column marked "REM" for central station, remote, proprietary, or auxiliary alarms.
If results are not satisfactory, record "no: as outlined above.
Advise receiving station (if any) that tests are concluded, and confirm the receipt of all signals.
MAIN DRAIN TEST PROCEDURES - Conduct these tests annually
Ensure the discharge area is clear and water will drain away safely.
Open the main drain fully, and keep it open until pressures stabilize.
Record residual pressure in column marked "RES"
Close the main drain slowly to avoid water hammer.
Record static pressure in column marked "STAT"