## Simplified
DATA SYSTEM | [5 empty] | Informations
Alternator |  | VGn | Rated Voltage of Alternator (V) |  |  | This informations are necessary, mainly, for users who want to use the worksheet without having read the technical information on the theory. -Filling in all Alternator data is mandatory; -At least, the data of one load must be filled in. Data for other loads can be left blank. - Only Alternator data and Loads Data must be filled in; - The correctness of the result depends on the correctness of the input data; - Constant loads are composed of induction motors, battery chargers, communication systems, etc. - Variable loads are composed of transformers, lighting systems, heating resistors, etc. Important: All fields on this spreadsheet tab are identical to the fields on the Complete spreadsheet, which is on another spreadsheet tab. They are just not visible. Therefore, only the fields in green must be completed.
|  | VGA | Adjusted Voltage of Operating the Alternator (V) |  |  |  | 0
|  | PGn | Rated Power of Alternator (kVA)
|  | VGT | Voltage at Alternator Terminals (V)
Loads Data | Initial | Pckn | Rated Power of Initial Constant Load (kVA) |  |  |  | #DIV/0!
|  | Vckn | Rated Voltage of Initial Constant Load (V)
|  | FPck | Power Factor of Initial Constant Load
|  | Pcvn | Rated Power of Initial Variable Load (kVA) |  |  |  | #DIV/0!
|  | Vcvn | Rated Voltage of Initial Variable Load (V)
|  | FPcv | Power Factor of Initial Variable Load
| Load to be Applied | PCKn | Rated Power of Constant Load (kVA) |  |  |  | 0
|  | VCKn | Rated Voltage of Constant Load (V)
|  | FPCK | Power Factor of Constant Load
|  | PCVn | Rated Power of Variable Load (kVA) |  |  | REFERENCE DOCUMENTS
|  | VCVn | Rated Voltage of Variable Load (V) |  |  | TE.EL.SA.CA.02.R1 DIESEL GENERATORS SETS - Calculations of Transient Reactance and Terminals Voltage | #DIV/0!
|  | FPCV | Power Factor of Variable Load
|  | VMPn | Rated Voltage of Motor(s) (V) |  |  | PL.EL.SA.CA.03.R0 DIESEL GENERATORS SETS - Calculations of Terminals Voltage
|  | IMPn | Starting Current of Motor(s) at Rated Voltage (A)
|  | FPMP | Power Factor of Motor(s) at Starting |  |  |  | #DIV/0!
|  |  | Transient Reactance of Alternator | X'Gn (%) | #DIV/0!
#DIV/0!
#DIV/0!
0
|  |  | 1.5708 | 1.5708
|  |  | 90 | 90
|  |  | 1.5708 | 1.5708
|  |  | 90 | 90
1.5708
90

## Complete
DATA SYSTEM | [5 empty] | Informations
Alternator |  | VGn | Rated Voltage of Alternator (V) |  |  | -Filling in all Alternator data is mandatory; -At least, the data of one load must be filled in. Data for other loads can be left blank. - Only Alternator data and Loads Data must be filled in; - The correctness of the result depends on the correctness of the input data; - Constant loads are composed of induction motors, battery chargers, communication systems, etc. - Variable loads are composed of transformers, lighting systems, heating resistors, etc.
|  | VGA | Adjusted Voltage of Operating the Alternator (V) |  |  |  | 0
|  | PGn | Rated Power of Alternator (kVA)
|  | VGT | Voltage at Alternator Terminals (V)
Loads Data | Initial | Pckn | Rated Power of Initial Constant Load (kVA) |  |  |  | #DIV/0!
|  | Vckn | Rated Voltage of Initial Constant Load (V)
|  | FPck | Power Factor of Initial Constant Load
|  | Pcvn | Rated Power of Initial Variable Load (kVA) |  |  |  | #DIV/0!
|  | Vcvn | Rated Voltage of Initial Variable Load (V)
|  | FPcv | Power Factor of Initial Variable Load
| Load to be Applied | PCKn | Rated Power of Constant Load (kVA) |  |  |  | 0
|  | VCKn | Rated Voltage of Constant Load (V)
|  | FPCK | Power Factor of Constant Load
|  | PCVn | Rated Power of Variable Load (kVA) |  |  | REFERENCE DOCUMENTS
|  | VCVn | Rated Voltage of Variable Load (V) |  |  | TE.EL.SA.CA.02.R1 DIESEL GENERATORS SETS - Calculations of Transient Reactance and Terminals Voltage | #DIV/0!
|  | FPCV | Power Factor of Variable Load
|  | VMPn | Rated Voltage of Motor(s) (V) |  |  | PL.EL.SA.CA.03.R0 DIESEL GENERATORS SETS - Calculations of Terminals Voltage
|  | IMPn | Starting Current of Motor(s) at Rated Voltage (A)
|  | FPMP | Power Factor of Motor(s) at Starting |  |  |  | #DIV/0!
|  |  | Transient Reactance of Alternator | X'Gn (%) | #DIV/0!
#DIV/0!
#DIV/0!
0
|  |  | 1.5708 | 1.5708
|  |  | 90 | 90
|  |  | 1.5708 | 1.5708
|  |  | 90 | 90
1.5708
90
𝜽_(𝒄_𝒌 )
𝜽_(𝒄_𝒗 )
𝒂_𝟏
𝒃_𝟏=((𝑷_(𝒄_𝒌𝒏 ) 𝒔𝒆𝒏⁡〖𝜽_(𝒄_𝒌 ) 〗)/𝑽_(𝑮_𝑨 ) ┤ ├ +├ ├ (𝑽_(𝑮_𝑨 ) 𝑷_(𝒄_𝒗𝒏 ) 𝒔𝒆𝒏𝜽_(𝒄_𝒗 ))/〖𝑽_(𝒄_𝒗𝒏 )〗^𝟐 ) 〖𝑽_(𝑮_𝒏 )〗^𝟐/(𝟏𝟎𝟎√(𝟑 ) 𝑷_(𝑮_𝒏 ) )┤┤
𝒄_𝟏=((𝑷_(𝒄_𝒌𝒏 ) 𝒄𝒐𝒔⁡〖𝜽_(𝒄_𝒌 ) 〗)/𝑽_(𝑮_𝑨 ) +┤ ├ (𝑽_(𝑮_𝑨 ) 𝑷_(𝒄_𝒗𝒏 ) 𝒄𝒐𝒔𝜽_(𝒄_𝒗 ))/〖𝑽_(𝒄_𝒗𝒏 )〗^𝟐 ) 〖𝑽_(𝑮_𝒏 )〗^𝟐/(𝟏𝟎𝟎√(𝟑 ) 𝑷_(𝑮_𝒏 ) )
𝒄_𝟐=├ ((𝑷_(𝑪_𝑲𝒏 ) 𝒄𝒐𝒔𝜽_(𝑪_𝑲 ))/(√𝟑 𝑽_(𝑮_𝑻 ) )┤┤+(𝑽_(𝑮_𝑻 ) 𝑷_(𝑪_𝑽𝒏 ) 𝒄𝒐𝒔𝜽_(𝑪_𝑽 ))/(√𝟑 〖𝑽_(𝑪_𝑽𝒏 )〗^𝟐 )+(𝑽_(𝑮_𝑻 ) 𝑰_(𝑴_𝑷𝒏 ) 𝒄𝒐𝒔𝜽_(𝑴_𝑷 ))/𝑽_(𝑴_𝑷𝒏 ) +(𝑷_(𝒄_𝒌𝒏 ) 𝒄𝒐𝒔𝜽_(𝒄_𝒌 ))/(√𝟑 𝑽_(𝑮_𝑻 ) )+├ ├ (𝑽_(𝑮_𝑻 ) 𝑷_(𝒄_𝒗𝒏 ) 𝒄𝒐𝒔𝜽_(𝒄_𝒗 ))/(√𝟑 〖𝑽_(𝒄_𝒗𝒏 )〗^𝟐 )) 〖𝑽_(𝑮_𝒏 )〗^𝟐/(𝟏𝟎𝟎𝑷_(𝑮_𝒏 ) )┤
𝒂_𝟏=𝑽_(𝑮_𝑨 )/√𝟑
𝒃_𝟏
𝒄_𝟏
𝒂_𝟐=├ 𝑽_(𝑮_𝑻 )/√𝟑┤
𝒂_𝟐
𝒄_𝟐
𝒃_𝟐=├ ((𝑷_(𝑪_𝑲𝒏 ) 𝒔𝒆𝒏𝜽_(𝑪_𝑲 ))/(√𝟑 𝑽_(𝑮_𝑻 ) )+(𝑽_(𝑮_𝑻 ) 𝑷_(𝑪_𝑽𝒏 ) 𝒔𝒆𝒏𝜽_(𝑪_𝑽 ))/(√𝟑 〖𝑽_(𝑪_𝑽𝒏 )〗^𝟐 )┤┤+(𝑽_(𝑮_𝑻 ) 𝑰_(𝑴_𝑷𝒏 ) 𝒔𝒆𝒏𝜽_(𝑴_𝑷 ))/𝑽_(𝑴_𝑷𝒏 ) +(𝑷_(𝒄_𝒌𝒏 ) 𝒔𝒆𝒏𝜽_(𝒄_𝒌 ))/(√𝟑 𝑽_(𝑮_𝑻 ) )+├ (𝑽_(𝑮_𝑻 ) 𝑷_(𝒄_𝒗𝒏 ) 𝒔𝒆𝒏𝜽_(𝒄_𝒗 ))/(√𝟑 〖𝑽_(𝒄_𝒗𝒏 )〗^𝟐 )) 〖𝑽_(𝑮_𝒏 )〗^𝟐/(𝟏𝟎𝟎𝑷_(𝑮_𝒏 ) )
𝒃_𝟐
𝒂𝒙^𝟐+𝒄𝒙+𝒆=𝟎
𝒂=├ 〖𝒃_𝟐〗^𝟐−┤ 〖𝒃_𝟏〗^𝟐+〖𝒄_𝟐〗^𝟐−〖𝒄_𝟏〗^𝟐
𝒄=〖𝟐𝒂_𝟐 𝒃〗_𝟐 〖−𝟐𝒂_𝟏 𝒃〗_𝟏
𝒆=〖𝒂_𝟐〗^𝟐−〖𝒂_𝟏〗^𝟐
𝒂
𝒄
𝒆
〖𝑿′〗_(𝑮_𝒏 )=(−𝒄+√(𝒄^𝟐−𝟒𝒂𝒆))/𝟐𝒂