## Legend
Title: | Job Plan Form
Project ID: | DORM
Project: | University Residential Housing
Location: | East Healey St, Champaign, IL
Source File: | E:/Dropbox/COBieForms2025/src/Dorm-PSC-XX-XX-FED-13-R01.xlsx
Requirements File: | E:/Dropbox/COBieForms2025/src/COBieForms2025-Rqmts.xlsx
Template Form File: | Forms2025Submit.xlsx
Time/Date: | 2024-07-19
Prepared By: | Bill East(bill.east@prairieskyconsulting.com)
Basis: | NBIMS-US, V3, C4.2 | https://www.nationalbimstandard.org/files/NBIMS-US_V3_4.2_COBie.pdf
| NBIMS-US, V3, C4.2, Annex A | https://www.nationalbimstandard.org/files/NBIMS-US_V3_4.2_COBie_Annex_A.pdf
Prerequisites: | Lean Handover©: COBie For Contractors | https://tinyurl.com/LeanHandover
| COBie Practitioner Knowledge | https://tinyurl.com/COBieCurriculum
| COBie Certified Professional | https://cobiecert.buildingsmart.org/
Instructions: | See PDF User's Manual provided with registration
Help also available by clicking on form top headers & data cells
Form Color Codings: | Format | Meaning
| gray (and bold) | Header information - do not change
| white | Data derived from associated COBie file - do not change
| yellow | Data entry cells to be completed, per User's Manual, by the addressee
Copyright | © 2022-2025 Prairie Sky Consulting

## JobPlans
JOB PLAN FORM
PART 1. ROUTING
1.1 FROM
Name |  | Email |  | Phone |  | Address Line 1 | Address Line 2 | State/ Province | Postal Code | Country Code
Prairie Sky Consulting |  | contact@prairieskyconsulting.com |  | +01 217 552 8732 |  | 1104 Parkview Drive | Mahomet | IL | 61853 | US
1.2 TO
Name |  | Email |  | Phone |  | Address Line 1 | Address Line 2 | State/ Province | Postal Code | Country Code
SES (Engineering Services) |  | contact@ses-ltd.co.uk |  | 2073 801 8000 |  | First Floor | 184-192 Drummond Street | London | NW1 3HP | UK
PART 2. SUBJECT
|  | Project Name: | University Residential Housing
|  | Project Location: | East Healey St, Champaign, IL
|  | Type Category: | 23-35 31 29 : Switchboards
|  | Submittal ID: | JP-Switchboards-R00
PART 3. VERSION CONTROL
Revision Number | Revision Code | Status | Date |  | Description
0 | I | T | 2024-07-19 |  | Initial Template
1 | I |  | 2024-07-23 |  | Initial Submittal
1 | I | A | 2024-07-23 |  | Receipt Acknowledged
PART 4. TYPE JOB PLANS
Part 4.3 Type Name: Lighting and Appliance Panelboard - 400V MCB - Surface (Lighting and Appliance Panelboard - 400V MCB - Surface_400 A)
Part 4.3.a Model
Model Number |  |  | Notes
LV Switchboard |  |  | n/a
Part 4.3.b Manufacturer
Name |  | Email |  | Phone |  | Address 1/ Street | Address 2/ City | State/ Province | Postal Code | Country Code
E&I Engineering Ltd |  | info@e-i-eng.com |  | 203 206 1650 |  | 2-8 Victoria Avenue | n/a | London | EC2M4NS | UK
Part 4.3.c Job Plan Task List
Job Name |  | Job Type |  | Job Frequency (mon.) | Task Description |  |  |  |  | Task Dur. (min.)
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanism - Check theMCHgear motor charging time at 0.85 Un |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanism - Check the general condition of the mechanism |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanism - Check the number of device operating cycles |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Breaking unit (arc chutes + contacts) - Check the condition of the breaking unit |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Breaking unit (arc chutes + contacts) - Check mounting of arc chutes and filter cleanliness |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Auxiliaries - Check operation of indication contacts (OF,PF) |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Auxiliaries - Check closing operation withXFclosing voltage release at 0.85 Un |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Auxiliaries - Check opening operation withMXopening voltage release at 0.70 Un |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Auxiliaries - Check closing and opening operations withMNundervoltage release |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Auxiliaries - Check time delay ofMNRdelayed undervoltage release |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control unit - Check microswitchesOF/SDE/PF/CH |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control unit - CheckM2Cprogrammable contacts |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control unit - Save protection settings, reports, and event logs withEcoStruxure Power Commissionsoftware |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control unit - Check overcurrent protection |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Check operation ofCD,CT,CEposition contacts andEFauxiliary contacts |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Check operation of safety shutters |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Clean chassis and check presence of grease on chassis |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Check disconnecting contact clusters |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Power connections - Check connection system |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Device - Check the general condition of the device |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanism - Operate the device manually and electrically |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanism - Charge the device electrically withMCHgear motor |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanism - Check the complete closing of device poles |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Auxiliaries - Check auxiliary wiring and insulation |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control Unit - Check device tripping and operation of SDE fault-trip indication contacts |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control Unit - Check ground-fault (MicroLogic 6.0 X) or earth-leakage (MicroLogic 7.0 X) protection function |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Control Unit - Check operation of Energy Reduction Maintenance Settings (ERMS) |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Device locking - Operate device keylocks |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Device locking - Operate device padlocks |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Check device racking operation |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Check IBPO racking interlock between racking handle and opening pushbutton (MasterPact MTZ2/MTZ3) |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis - Check EIFE chassis position limit switches |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis locking - Operate chassis keylocking system |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Chassis locking - Operate chassis padlocking system |  |  |  |  | 5
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Mechanical interlocking - Operate interlocking systems |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Device - Measure insulation resistance |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Mechanism - Check opening and closing forces |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Mechanism - Clean and regrease the mechanism |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Breaking Unit - Measure the contact resistance for each pole |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Auxiliaries - Check opening time ofMXopening voltage release |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Auxiliaries - Check closing time ofXFclosing voltage release |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Auxiliaries - Preventively replace theXF,MX,MNvoltage releases |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Auxiliaries - Preventively replaceMicroLogic Xcontrol unit and electrronic modules |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Control unit - Diagnose the performance of theMicroLogic Xcontrol unit functions |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Control unit - Preventively replace theMicroLogic Xcontrol uni |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Chassis - Check connection/disconnection torque |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Chassis - Clean and regrease chassis ofMasterPactdrawout devices |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Communication system - Check data transmission over theIFEEthernetinterface orEIFEembeddedEthernetinterface |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Mechanical interlocking - Operate mechanical interlocking by cable |  |  |  |  | 5
Manufacturer Maintenance |  | PM : Preventative Maintenance |  | 60 | Mechanical interlocking - Operate mechanical interlocking by rod |  |  |  |  | 5
Safety Procedures |  | SA : Safety Procedures |  | 12 | DANGER - HAZARD OF ELECTRIC SHOCK, EXPLOSION, OR ARC FLASH |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | Apply appropriate personal protective equipment (PPE) and follow safe electrical work practices. See NFPA 70E or CSA Z462 or local equivalent. |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | This equipment must be installed and serviced by qualified electrical personnel. |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | Turn off all power supplying this equipment before performing maintenance inspections. Assume that all circuits are live until they are de-energized, tested, grounded, and tagged. Consider all sources of power, including the possibility of backfeeding and control power. |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | Always use a properly rated voltage sensing device to confirm that power is off. |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | Replace all devices, doors, and covers before turning on power to this equipment. |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | Beware of potential hazards and carefully inspect the work area for tools and objects that may have been left inside the equipment. |  |  |  |  | 0
Safety Procedures |  | SA : Safety Procedures |  | 12 | Failure to follow these instructions will result in death or serious injury. |  |  |  |  | 0
(c) 2021-2025 Prairie Sky Consulting