## Legend
Title: | Job Plan Form
Project ID: | DORM
Project: | University Residential Housing
Location: | East Healey St, Champaign, IL
Source File: | E:/Dropbox/COBieForms2025/src/Dorm-PSC-XX-XX-FED-13-R01.xlsx
Requirements File: | E:/Dropbox/COBieForms2025/src/COBieForms2025-Rqmts.xlsx
Template Form File: | Forms2025Submit.xlsx
Time/Date: | 2024-07-19
Prepared By: | Bill East(bill.east@prairieskyconsulting.com)
Basis: | NBIMS-US, V3, C4.2 | https://www.nationalbimstandard.org/files/NBIMS-US_V3_4.2_COBie.pdf
| NBIMS-US, V3, C4.2, Annex A | https://www.nationalbimstandard.org/files/NBIMS-US_V3_4.2_COBie_Annex_A.pdf
Prerequisites: | Lean Handover©: COBie For Contractors | https://tinyurl.com/LeanHandover
| COBie Practitioner Knowledge | https://tinyurl.com/COBieCurriculum
| COBie Certified Professional | https://cobiecert.buildingsmart.org/
Instructions: | See PDF User's Manual provided with registration
Help also available by clicking on form top headers & data cells
Form Color Codings: | Format | Meaning
| gray (and bold) | Header information - do not change
| white | Data derived from associated COBie file - do not change
| yellow | Data entry cells to be completed, per User's Manual, by the addressee
Copyright | © 2022-2025 Prairie Sky Consulting

## JobPlans
JOB PLAN FORM
PART 1. ROUTING
1.1 FROM
Name |  | Email |  | Phone |  | Address Line 1 | Address Line 2 | State/ Province | Postal Code | Country Code
Prairie Sky Consulting |  | contact@prairieskyconsulting.com |  | +01 217 552 8732 |  | 1104 Parkview Drive | Mahomet | IL | 61853 | US
1.2 TO
Name |  | Email |  | Phone |  | Address Line 1 | Address Line 2 | State/ Province | Postal Code | Country Code
Commercial Services |  | contact@commercialservices.com |  | 812-339-9114 |  | 4710 W Vernal Pike | Bloomington | IN | 47404 | US
PART 2. SUBJECT
|  | Project Name: | University Residential Housing
|  | Project Location: | East Healey St, Champaign, IL
|  | Type Category: | 23-27 29 19 : Tanks
|  | Submittal ID: | JP-Tanks-R00
PART 3. VERSION CONTROL
Revision Number | Revision Code | Status | Date |  | Description
0 | I | T | 2024-07-19 |  | Initial Template
1 | I |  | 2024-07-22 |  | Initial Submittal
1 | I | A | 2024-07-23 |  | Receipt Acknowledged
PART 4. TYPE JOB PLANS
Part 4.1 Type Name: Tank-Cylinder (Tank - Cylinder_19 L)
Part 4.1.a Model
Model Number |  |  | Notes
DS-13 100 |  |  | n/a
Part 4.1.b Manufacturer
Name |  | Email |  | Phone |  | Address 1/ Street | Address 2/ City | State/ Province | Postal Code | Country Code
Sullair, LLC |  | info@sullair.com |  | 800-785-5247 |  | Sullair, LLC North America Operations 1 Sullair Way , IN | Michigan City | IN | 46360 | US
Part 4.1.c Job Plan Task List
Job Name |  | Job Type |  | Job Frequency (mon.) | Task Description |  |  |  |  | Task Dur. (min.)
Annual Maintenance - T&P Valve |  | PM : Preventative Maintenance |  | 12 | Both gas and electric water heaters have a safety device called a temperature and pressure relief valve, or T&P valve for short. In the event the tank is overpressurized, the relief valve opens and releases the pressure. If the valve doesn't operate correctly, the tank can overpressurize and explode. Maintenance should be performed on the T&P Valve once a year by the consumer and should be inspected by a professional every 5 years. |  |  |  |  | 15
Annual Maintenance - T&P Valve |  | PM : Preventative Maintenance |  | 12 | Shut Off the Unit. Turn off the electricity to the water heater or turn off the gas to extinguish the pilot light. Shut off the cold-water inlet to the water heater. |  |  |  |  | 5
Annual Maintenance - T&P Valve |  | PM : Preventative Maintenance |  | 12 | Pull the Trip Lever. Position a bucket to catch water from the pressure relief valve, and then pull the trip lever on the valve to release the water. Be careful as the water can be very hot. If you don't see any water coming out of the t&p valve, drain the tank and replace the valve. |  |  |  |  | 5
Annual Maintenance - T&P Valve |  | PM : Preventative Maintenance |  | 12 | IF NEEDED Replace the Valve. To replace the valve, remove the discharge pipe, and unscrew the valve from the water heater. Note the stem length and buy an exact replacement. Screw the new valve into place, tightening with a wrench. Reattach the discharge pipe, turn on the water, purge the air and either reconnect the electricity or restart the pilot light according to the manufacturer's instructions. |  |  |  |  | 30
Annual Maintenance - Flush Tank |  | PM : Preventative Maintenance |  | 12 | Flushing the Tank. Sediment buildup in the tank can reduce your water heater's energy efficiency and also clog your water lines. Avoid these problems with preventative maintenance, and increase the life of your unit by flushing the tank each time you check the pressure relief valve. |  |  |  |  | 30
Annual Maintenance - Flush Tank |  | PM : Preventative Maintenance |  | 12 | Turn Off the Unit. Turn off the electricity to the water heater or turn off the gas to extinguish the pilot. Shut off the cold-water inlet to the water heater. Open a faucet and run the water until it goes cold. |  |  |  |  | 5
Annual Maintenance - Flush Tank |  | PM : Preventative Maintenance |  | 12 | Connect a Hose. Connect a garden hose to the tank's drain valve. Place the hose’s draining end in an area that can handle several gallons of hot water. |  |  |  |  | 5
Annual Maintenance - Flush Tank |  | PM : Preventative Maintenance |  | 12 | Open the Drain Valve. Turn off the water, open the drain valve and let the tank drain completely and letting the water run until it is clear and sediment is not coming out ensures that you've removed all the sediment you can. |  |  |  |  | 10
Annual Maintenance - Flush Tank |  | PM : Preventative Maintenance |  | 12 | Close the Valve. Close the tank drain valve, disconnect the hose from the valve and close the pressure relief valve. Open all the hot-water spigots in the house to remove any air that may have been introduced into the system. Close the spigots once air stops coming from the faucet. and turn on the cold-water inlet to the tank. |  |  |  |  | 5
Annual Maintenance - Flush Tank |  | PM : Preventative Maintenance |  | 12 | Turn the Unit Back On. Close each hot-water spigot as water begins to flow from it. After closing all the spigots, Turn on the electricity to the water heater, or turn the gas switch to run. Following the instructions on the water heater, the pilot light may need to be relit. |  |  |  |  | 5
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Checking the Sacrificial Anode. Sacrificial anode rods protect the inside of water heater tanks from a process called galvanic corrosion. Because water heater tanks are made from metal that’s susceptible to corrosive elements in water, the anode sacrifices itself to protect the tank. The anode freely gives up ions so electrolysis does not dissipate the steel of the tank. |  |  |  |  | 30
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Turn Off the Unit. Turn off the electricity to the water heater or turn off the gas to extinguish the pilot. Open a facet to run the water cold. |  |  |  |  | 5
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Locate the Rod. Locate the sacrificial anode rod. This water heater component typically hangs down into the tank from the top. |  |  |  |  | 5
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Drain some water from the water heater. Shut off the incoming cold water. Attach a garden hose to the drain valve. Open the drain valve and let a few gallons of water drain from the water heater. |  |  |  |  | 5
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Remove the Rod. Using an electric impact wrench, use a 1 1/16 deep well socket to remove the anode. |  |  |  |  | 5
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Inspect the Rod. Perform a visual inspection. A rod in good working condition should be smooth and around a half inch in diameter. If the sacrificial anode rod shows signs of deterioration or has several inches of exposed core wire, replace it. |  |  |  |  | 5
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | IF NEEDED Install a New Rod. Determine the type of sacrificial anode rod your water heater needs, typically magnesium, aluminum or zinc. Install the new part in place of the old one, making sure to properly align all parts and secure all threaded screws. |  |  |  |  | 10
Annual Maintenance - Sacrificial Anode |  | PM : Preventative Maintenance |  | 12 | Turn the Unit Back On. Refill the water heater, purge all the air from the tank by running a faucet for several minutes. Turn the power on or relight the pilot light, and check for leaks. |  |  |  |  | 5
(c) 2021-2025 Prairie Sky Consulting