## Legend
Title: | Job Plan Form
Project ID: | DORM
Project: | University Residential Housing
Location: | East Healey St, Champaign, IL
Source File: | E:/Dropbox/COBieForms2025/src/Dorm-PSC-XX-XX-FED-13-R01.xlsx
Requirements File: | E:/Dropbox/COBieForms2025/src/COBieForms2025-Rqmts.xlsx
Template Form File: | Forms2025Submit.xlsx
Time/Date: | 2024-07-19
Prepared By: | Bill East(bill.east@prairieskyconsulting.com)
Basis: | NBIMS-US, V3, C4.2 | https://www.nationalbimstandard.org/files/NBIMS-US_V3_4.2_COBie.pdf
| NBIMS-US, V3, C4.2, Annex A | https://www.nationalbimstandard.org/files/NBIMS-US_V3_4.2_COBie_Annex_A.pdf
Prerequisites: | Lean Handover©: COBie For Contractors | https://tinyurl.com/LeanHandover
| COBie Practitioner Knowledge | https://tinyurl.com/COBieCurriculum
| COBie Certified Professional | https://cobiecert.buildingsmart.org/
Instructions: | See PDF User's Manual provided with registration
Help also available by clicking on form top headers & data cells
Form Color Codings: | Format | Meaning
| gray (and bold) | Header information - do not change
| white | Data derived from associated COBie file - do not change
| yellow | Data entry cells to be completed, per User's Manual, by the addressee
Copyright | © 2022-2025 Prairie Sky Consulting

## JobPlans
JOB PLAN FORM
PART 1. ROUTING
1.1 FROM
Name |  | Email |  | Phone |  | Address Line 1 | Address Line 2 | State/ Province | Postal Code | Country Code
Prairie Sky Consulting |  | contact@prairieskyconsulting.com |  | +01 217 552 8732 |  | 1104 Parkview Drive | Mahomet | IL | 61853 | US
1.2 TO
Name |  | Email |  | Phone |  | Address Line 1 | Address Line 2 | State/ Province | Postal Code | Country Code
SES (Engineering Services) |  | contact@ses-ltd.co.uk |  | 2073 801 8000 |  | First Floor | 184-192 Drummond Street | London | NW1 3HP | UK
PART 2. SUBJECT
|  | Project Name: | University Residential Housing
|  | Project Location: | East Healey St, Champaign, IL
|  | Type Category: | 23-33 25 00 : Air Handling Units
|  | Submittal ID: | JP-AirHandlingUnits-R00
PART 3. VERSION CONTROL
Revision Number | Revision Code | Status | Date |  | Description
0 | I | T | 2024-07-19 |  | Initial Template
1 | I |  | 2024-07-23 |  | Initial Submittal
1 | I | A | 2024-07-23 |  | Receipt Acknowledged
PART 4. TYPE JOB PLANS
Part 4.1 Type Name: Air Handling Unit (Air Handling Unit_63300000 J)
Part 4.1.a Model
Model Number |  |  | Notes
MAX37/A/SW/S |  |  | n/a
Part 4.1.b Manufacturer
Name |  | Email |  | Phone |  | Address 1/ Street | Address 2/ City | State/ Province | Postal Code | Country Code
VES Andover Ltd |  | vesltd@ves.co.uk |  | 844 815 1660 |  | Eagle Close, Chandlers Ford Industrial Estate | Eastleigh | Hampshire | SO53 4NF | UK
Part 4.1.c Job Plan Task List
Job Name |  | Job Type |  | Job Frequency (mon.) | Task Description |  |  |  |  | Task Dur. (min.)
Quarterly Maintenance |  | PM : Preventative Maintenance |  | 3 | For individual component maintenance requirements please refer to the relevant section of the manufacturers O&M Manual. |  |  |  |  | 0
Quarterly Maintenance |  | PM : Preventative Maintenance |  | 3 | The belt drive should be thoroughly checked. If belts are found to be loose or worn, retighten or replace as necessary. Refer to relevant accompanying documentation for details and recommended tension. |  |  |  |  | 15
Quarterly Maintenance |  | PM : Preventative Maintenance |  | 3 | Filters should be inspected regularly. If they are found to be heavily soiled or damaged they should be replaced immediately. |  |  |  |  | 15
Quarterly Maintenance |  | PM : Preventative Maintenance |  | 3 | The general operation of the unit should be inspected, particularly for noise from bearings, motors and fans. An irregular noise could signify that unit failure is imminent. |  |  |  |  | 15
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | For individual component maintenance requirements please refer to the relevant section of the manufacturers O&M Manual. |  |  |  |  | 0
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | The belt drive should be thoroughly checked. If belts are found to be loose or worn, retighten or replace as necessary. Refer to relevant accompanying documentation for details and recommended tension. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Filters should be inspected regularly. If they are found to be heavily soiled or damaged they should be replaced immediately. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | The general operation of the unit should be inspected, particularly for noise from bearings, motors and fans. An irregular noise could signify that unit failure is imminent. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Check for dust build-up in the system, especially around the impeller. Remove dust if necessary. Failure to do this periodically could lead to a loss of performance or cause the fan to become out of balance, ultimately leading to bearing failure. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Coils should be inspected to ascertain if any foreign matter has accumulated between the fins and that the coil connections are free from any leaks. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Should any matter be found, the coils should be cleaned using a soft brush and mild solution of commercial detergent. If heavily contaminated, a steam lance may be used. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Care should be taken so as not to damage or distort the fins during this cleaning process. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Periodically inspect heat exchange matrix for any debris, dust or dirt build up. Frequent contamination might be as a result of poor filtration and should be investigated. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Under NO circumstances should the heat exchanger be steam cleaned. |  |  |  |  | 30
Semi-Annual Maintenance |  | PM : Preventative Maintenance |  | 6 | Ensure the drain pan and the drain connection is free from debris ensuring any condensate produced can freely drain away. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | For individual component maintenance requirements please refer to the relevant section of the manufacturers O&M Manual. |  |  |  |  | 0
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | The belt drive should be thoroughly checked. If belts are found to be loose or worn, retighten or replace as necessary. Refer to relevant accompanying documentation for details and recommended tension. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Filters should be inspected regularly. If they are found to be heavily soiled or damaged they should be replaced immediately. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | The general operation of the unit should be inspected, particularly for noise from bearings, motors and fans. An irregular noise could signify that unit failure is imminent. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Check for dust build-up in the system, especially around the impeller. Remove dust if necessary. Failure to do this periodically could lead to a loss of performance or cause the fan to become out of balance, ultimately leading to bearing failure. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Coils should be inspected to ascertain if any foreign matter has accumulated between the fins and that the coil connections are free from any leaks. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Should any matter be found, the coils should be cleaned using a soft brush and mild solution of commercial detergent. If heavily contaminated, a steam lance may be used. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Care should be taken so as not to damage or distort the fins during this cleaning process. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Periodically inspect heat exchange matrix for any debris, dust or dirt build up. Frequent contamination might be as a result of poor filtration and should be investigated. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Under NO circumstances should the heat exchanger be steam cleaned. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Ensure the drain pan and the drain connection is free from debris ensuring any condensate produced can freely drain away. |  |  |  |  | 30
Annual Maintenance |  | PM : Preventative Maintenance |  | 12 | Max units are supplied with either unpainted galvanized sheet steel or powder coat paint finishes. Check all painted items to ensure that they have not deteriorated. Repaint as necessary. Paint can be supplied upon request. Checks should be carried out for missing fasteners. |  |  |  |  | 30
(c) 2021-2025 Prairie Sky Consulting