## Part 4
KCTMO | Issue 1 | Issue 2 | Person
Some, perhaps many, occupants of the tower regarded the TMO as an uncaring and bullying overlord that belittled and marginalised them, regarded them as a nuisance, or worse, and failed to take their concerns seriously. For its part, the TMO regarded some of the residents as militant troublemakers led on by a handful of vocal activists, principally Edward Daffarn, whose style they found offensive. The result was a toxic atmosphere fuelled by mistrust on both sides. | Customer service | Victimisation | Residents
Created an unequal relationship and a corresponding need for the TMO to ensure that, whatever the difficulties, the residents were treated with understanding and respect. We have concluded that the TMO failed to recognise that need and therefore failed to take the steps necessary to ensure that it was met. | Customer service | Victimisation | Residents
Chapter 31 Structure and Governance
Finance, Audit and Risk Committee: Health and Safety (including fire safety). | Structure | Health and Safety | KCTMO
Every March, a Health and Safety report was presented to above committee. | Structure | Health and Safety | KCTMO
RBKC Housing and Property Scruitiny Committee. | Structure | Committee | RBKC
Director of Finance and ICT responsible for health and safety and strategic level performance | Responsibility | Health and Safety | Barbara Matthews
Barbara Matthews had no experience of health and safety (Finance Director) | Expertise | Health and Safety | Barbara Matthews
Relied heavily on Janice Wray (Health and Safety Facilities Manager), too much work | Expertise | Health and Safety | Janice Wray
Annual health and safety report | Structure | Health and Safety | KCTMO
Barbara Matthews and Janine Wray responsible for health and safety | Expertise | Health and Safety | Barbara Matthews
LFB concerned that FRAs were not adequate | Compliance | Health and Safety | Fire Brigade
LFB would serve enforcement notice hence TMO entered into a contract with Salvas Consulting for FRAs | Compliance | Health and Safety | Fire Brigade
Fire safety breaches identified by Salvas: flat entrance doors, self closing devices, intumescent strips and cold smoke seals | Compliance | Health and Safety | Salvas Consultant
Dec 2009 report to the Board said nothing about the 19 breaches of Fire Safety Order | Withheld Information | Health and Safety | Janice Wray
Janice Wray and Robert Black equally at fault in not advising the Board | Withheld Information | Health and Safety | Robert Black
Mar 2010 report did not advise the Board about LFB concerns of FRAs | Withheld Information | Health and Safety | Robert Black
April 2010 fire at lift lobby. | Incident | Health and Safety | Fire Brigade
May 2010, Janice Wray advised Collette O'Hara of LFB about fire being smoke leakage | Withheld Information | Health and Safety | Janice Wray
June 2010, Janice Wray did not advise the Board about the fire smoke leakage or that residents belief in being trapped | Withheld Information | Health and Safety | Janice Wray
Janice Wray made smoke leakage being a minor issue, mislead and understated about this | Withheld Information | Health and Safety | Janice Wray
Robert Black did not correct what Janice Wray had understated | Withheld Information | Health and Safety | Robert Black
Mar 2014 LFB deficiency notice to KCTMO for smoke ventiliation system, complaints by Leaseholders Association | Compliance | Health and Safety | Fire Brigade
May 2014 Board meeting made no mention by Robert Black of LFB deficiency notice. | Withheld Information | Health and Safety | Robert Black
Oct 2015 LFB issued deficiency notice for Adair Tower by LFB, Fire Safety Order due to failures to carry out remedial works in FRAs | Compliance | Health and Safety | Fire Brigade
Oct 2015 Janice Wray received notice from LFB but did not tell Robert Black until late October. | Withheld Information | Health and Safety | Janice Wray
Late October 2015, Robert Black did not mention to the Board about LFB deficiency notice. | Withheld Information | Health and Safety | Robert Black
Nov 2015, Rebecca Burton of LFB sent email to Janice Wray about Adair Tower fire. | Compliance | Health and Safety | Fire Brigade
In Oct 2015, LFB said it would issue further deficiency notices for other KCTMO properties with some due to absence of effective self-closing devices. | Compliance | Health and Safety | Fire Brigade
Robert Black on Nov 2015 did not mention the Adair Tower deficiency notice to RBKC's Housing and Property Scrutiny Committee | Withheld Information | Health and Safety | Robert Black
Robert Black serious dereliction of duty on his part as per not telling scrutiny committee | Withheld Information | Health and Safety | Robert Black
Barbara Matthews did not mention the deficiency notice issued in Oct 2015 and did not mention various enforcement measures of the LFB | Withheld Information | Health and Safety | Barbara Matthews
Dec 2015 further enforcement notice to KCTMO following fire at Adair Tower. | Compliance | Health and Safety | Fire Brigade
Jul 2016, Janice Wray spoke to Ben Dewis of LFB. LFB were considering taking legal action. | Compliance | Health and Safety | Fire Brigade
Jul 2016, Robert Black did not advice the Board of LFB possibly taking legal action against KCTMO. | Withheld Information | Health and Safety | Robert Black
Nov 2016, LFB issued deficiency notice to KCTMO for Grenfell Tower, absence of self-closing devices on some doors. | Compliance | Health and Safety | Fire Brigade
Chapter 32 RBKC Oversight of the TMO
No fire safety KPI from TMO to RBKC | Compliance | Health and Safety | KCTMO
Janice Wray was writing her own reference relating to fire safety | Withheld Information | Health and Safety | Janice Wray
No evidence of audit for FRAs took place when meant to in 2012 | Compliance | Health and Safety | Audit
Other three general health and safety audits. | Compliance | Health and Safety | Audit
Sept 2009 Salvas Consulting considered fire safety policy and procedures. | Compliance | Health and Safety | Salvas Consultant
July 2013 Matt Hodgson on safety management review. | Compliance | Health and Safety | Hodgson Consultant
Chapter 33 TMO's relationship with its residents
Memoli and Butler reports in 2009, lack of trust of the TMO. | Customer service | Victimisation | Residents
RBKC would consider mediation when this was recommended. | Customer service | Victimisation | RBKC
TMO give leaseholders opportunity about share of cost from needing to share info with residents. | Customer service | Consultation | KCTMO
TMO to have equality and diversity considerations which resulted in an action plan. | Customer service | Equality | KCTMO
Historical them and us between RBKC and KCTMO, changes took place at Executive level | Structure | Relationship | KCTMO
RBKC should be more robust in making sure TMO's technical services were capable of delivering effective major works program and cyclical repairs | Repairs | Health and Safety | RBKC
Even though recommendations from reports needed actions, TMO did little changes in 8 years | Customer service | Relationship | KCTMO
Complaint policy not reviewed in 3 year period, done in 2010 then 2015 and broadened complaint definition. | Complaints | Customer Service | KCTMO
Lancaster West Residents Association, Grenfell Action Group, Grenfell Tower Leaseholders Association and Grenfell Tower Compact | Customer service | Groups | Groups
Shah Ahmed afraid of his lease being forfeited due to raising issues. | Customer service | Leaseholder | Shah Ahmed
Shah Ahmed felt fire in 2010 had been understated. | Customer service | Leaseholder | Shah Ahmed
Eddie Daffarn and Francis O'Connor produced Grenfell Action Group blog. | Customer service | Relationship | Eddie Daffarn
2013 power surges resulted in emails to TMO aswell as a petition. | Electricity | Health and Safety | KCTMO
Peter Maddison (Head of Assets) felt being agitated by Eddie Daffarn in March 2015. | Customer service | Relationship | Peter Maddison
TMO were nervous of Eddie Daffarn. | Customer service | Relationship | Eddie Daffarn
Consultation where Eddie Daffarn complained residents at Grenfell not been consulted about Studio E as architect | Customer service | Relationship | Eddie Daffarn
Eddie Daffarn questioned by Studio E had been selected for Grenfell in March 2012. | Customer service | Relationship | Eddie Daffarn
Eddie Daffarn asked if Studio E had any experience with tower blocks, no response to him by TMO. | Customer service | Relationship | Eddie Daffarn
Dec 2013 felt by two councillors and Peter Maddison that Eddie Daffarn was too disruptive. | Customer service | Relationship | Eddie Daffarn
Dec 2015 petition by some 60 residents, felt ignored | Customer service | Relationship | Eddie Daffarn
TMO and RBKC seemed to seek to silence Councillor Blakeman. | Structure | Relationship | Councillor Blakeman
Jan 2016 Edward Daffarn able to address housing committee. | Customer service | Relationship | Eddie Daffarn
Jan 2016 to March 2016, TMO Board carried out review of the refurbishment. | Compliance | Health and Safety | KCTMO
Robert Black inferred as having ignored residents views in 2016. | Customer service | Consultation | Robert Black
Flawed Working Group report in March 2016. | Structure | Health and Safety | KCTMO
Distrust, dislike, personal antagonism and anger, some residents considered TMO as uncaring and bullying overlord. | Customer service | Relationship | KCTMO
Lack of respect and unequal relationship. | Customer service | Relationship | KCTMO

## Part 5
The Management of Fire Safety at Grenfell Tower | Issue 1 | Issue 2 | Person
RBKC oversight of KCTMO was weak, no fire safety KPI | Compliance | Health and Safety | KCTMO
Robert Black failed to report any fire safety issues to RBKC | Withheld Information | Health and Safety | Robert Black
Robert Black did not advise Board about LFB issues | Withheld Information | Health and Safety | Robert Black
Carl Stokes only fire assessor with no formal procurement or selection process, Janice Wray instructed for Carl Stokes | Procurement | Health and Safety | Carl Stokes
Stokes had misrepresented his experience and qualifications (some of which he had invented) and was ill-qualified to carry out fire risk assessments on buildings of the size and complexity of Grenfell Tower, let alone to hold the entire TMO portfolio. As a result there was a danger that fire risk assessments would not meet the required standard. | Fraud | Qualification | Carl Stokes
Despite the concerns expressed by the LFB about his competence, the TMO continued to rely uncritically on him, a situation which made the danger more acute in the absence of any arrangements for assessing the quality of his work. | Expertise | Health and Safety | Fire Brigade
New front doors installed by the TMO in 2011 and 2012 did not meet the fire resistance standards suggested by Approved Document B because the TMO had failed to specify the correct fire safety standard when ordering them. | Compliance | Health and Safety | KCTMO | Back in November 2016, and following a referral from Sandwell Council, officers from the West Midlands Fire Service visited Metro Court, which was originally designed as an office block – and discovered multiple fire safety breaches as follows:
The TMO did not institute an effective inspection and maintenance programme for self-closing devices on entrance doors despite an Enforcement Notice issued by the LFB in late 2015 relating to ineffective door closers in another high-rise residential building it managed, Adair Tower, and a Deficiency Notice issued in 2016 in relation to Grenfell Tower itself on the same grounds. | Compliance | Health and Safety | Fire Brigade
The TMO did take some steps to gather information of that kind, both before and during the refurbishment, but its data systems were not properly co-ordinated. Such information as was collected was not always used to revise its records, with the result that the spreadsheet available on the night of the fire was incomplete. The TMO’s failure to collect such information amounted to a basic neglect of its obligations in relation to fire safety. | Data | Health and Safety | KCTMO | *there was no power to the fire alarm system, which was also faulty
Chapter 35 The Fire Safety Order
Article 8 of the Regulatory Reform (Fire Safety) Order 2005 (the Fire Safety Order) imposes on “the responsible person” an obligation to take such general fire precautions as will ensure, so far as is reasonably practicable, that the premises are safe | Compliance | Health and Safety | KCTMO | *insufficient fire detection in the third floor corridor
Article 5(3) imposes on anyone other than the responsible person who has control of the premises the same duties as those imposed on the responsible person, so far as they relate to matters within his control. | Compliance | Health and Safety | KCTMO
a. Suitable and sufficient fire risk assessment, identify general fire precautions. | Compliance | Health and Safety | KCTMO | *numerous fire doors were either wedged or propped open
b. Preventative and protective measures. | Compliance | Health and Safety | KCTMO
c. Safeguard safety of relevant persons, premises appropriately equipped with fire-fighting equipment and fire detectors and alarms, any non-automatic fire-fighting equipment is easily accessible, simple to use, signage. | Compliance | Health and Safety | KCTMO | *combustible materials were present in the staircase and obstructing the means of escape
d. Measures for fire-fighting, nominate competent persons to implement. Training and equipment available are adequate. | Compliance | Health and Safety | KCTMO
e. Routes to emergency exits from premises and the exits themselves are kept clear all times. | Compliance | Health and Safety | KCTMO | *flat windows opening on to a staircase were not fire-resistant
f. Appropriate procedures including fire safety drills, followed in event of serious and imminent danger. | Compliance | Health and Safety | KCTMO
g. Premises subject to suitable system of maintenance and maintained in efficient stage, efficient working order and in good repair. | Compliance | Health and Safety | KCTMO | The failures were so serious that a Prohibition Notice was served, thereby preventing anyone from using the premises for residential purposes. However, revisits over the following months revealed that people were still living there.
h. Appoint one or more competent persons to assist with preventative and protective measures. | Compliance | Health and Safety | KCTMO
i. Ensure all employees are provided with adequate safety training. | Compliance | Health and Safety | KCTMO
TMO as the responsible person where set out its understanding of division of responsibilities. Set out in annual health and safety report for 2009-2010 | Compliance | Health and Safety | KCTMO
a. Operational compliance with the Fire Safety Order had been delegated to the TMO. | Compliance | Health and Safety | KCTMO
b. RBKC was liable for any breach of the Fire Safety Order and subject to enforcement notices or prosecution or both | Compliance | Health and Safety | KCTMO
c. RBKC would monitor the TMO's actions on health and safety matters to ensure compliance with relevant statutory responsibilities and adherence to best practice. | Compliance | Health and Safety | KCTMO
d. RBKC's corporate health and safety adviser and health and safety adviser for housing, health and adult social care would receive minutes of the meetings of the TMO's health and safety committee and copies of the TMO's annual report on health and safety. | Compliance | Health and Safety | KCTMO
e. TMO's health and safety adviser would attend RBKC's six-weekly meetings of its main Co-ordinating Committee dealing with health and safety matters. | Compliance | Health and Safety | KCTMO
f. It would notify RBKC of major incidents, accidents, significant near-misses and any current investigations. | Compliance | Health and Safety | KCTMO
Robert Black understood the distinction between responsible person and competent person. | Compliance | Health and Safety | Robert Black
Barbara Matthews believed RBKC and TMO were both responsible persons for premises owned by RBKC but managed by TMO. | Compliance | Health and Safety | Barbara Matthews
Article 18(1) of Fire Safety Order: responsible person to appoint one or more competent persons to assist him in undertaking the preventive and protective measures. | Compliance | Health and Safety | KCTMO
Article 18(3) of Fire Safety Order: obliges the responsible person to ensure that the number of competent persons appointed, the time available for them to fulfil their functions and the means at their disposal are adequate having regard to the size of the premises, the risks to which relevant persons are exposed and the distribution of those risks throughout the premises | Compliance | Health and Safety | KCTMO
Article 18(5) of Fire Safety Order: a person is to be regarded as competent if he has sufficient training and experience or knowledge and other qualities to enable him properly to assist in undertaking the preventive and protective measures. Janice Wray, the TMO’s health and safety manager, was familiar with the concept of the competent person and undertook that role for the TMO. | Compliance | Health and Safety | KCTMO
Originally Janice Wray remit was to advise on compliance with the Fire Safety Order and attend meetings and committees as necessary to provide information on the TMO's performance in relation to specific areas of health and safety, including compliance with the Fire Safety Order. But from mid-2015 primary operational responsibility lay with Barbara Matthews. | Compliance | Health and Safety | Barbara Matthews
Matt Hodgson identified Janet Wray as the competent person, requested amend from Adrian Bowman who was Janet's assistant. | Compliance | Health and Safety | Janice Wray
Chapter 36 Fire Safety Management at the TMO
Robert Black was ultimately responsible for health and safety at TMO. | Compliance | Health and Safety | Robert Black
Policies and fire safety strategies reviewed. | Compliance | Health and Safety | KCTMO
Chapter 37 Development of Fire Safety Strategies and Policies
Before 2008, Adrian Bowman and Janice Wray carried out FRAs. May 2008, LFB not happy with FRAs. | Compliance | Health and Safety | Fire Brigade
Jan 2009 LFB further not happy that FRAs had improved, not good with Article 9(1) of FSO. | Compliance | Health and Safety | Fire Brigade
Discussions between Janice Wray and LFB. | Compliance | Health and Safety | Janice Wray
Jun 2009 FRAs not competent in being carried out hence LFB would issue enforcement notice against RBKC and TMO requiring FRAs to be carried out by a competent person. | Compliance | Health and Safety | Fire Brigade
Janice Wray advised senior management which then resulted in getting specialist to carry them out. | Compliance | Health and Safety | Janice Wray
RBKC agreed for need of an external consultant for FRAs. | Compliance | Health and Safety | RBKC
Sep 2009 Salvas Consulting was appointed for first phase of FRAs. | Compliance | Health and Safety | Salvas Consultant
Jan 2010 LFB satisfied with TMO proposal for FRAs, Robert Black had written to them. | Compliance | Health and Safety | Robert Black
Sep 2009 Salvas carried out detailed assessment of TMO's fire safety management systems. | Compliance | Health and Safety | Salvas Consultant
Salvas report part 1 identified 25 deficiencies in TMO's fire safety management arrangements. | Compliance | Health and Safety | Salvas Consultant
Salvas report part 2 was an action plan which set out 49 steps required to reduce risks identified. | Compliance | Health and Safety | Salvas Consultant
Janice Wray should have advised Executive Team about substance of Salvas report | Compliance | Health and Safety | Janice Wray
Dec 2019 Janice Wray did not advise Board about consultant's critical findings and urgent measures. | Compliance | Health and Safety | Janice Wray
Salvas report and findings were discussed with TMO and RBKC in Jan 2010. | Compliance | Health and Safety | Salvas Consultant
Fire safety policy not produced as per recommendation until Nov 2013. | Compliance | Health and Safety | KCTMO
TMO failed to implement recommendations promptly. | Compliance | Health and Safety | KCTMO
Salvas also recommended for TMO to introduce a senior managerial audit, this was not done. | Compliance | Audit | KCTMO
No audit of FRAs aswell as no audit of fire safety management system as a whole, not complied with Salvas recommendation. | Compliance | Audit | KCTMO
Jun 2013 PAS 7, 2013. Paragraph 7.4.3 stated that an organisation should audit the fire risk assessment programme after the delivery of the fire risk assessments and hold review meetings at planned intervals to discuss the results of the audits of fire risk assessments and the efforts made to respond to the findings. | Compliance | Audit | KCTMO
At paragraph 8.3.1, it provided that senior management should review the organisation’s fire risk management system at planned intervals to ensure its continuing suitability, adequacy and effectiveness. That specification bears a striking resemblance to the recommendation made by Salvus in September 2009 for a senior managerial audit of fire safety arrangements. | Compliance | Audit | KCTMO
Janice Wray aware of PAS 7, made no provision for audit of FRA or for Fire Risk Management system. | Compliance | Audit | Janice Wray
Audits were carried out by RBKC with assurance ratings given. | Compliance | Audit | KCTMO
RBKC carried out audit of TMO Health and Safety department in April 2013, gave limited assurance. | Compliance | Audit | KCTMO
RBKC audit said high priority remedial work should be reviewed and undertaken promptly. | Compliance | Audit | KCTMO
RBKC audit also said appropriate performance indicators relating to health and safety inspections should be developed by management. | Compliance | Audit | KCTMO
Following RBKC audit, TMO got Health and Safety professional Matt Hodgson to carry out review. | Compliance | Audit | KCTMO
Mr Hodgson identified 39 matters relating to health and safety. Said RBKC's Chief Exec should not be responsible person for the purposes of the FSO. Instead should be someone in the TMO. | Compliance | Health and Safety | Hodgson Consultant
TMO health and safety policy did not identify risks that was exposed to and failed to explain obligations towards fire safety. Not enough detail and echoed the criticism made by Salvas in 2009. | Compliance | Policy | KCTMO
Reactive rather than planned maintenance arrangements. | Compliance | Health and Safety | Reactive
Hodgson found FRAs records not up to date and not possible if complied. 900-1000 outstanding matters from previous FRAs. | Compliance | Health and Safety | Hodgson Consultant
Robert Black did not mention in Sep 2013 Hodgson's report to the Board about shortcomings especially how TMO itself and the members of the board could be exposed to liability if some of the deficiencies that had been identified were not remedied. Nor did he mention the lack of a co-ordinated approach to risk management or a lack of leadership from the executive team. | Withheld Information | Health and Safety | Robert Black
Inferred Black chose to avoid embarassment from the Board for Hodgson's report as 4 years since Salvas report. Mr Black’s decision not to inform the board about those important matters prevented it from exercising effective supervision and control over the development of adequate fire safety management policies and arrangements. That was a very serious failing on his part. | Withheld Information | Health and Safety | Robert Black
His own failure to take responsibility for implementing the recommendations and put in place a strategy for solving the myriad of deficiencies in the management system was a further serious failing on his part. It was also a serious failing on the part of Janice Wray, who knew as much as he did and on whom he relied. Clearly neither of them regarded fire safety as a high priority, even though the TMO had gone to the trouble and expense of commissioning the reports. | Withheld Information | Health and Safety | Robert Black
Dec 2013 further audit of TMO's Health and Safety department. Went from limited to satisfactory. | Compliance | Audit | KCTMO
The final report, dated Mar 2016, was a “high level audit review”. It did not identify any shortcomings in the TMO’s management of fire safety. It found that appropriate procedure and guidance documents existed covering fire safety policy and had recently been revised. It said that fire risk assessments were carried out by a specialist consultant and were reviewed by the TMO Assistant Safety Advisor during routine inspections to ensure that any significant findings and recommendations were pursued in a timely manner and in accordance with their stated priority. Checks on the electronic database relating to ten estates had confirmed that they were up to date and that all fire equipment had been inspected within the past twelve months. | Compliance | Audit | KCTMO
That finding failed to take account of the serious backlog of remedial work required by previous fire risk assessments that existed in the months before the final audit report. The TMO failed to correct the auditor’s mistake in thinking that all remedial work had been carried out in a timely manner and in accordance with their stated priority. None of the witnesses from the TMO could explain that failure. As a consequence, the audit report gave the misleading impression that there were no deficiencies in the TMO’s management of fire safety. Nor, once again, did the TMO take the opportunity to tell RBKC about the contents of Matt Hodgson’s reports or the systemic failings in its fire safety management he had identified. | Compliance | Audit | Hodgson Consultant
Chapter 38 Fire risk assessments
Janice Wray took responsibility for identifying which blocks should take priority, the procurement, commissioning the fire risk assessments and ensuring that progress met the LFB’s requirements. Valerie Sharples, and for a brief period Abigail Acosta, were the TMO’s project managers. Ann Muchmore, RBKC’s performance and contracts monitoring officer, had responsibility for overseeing the contract. | Compliance | Health and Safety | Janice Wray
At the start of the contract, Angus Sangster and Steve Reade of the LFB’s Fire Safety team met Janice Wray, Adrian Bowman and Abigail Acosta and Andrew Furness and Steve Wain of Salvus. Angus Sangster repeated the LFB’s requirements for the fire risk assessment programme, namely to have the entire property portfolio assessed within three years and to have the remedial work required for properties to be fully compliant with the Fire Safety Order completed within five years. | Compliance | Health and Safety | Fire Brigade
Carl Stokes started working for Salvus on 24 Sep 2009 on a six-month contract as a sub-contractor. No prior experience of residential blocks of flats 18 meters in height and less than two years' experience as a certified FRA. | Expertise | Health and Safety | Carl Stokes
FRA in relation to Grenfell Tower was completed on 30 Sep 2009 by Carl Stokes under the supervision of Andrew Furness. Fire risk assessment was subject to a quality control process and was reviewed by Andrew Furness on at least two occasions. It rated the overall risk for the building as “normal”, but identified 51 defects requiring remedial measures to reduce the risk. | Compliance | Health and Safety | KCTMO
Of those 51 defects, 19 were categorised as involving statutory breaches and were marked in red. Each defect was given a “priority rating” which identified the length of time within which it was recommended that action be taken to remedy it. Some of the measures required to remedy red defects, such as reviewing the evacuation procedure and confirming the policy and procedures for the operation of the smoke ventilation system, required action to be taken within one week. Other defects requiring remedial measures marked in red required the TMO to take action within three months or to agree a plan within six months. They included recommending that the TMO introduce and implement a system of formal checks on flat front doors to ensure that compartmentation remained fit for purpose. The assessment also recommended that the TMO engage competent engineers to test the smoke ventilation system and the lifts, if testing was not being carried out in accordance with current industry best practice. | Compliance | Health and Safety | KCTMO
February 2010 Janice Wray told Ann Muchmore that she had some concerns that Salvus were “very rule-bound” and that they had shown some reluctance to challenge the LFB on behalf of the TMO. She noted that Salvus was not as robust as she had hoped and that Carl Stokes, who had done most of the inspections as a sub-contractor, might be willing to tender for the work in future. Janice Wray felt that Salvus had not given her a clear indication on fire safety issues raised by the LFB and she wanted to know whether the course of action suggested by the LFB was required before she committed the budget. They decided to invite tenders for carrying out fire risk assessments in relation to the medium – and low-risk phases of the programme. | Compliance | Health and Safety | Janice Wray
Janice Wray’s message reveals that the TMO wanted a fire risk assessor that would take its side against the LFB when debating its fire safety requirements instead of taking them entirely at face value. Given that the LFB was the enforcing authority under the Fire Safety Order, that was a mistake. It also explains why Carl Stokes, who was ill-qualified to carry out fire risk assessments of buildings on this scale, let alone to hold the entire TMO portfolio, was selected by the TMO as the sole fire risk assessor and allowed to retain that role for the best part of seven years. | Compliance | Health and Safety | Janice Wray
Oct 2010 medium risk properties, Aug 2011 low risk properties. Carl Stokes appointed for both. | Compliance | Health and Safety | Carl Stokes
Procurement process for in 2010 decided on Carl Stokes, bears further examination. Carl Stokes, Salvas and three other companies invited for tender. | Procurement | FRA | Carl Stokes
Consultant appointed to be for 1 year with option for TMO to extend for a further year subject to Consultant's performance. | Procurement | FRA | Carl Stokes
Janice Wray could not explain why he had been conducting fire risk assessments for buildings in the TMO stock before the procurement process had started. She was adamant that she had not already decided to appoint Carl Stokes as the fire risk assessor and that it was to be a joint decision with RBKC. That may be so, but the episode does suggest that in some way Carl Stokes had an advantage in the procurement process. | Procurement | FRA | Carl Stokes
On 22 Jun 2010, Carl Stokes met Janice Wray. He sent her a letter the following day setting out the matters they had discussed, including employee fire training, personal emergency evacuation plans (PEEPs) and the lift maintenance policy for buildings over 18 metres in height. When he gave evidence he said that they had discussed the nature of the information that he would include in his fire risk assessments and their discussions were reflected in the assessments he subsequently produced. Carl Stokes could not explain the reason for that meeting. Janice Wray suggested that he had only been seeking more information about the organisation and its policies and procedures. She thought he had been trying to create a good impression. Ms Wray did not meet any of the other applicants, nor did she tell any of them that she had provided Carl Stokes with the information set out in the letter. | Procurement | FRA | Carl Stokes
Mr C Stokes, ACIArb, FPA Dip FP (Europe), Fire Eng (FPA), NEBOSH, FIA BS 5839 System Designer, Competent Engineer BS 5266, IFE Assessor/Auditor (FSO). 19 years Fire Safety experience with local Fire Authority, in enforcement and auditing roles, 3 years as an independent fire risk assessor. Member of the construction industry CPD certification Service. Professional Indemnity insurance cover provided by Hiscox. Enhanced C R B checked.” | Expertise | Health and Safety | Carl Stokes
Mr Stokes accepted in evidence that he had included that statement to lead the reader to think that he possessed the formal qualifications and professional body memberships set out in it. The purpose of including it was to advance his application to become the TMO’s fire risk assessor. | Expertise | Health and Safety | Carl Stokes
The statement was false in a number of respects. All but one of the qualifications referred to either did not exist or were irrelevant or meaningless. The only one that was valid and correctly stated was “ACIArb”, indicating he was an associate of the Chartered Institute of Arbitrators, which had no bearing on fire safety. Carl Stokes also claimed to hold an “FPA Dip FP (Europe)”, which, although incorrect in abbreviation, was intended to convey that he had completed the Diploma in Fire Prevention awarded by the Confederation of Fire Protection Association, as indeed he had. Carl Stokes was neither registered nor certificated by any professional or certification body as competent to carry out fire risk assessments. He suggested that the post-nominals were meant to evidence qualifications, training and experience required by the Fire Safety Order, but the fire safety training he had completed did not entitle him to invent qualifications and use them as he did in that statement. Mr Stokes accepted that he had known at the time that the statement was thoroughly misleading. | Expertise | Health and Safety | Carl Stokes
His claim that at the time he had carried out the fire risk assessment on 21 August 2010 he had been an independent fire risk assessor for three years was also false. In fact, he had begun work as an independent fire risk assessor only 11 months earlier on 24 September 2009. He accepted that the statement about the extent of his experience had been misleading. | Expertise | Health and Safety | Carl Stokes
We saw no evidence that Carl Stokes consistently undertook any formal training on an annual basis during the years he was employed as the TMO’s fire risk assessor and we conclude that he did not. | Expertise | Health and Safety | Carl Stokes
Janice Wray knew that Carl Stokes had elected not to join any professional bodies. When she raised it with him, he told her that he did not feel that he would gain anything from such memberships. | Expertise | Health and Safety | Carl Stokes
Janice Wray was aware of the FRACC Guide and was aware that Mr Stokes had chosen not to join any professional register, but she was not concerned. She thought that, as he had already demonstrated his competence in the work he had done for the TMO, the FRACC Guide did not demand that he be certificated. However, she thought it would apply to the appointment of any future fire risk assessor. | Expertise | Health and Safety | Carl Stokes
Stokes deliberately misleading description of his experience and qualifications demonstrate a lack of integrity and reliability on Mr Stokes’s part, but it is the failure of the TMO and RBKC to pay any serious attention to his supposed qualifications that represent the more serious failing, since it betrays a fundamental carelessness about fire safety matters in the housing stock for which they were responsible. | Expertise | Health and Safety | Carl Stokes
The consultants’ brief required applicants to demonstrate that they were able to satisfy the provisions of a quality management system in accordance with BS EN ISO 9001, but Carl Stokes was not required to satisfy that provision | Expertise | Health and Safety | Carl Stokes
Ms Wray’s approach was not in itself contrary to the Fire Safety Order, given that there is no requirement under article 9 for the responsible person to commission an independent fire risk assessment, nor for the person carrying out a fire risk assessment to be qualified or competent, but it did create a risk that the resulting fire risk assessment would not meet the statutory requirement of being suitable and sufficient. No good reason was given to justify the failure of the TMO and RBKC to require Mr Stokes to show that he could satisfy the provisions of an appropriate quality management system in accordance with the consultants’ brief. | Expertise | Health and Safety | Janice Wray
Nov 2010, Janice Wray reported to the Operations Committee the completion of the high-risk programme and the appointment of Carl Stokes as fire risk assessor for the TMO’s medium risk properties. She explained that he was willing to challenge the LFB if he considered its requirements to go beyond what it could reasonably require. Clearly, Mr Stokes’s willingness to be an advocate for the TMO in disagreements with the LFB was a material factor in the decision to appoint him. | Expertise | Health and Safety | Janice Wray
From Dec 2010 onwards, Carl Stokes carried out fire risk assessments for the TMO on its high-risk buildings. The TMO did not invite tenders for that work. Janice Wray believed she had taken advice from colleagues dealing with procurement, her line manager (Lornette Pemberton) and possibly RBKC before appointing Carl Stokes to review the fire risk assessments carried out the year before on high-risk buildings, but we have seen no evidence to support that. It had not originally been intended to appoint Carl Stokes to carry out that work but the need to review the assessments of the high-risk properties and the pressure of time led to a decision not to invite fresh tenders. Neither the TMO nor RBKC had established a programme for the regular review of the fire risk assessments on high-risk buildings at the conclusion of the first programme in Mar 2010. As a result, the need for the reviews had been overlooked and there was no proper recruitment or selection process. No written contract was entered into with Carl Stokes, who took over the work on an informal basis. Janice Wray could not recall whether the appointment had been approved by the TMO executive team or RBKC or how the funding for it had been obtained. The TMO simply drifted unthinkingly into a broader retainer of Carl Stokes without any formalities. | Procurement | Health and Safety | Janice Wray
Robert Black was aware that Carl Stokes had been retained but he did not know that his continued appointment had not been subject to a further procurement process. He had assumed that a formal procurement process of some kind had taken place and accepted that the failure to keep him informed pointed to a defect in the reporting processes and governance of the TMO. | Procurement | Health and Safety | Robert Black
That was not a proper or safe way for either the TMO or RBKC to seek to discharge their duties under the Fire Safety Order and it created a risk that the standard of the fire risk assessments produced as a result might not meet the statutory requirement | Procurement | Health and Safety | KCTMO
FRA required examining communal fire door as part of brief, fire risk assessor to focus on a building’s compartmentation (and any possible shortcomings), the operation and adequacy of fire doors, firefighting equipment and automatic detection and other systems, the means of escape, fire safety management systems and the overall fitness for purpose of the building in relation to fire safety. | Compliance | Health and Safety | KCTMO
LGA guide, types 1 to 4. | Compliance | Health and Safety | KCTMO
PAS 79 required to review any shortcomings in evacuation. | Compliance | Health and Safety | KCTMO
Dec 2016 and July 2017 Stokes provided training to the Estate Service Assistants | Expertise | Health and Safety | Carl Stokes
During the course of the refurbishment Stokes provided advice in relation to the smoke vents and lifts, rights of way to Grenfell Tower, the heating interface units, floor numbering and premises information boxes. | Expertise | Health and Safety | Carl Stokes
Carl Stokes does not appear to have taken any steps to find out whether the TMO had resolved, or planned to resolve, the statutory breaches identified in the Salvas report. We find that very surprising, given the widespread and significant failings identified by Salvus and the effect they must have had on the risk to the TMO’s properties. | Expertise | Health and Safety | Carl Stokes
We have concluded that when drawing up the latest fire risk assessment he had little information before him about which of the remedial measures he had recommended in his previous fire risk assessment had been completed and which had not and why. | Expertise | Health and Safety | Carl Stokes
Provided nothing had changed, Mr Stokes’s practice was to copy text from one fire risk assessment of Grenfell Tower to the next. He also copied text from fire risk assessments of other buildings. For example, in the fire risk assessment for Grenfell Tower dated 17 Oct 2014, he included some text referring to balconies taken from the assessment of another building, even though there were no balconies at Grenfell Tower. The passage was then repeated in his fire risk assessment dated 26 Apr 2016. Similarly, in section 11 of his fire risk assessments, he always included a passage headed “Pest control”. In the fire risk assessment for Grenfell Tower dated 17 Oct 2014 he reported on the condition of pigeon netting on the balconies, although there were no balconies on Grenfell Tower. That was simply lazy and careless and undermined the authority and quality of the fire risk assessment. Thoughtless drafting of that kind was bad enough, but it was aggravated by the fact that the same inapposite information was repeated in the fire risk assessments dated 26 Apr 2016 and 20 Jun 2016. Carl Stokes explained that the information had been repeated in those assessments because he knew that nothing had changed in relation to pest control and had not read the section again. He did not read through those fire risk assessments before sending them to the TMO, which Mr Todd described as very bad practice. We agree. | Expertise | Health and Safety | Carl Stokes
What is worse, nobody at the TMO noticed those inapposite observations that had clearly been transposed from fire risk assessments on other buildings. That strongly suggests that Janice Wray did not read the fire risk assessments with any degree of care. | Compliance | Health and Safety | Janice Wray
Carl Stokes included a section headed “Legal statement” in every fire risk assessment for Grenfell Tower. In it he told the recipient (in this case the TMO), among other things, that it did not have to give a copy to anybody, not even the fire authority, and that, if it did so, the document could be used against it at a later date. | Expertise | Health and Safety | Carl Stokes
Carl Stokes carried out fire risk assessments of Grenfell Tower on 29 Dec 2010, 20 Nov 2012, 17 Oct 2014, 26 Apr 2016 and 20 Jun 2016. In each case he identified the chief executive of RBKC as the responsible person, although he did not provide any of his assessments directly to RBKC. In fact, he had no contact with anyone at RBKC. | Expertise | Health and Safety | Carl Stokes
It was a significant failure on the part of the TMO not to monitor the quality of the work done by Mr Stokes as the sole provider of fire risk assessments for its portfolio of buildings. | Compliance | Health and Safety | KCTMO
PAS 7, 2013 states organisation should audit its fire risk assessment programme after fire risk assessments had been delivered and conduct review meetings at planned intervals to discuss the results of the audits. | Compliance | Audit | KCTMO
Robert Black never gave any thought to whether a sole trader could properly act as the fire risk assessor for 650 buildings. | Expertise | Health and Safety | Robert Black
Janice Wray said that, as far as she could remember, the LFB had never commented on fire risk assessments produced by Carl Stokes in such a way as to give the TMO any reason to doubt his competence or the quality of the assessments themselves. In fact, however, that was not the case. | Expertise | Health and Safety | Janice Wray
Concerns about Carl Stokes raised by LFB and LFB's Rebecca Burton raised this with TMO on a number of occassions. | Compliance | Health and Safety | Fire Brigade
May 2016, Rebecca Burton reported what had transpired in an email to her superior, Spencer Sutcliff, when discussing the review. She said that various areas of concern about fire risk assessments had been discussed with Janice Wray, including the assessor’s approach to self-closing devices on flat entrance doors generally, his claim that the LFB had agreed that self-closing devices were not required on flat entrance doors and the failure of his fire risk assessment to reflect an understanding of the strategy for the building and how occupants were to be kept safe in the event of fire. Although he is not mentioned by name, it is obvious that when she referred to the fire risk assessor she was referring to Carl Stokes. She went on to record that Janice Wray had agreed to consider each of those points and discuss with Mr Stokes what improvements could be made. | Compliance | Health and Safety | Fire Brigade
Barbara Matthews was also well aware of the LFB’s views about Carl Stokes’s fire risk assessments | Compliance | Health and Safety | Barbara Matthews
On 30 Nov 2015, Barbara Matthews had a telephone conversation with Rebecca Burton, during which they discussed the proposed enforcement notices for Adair and Hazlewood Towers. According to her note of the call, Barbara Matthews was told by Rebecca Burton that the fire risk assessments for Adair and Hazelwood Towers were not suitable and sufficient, that Carl Stokes had not considered the question of smoke ventilation and that his risk assessments were not comprehensive | Compliance | Health and Safety | Barbara Matthews
On 4 Dec 2015, Barbara Matthews wrote to the TMO board to provide a report on the Adair Tower fire. She said that the LFB had confirmed that it would serve enforcement notices in respect of Adair and Hazlewood Towers. She explained that the LFB had advised the TMO of what she called “key matters of concern”, specifically smoke ventilation and the absence of self-closing devices on flat entrance doors, but she made no reference to the direct criticism of Carl Stokes’s fire risk assessments that Rebecca Burton had made during their conversation on 30 Nov 2015, less than a week earlier. Nor, strikingly, did she refer to the service of the deficiency notice in relation to Adair Tower on 12 Oct 2015, a point which is considered elsewhere in this report. | Compliance | Health and Safety | Barbara Matthews
Her failure to do so was consistent with the desire of Robert Black and the executive team as a whole to keep any bad news about fire safety away from the board | Compliance | Health and Safety | Barbara Matthews
Rebecca Burton again raised her concern about Carl Stokes with the TMO at their bi-monthly meeting on January 2016. | Compliance | Health and Safety | Fire Brigade
On 31 March 2016 there was a meeting of the TMO board at which Barbara Matthews described the progress of the enforcement notices relating to Adair and Hazlewood Towers. At the meeting, Jeff Zitron, a board member nominated by the council, asked why enforcement notices had been issued, given that at the time of the fire the TMO had valid fire risk assessments. Sacha Jevans responded, telling the board that enforcement notices had been served despite the fact that Carl Stokes had not identified any problems when carrying out his fire risk assessment, and that the LFB had identified none either when it carried out its fire audit. That was wrong and misleading. In fact, the LFB had served a deficiency notice relating to Adair Tower on 12 Oct 2015, about 2 weeks before the Adair Tower fire, which had identified contraventions of Articles 11, 17(1) and 8 of the Fire Safety Order | Compliance | Health and Safety | Sasha Jevans
We have already commented on this and other examples of the TMO’s executive officers misleading the board or failing to disclose to it material matters relating to fire safety. The result in this particular case was that Mr Zitron did not get a straight answer to his question but it was a question that the TMO ought to have asked itself instead of resorting to deflection and concealment. | Compliance | Health and Safety | Sasha Jevans
In June 2016, Janice Wray and Barbara Matthews produced the TMO’s Health & Safety Report for the period 1 Apr 2015 to 31 Mar 2016. In the section relating to fire risk assessments, it said that suitable and sufficient fire risk assessments were in place which had been produced in accordance with best practice as set out in PAS 79. No mention was made of the concerns raised by Rebecca Burton in Nov 2015 and Jan 2016. Janice Wray was unable to explain that omission. Yet again, the board of the TMO was kept in the dark about concerns expressed by the enforcing authority about the quality of the TMO’s fire risk assessments. That was a particularly important matter for the board to know because it put the TMO, and indirectly the members of the board, at risk of incurring liability for breach of the Fire Safety Order, which carried serious sanctions. | Compliance | Health and Safety | Barbara Matthews
The report referred to the TMO’s intention to procure a new contract for fire consultancy and fire risk assessment services. Janice Wray and Barbara Matthews both denied that that had been prompted by criticisms of Carl Stokes’s work. In the event, the procurement manager apparently did not think that a new contract was required at that time and no steps were taken to obtain one. The subject was not discussed further by the TMO’s Health and Safety Committee, the executive team or the board. | Procurement | Health and Safety | Barbara Matthews
Chapter 39 Response to Fire Risk Assessments
Article 9(6) of the Fire Safety Order requires the responsible person to record certain information, including the significant findings of the assessment and the measures which have been or will be taken by that person pursuant to the order. | Compliance | Health and Safety | KCTMO
The edition of PAS 79 relevant to the fire risk assessments carried out in relation to Grenfell Tower by Carl Stokes (other than that carried out in December 2010) was PAS 79:2012. | Compliance | Health and Safety | Carl Stokes
Clause 19 of PAS 79:2012 provided guidance on the formulation of an action plan. It recommended that every documented fire risk assessment should incorporate an action plan such as to ensure that, if implemented, it would reduce the fire risk to, or maintain it at, a tolerable level. | Compliance | Health and Safety | KCTMO
Pro forma reports exist from PAS 79 for the Fire Risk Assessor. | Compliance | Health and Safety | KCTMO
In contrast to the pro forma at Annex E of PAS 79:2012, Carl Stokes’s form did not contain a section for the assessor to record any actions that had not been completed since the last inspection, nor did it contain an indication of the level of risk to the premises once the actions identified had been completed. | Compliance | Health and Safety | Carl Stokes
However, we doubt that he did in fact adopt an approach of schedule of significant findings produced following previous visit, which he would use as a starting point to ensure that all the points raised had been dealt with. Although the annotated copies of his significant findings and action plans for Grenfell Tower made in Oct 2014 and Apr 2016 contain his manuscript annotations, there is no reference in any of his fire risk assessments or action plans to any outstanding (or indeed, completed) work that he had identified as necessary during a previous assessment. | Compliance | Health and Safety | Carl Stokes
TMO therefore had no reliable or comprehensive record of what remedial work Mr Stokes thought it particularly important to complete. | Compliance | Health and Safety | Carl Stokes
Janice Wray’s responsibility to allocate the remedial work to the appropriate team in the TMO. | Compliance | Health and Safety | Janice Wray
Carl Stokes had to rely for information about the maintenance and servicing of equipment on records printed out for him by the TMO Maintenance Department or Janice Wray. | Compliance | Health and Safety | Carl Stokes
Carl Stokes had access to the Keystone system by the time he carried out the fire risk assessment in April 2016, as he recorded in that assessment that he had checked the Keystone records in relation to certain items. | Compliance | Health and Safety | Carl Stokes
Keystone did not contain maintenance and servicing records for some equipment that was critical to fire safety. In particular, it did not contain maintenance and servicing records for the fire control system, dry rising fire main or emergency lighting system at Grenfell Tower. Carl Stokes told us that if he could not obtain information for himself, he asked the TMO for the information he needed. | Compliance | Health and Safety | Carl Stokes
However, we doubt that he was consistently conscientious in doing so and his requests for information were patchy. Paul Steadman, who was the estates services assistant (ESA) for Grenfell Tower at the relevant time, had no recollection of having been consulted by Carl Stokes in relation to a fire risk assessment, despite the fact that Mr Stokes recorded having consulted him by name in connection with the fire risk assessments for Grenfell Tower carried out in 2010, 2012, and 2014. Moreover, Mr Stokes was never given access to the W2 system and was therefore unable to check for himself whether actions which had been identified during his previous visit to a property had been completed. He said that he had been forced to rely on documents printed out by Janice Wray, but if that was so, it is surprising that they were not mentioned in his fire risk assessments. | Compliance | Health and Safety | Carl Stokes
PAS 79 of remedial work "immediate", "short term", "long term", also a "medium term." | Compliance | Health and Safety | KCTMO
Carl Stokes combined risk and urgency together which was not ideal. Did not contain form of overall assessment of risk. | Compliance | Health and Safety | Carl Stokes
Carl Stokes extended time for remedial works needed for medium and low risk but no guidelines sources could be identified as to support him doing this. | Compliance | Health and Safety | Carl Stokes
Dr Lane considered it to be entirely incorrect for extending time and Stokes belief of companies experiencing issues with capital investment. | Compliance | Health and Safety | Carl Stokes
We think that Carl Stokes’s unusual and potentially dangerous approach to the completion of remedial work from 2014 onwards probably had little or no effect on how the TMO dealt with the work in practice | Compliance | Health and Safety | Carl Stokes
Peter Maddison sought to wish to divide the remedial measures into categories or sub-categories of priority action. | Compliance | Health and Safety | Peter Maddison
Peter Maddison asked Janice Wray which of the actions could be defined as absolute requirements and which were best practice. | Compliance | Health and Safety | Peter Maddison
Peter Maddison in which he suggested that it would be useful to have more information about priority levels and the nature of each outstanding action. Janice Wray agreed to “split the outstanding actions into high, medium and low categories with targets”. | Compliance | Health and Safety | Peter Maddison
Nov 2015 for Adair Building, Peter Maddison sent an email to Sacha Jevans, Janice Wray, Robert Black, Alex Bosman and Daniel Wood at 07:45 in which he questioned Carl Stokes’s assignment of a high priority rating to the recommendation that self-closing devices be fitted. He explained that he did not consider that to be justified because it was not a statutory requirement to install self-closing devices retrospectively and because the entrance doors of the leasehold flats were demised to the leaseholders. The proposed action plan would therefore require the TMO to carry out work that it could not require the leaseholders to undertake. Peter Maddison could not remember how he had gained the understanding that there was no statutory requirement to fit self-closing devices. In his email he went on to express his concern that committing itself to carrying out work that it did not have the power to undertake would leave the TMO exposed. He suggested that the priority be reduced to “low” or “advice” and that a note be added that the TMO could not enforce the requirement in relation to leasehold properties. | Compliance | Health and Safety | Peter Maddison
Peter Maddison’s view was supported by Barbara Matthews and Robert Black. Surprising given that LFB were concentrating on self closing devices. | Compliance | Health and Safety | Robert Black
The TMO, in full knowledge of risks involved, persuaded him to downgrade an important aspect of his assessment in relation to a building in which a serious fire had already occurred and in respect of which the LFB was already considering enforcement action. Altering at request of client not professional of a competent FRA. | Compliance | Health and Safety | Carl Stokes
TMO behaviour in seeking to challenge and dilute Mr Stokes’s risk assessment, not for the first time, suggests that the TMO treated the demands of managing fire safety as an inconvenience rather than an essential aspect of its care for those living in the buildings under its management. It was a betrayal of its statutory obligations to its tenants. | Compliance | Health and Safety | KCTMO
By January 2012, therefore, the TMO was at least 12 months behind in completing some of the remedial work. By December 2012 a significant amount of work was outstanding, which was causing concern. | Compliance | Health and Safety | KCTMO
Backlog identified by Hodgson's report of 900-1000, limited actions. Subsequent report by Hodgson did not mention backlog. At no time does the TMO Health and Safety Committee or the executive team appear to have considered the risk to life presented by the arrears. | Compliance | Health and Safety | Hodgson Consultant
Less details and stats provided in Jan 2016 than Nov 2015 to committee. | Compliance | Health and Safety | KCTMO
No evidence of any interim measures for high risk actions required. | Compliance | Health and Safety | KCTMO
TMO executive team never reported to the board on the need for remedial work or the extent of the delay in carrying it out. That is consistent with its failure to report to the board other matters of importance to fire safety. Barbara Matthews said that the only health and safety matters referred to the TMO board were those which had been included in the annual health and safety report or exceptional items, such as matters to do with the enforcement notice served following the fire at Adair Tower. As a result, the board lacked the information it needed to perform its function. It did not know whether the TMO was complying with its statutory duties and did not have the information it needed to make decisions that might enable its management to eradicate the arrears of remedial work | Compliance | Health and Safety | Barbara Matthews
No trends identified in Fire Assessment program even though recommended by an audit to do this. | Compliance | Health and Safety | KCTMO
At many points in her evidence Janice Wray blamed a lack of money for her failure to act in a more efficient and effective way, but the evidence does not enable us to reach any firm conclusion on that question. | Compliance | Health and Safety | Janice Wray
Robert Black was unsure whether the TMO had a specific budget or sub-budget line item for health and safety, and agreed that the TMO “probably” did not have a line item within the general budget to cover remedial work identified in fire risk assessments. | Compliance | Health and Safety | Robert Black
Barbara Matthews told us that there had been a specific budget to enable the TMO to meet its health and safety obligations. Although the budget was restricted, if there had been specific demands which could not be managed within the existing budget, it would have approached RBKC for additional funds. She could not recall any occasion on which RBKC had refused a request for additional funds. However, it had not occurred to her to approach RBKC to obtain funding for additional staff to support Janice Wray because she had felt that she might not have been able to make a strong enough case. She thus appears to have adopted a degree of self-restraint when considering whether to ask RBKC for more funds. By contrast, Janice Wray was under the impression that no additional funding was available | Compliance | Health and Safety | Barbara Matthews
We do not consider that we have enough information about the TMO’s finances or the extent to which RBKC was willing to make additional funds available to it to be able to reach a reliable conclusion on that question. | Compliance | Finance | KCTMO
Carl Stokes not considered arrears of remedial works or effectiveness of fire management system. | Compliance | Health and Safety | Carl Stokes
Carl Stokes could not tell how long individual deficiencies had remained outstanding. That was particularly important when assessing the extent to which the risk to residents was affected by arrears of remedial work. However, Carl Stokes was aware that the TMO was not completing remedial work within the recommended times. | Compliance | Health and Safety | Carl Stokes
Chapter 40 Replacement of Entrance Doors
A survey of fire safety features of entrance doors conducted by Rand Associates across the whole of the TMO’s housing stock completed in October 2010 found that a significant proportion of entrance doors did not have fire safety features and in particular did not have the necessary 30 minute fire resistance | Compliance | Health and Safety | KCTMO
TMO procured replacement doors through the London Housing Consortium, a social housing procurement company with a framework agreement for external doorsets. Following a competition, Manse Masterdor’s tender was accepted by the TMO’s Operations Committee on 22 February 2011. | Compliance | Health and Safety | KCTMO
It appears that no fire resistance tests were carried out in accordance with the standard because the test certificates show that the doorset was tested on one side only and not, as required, on both sides. There is no evidence that the door was tested for smoke leakage as required by BS 476-31. | Compliance | Health and Safety | KCTMO
Dr Lane and her team examined many of the entrance doors to the flats in Grenfell Tower after the fire for the purposes of Phase 1 of the Inquiry and in Annex I of her report she identified numerous discrepancies between the construction of the doors fitted to the flats and the construction of the door that had been subjected to testing. We accept her evidence, from which it follows that in many, if not all, cases the doors installed under the replacement programme did not satisfy the requirements of Approved Document B for that reason also. | Compliance | Health and Safety | Dr Lane
The tender documents required that the doors be “Security/30 min fire doors”, but despite the clear requirements of Approved Document B, they did not specify that the doorsets should be rated FD30S, nor did they expressly require the inclusion of cold smoke seals or confirmation that cold smoke leakage testing had been carried out. The documents did require fire test certification to be provided on request, but there was no similar requirement in relation to cold smoke leakage. | Compliance | Health and Safety | KCTMO
Although it is unclear whether the TMO received copies of the certificates relating to tests carried out in accordance with BS 476-22, no one took any steps to check whether the doors supplied corresponded to the test certificates available. | Compliance | Health and Safety | KCTMO
Carl Stokes made no reference to the requirement for doors to be tested for cold smoke leakage. Clearly unaware of the requirement for entrance doors to flats on protected corridors to have been tested for cold smoke leakage to the standard set out in BS 476-31. | Compliance | Health and Safety | Carl Stokes
Carl Stokes did not tell the TMO that entrance doors to flats should be tested for cold smoke leakage and his advice led Janice Wray to understand that, if doors had been tested for fire resistance for 30 minutes and had self-closing devices and smoke seals, they were FD30S doors. | Compliance | Health and Safety | Carl Stokes
The TMO’s invitation to tender did not specify, as it should have done, that FD30S doors were required. Responsibility for that omission lies squarely with the TMO, which should have taken effective steps to make sure that it was procuring entrance doors that met the required standards. However, conditions on the night of 14 June 2017 were such that even a door rated FD30S would have provided little protection to the lobbies or the occupants of any of the flats. | Compliance | Health and Safety | KCTMO
Chapter 41 Inspection and Maintenance of Entrance Doors
On the night of the Grenfell Tower fire many of the self-closing devices on the front doors of flats in the block failed to work effectively and some were entirely missing. As a result, many doors remained open when the occupants left, allowing smoke to enter the lobbies, which quickly became smoke-logged. The absence of effective self-closing devices was therefore an important cause of the inability of many occupants to escape the tower at a time when the stairs were relatively free of smoke. It represents a serious defect in the management of the building in relation to fire safety. | Compliance | Health and Safety | KCTMO
Under article 17(1) of the Fire Safety Order the responsible person must ensure that any equipment or devices provided in respect of the premises under the order are subject to a suitable system of maintenance and are maintained in efficient working order and good repair where necessary in order to protect the safety of relevant persons. | Compliance | Health and Safety | KCTMO
Janice Wray was therefore aware by 30 April 2011, if not before, that entrance doors needed to be fitted with self-closing devices and that residents might remove or disconnect them. | Compliance | Health and Safety | Janice Wray
Shortly after Manse Masterdor began installing new entrance doors in March 2011, two problems began to emerge with the concealed self-closing devices fitted to them. One was a mechanical fault in the self-closing device which prevented the door from closing or which caused it to become stuck in the closed position. That appears to have been caused by a defect in the fixings connecting the self-closing device to the door and the doorframe. | Compliance | Health and Safety | KCTMO
The other was that the self-closing devices were too strong for some residents, particularly those who were elderly or frail, who had difficulty opening and closing their doors. The evidence suggests that both problems were inherent in the design or manufacture of the doorsets rather than the result of defective installation. However, whether the problem was one of design, manufacture or installation, doors were proving difficult to open easily and the solution adopted by many, including the TMO’s repair staff, was to remove the self-closing devices, even though they were an important fire safety measure. | Compliance | Health and Safety | KCTMO
On 17 May 2011, Andy Webster, a project manager for Manse Masterdor, sent an email to fellow employees Paul Birkett and Richard Moore about the entrance doors being installed for the TMO in which he referred to a defect in concealed self-closing devices that prevented doors from closing. He recognised that the doors should not have left the factory in that state. | Compliance | Health and Safety | Manse Masterdor
It is clear, however, that Manse Masterdor did not tell the TMO about the problem. | Compliance | Health and Safety | Manse Masterdor
It is clear that from the outset inadequate screws and fixings presented a systemic problem in relation to self-closing devices on the new entrance doors throughout the TMO stock, as the TMO knew. | Compliance | Health and Safety | KCTMO
At Grenfell Tower, the vast majority of the new entrance doors had been installed by the end of June 2011. Unless Manse Masterdor returned to change them, therefore, they retained the original fixings and did not have the larger screws and fixings that the factory apparently used from July 2011 onwards. There is in fact no evidence that Manse Masterdor replaced the fixings of the self-closing devices on any of the new entrance doors. | Compliance | Health and Safety | Manse Masterdor
Carl Stokes also assumed that the problem had been cured. He did not carry out any checks at the time or investigate whether the problem had been satisfactorily resolved when he carried out his next fire risk assessment at Grenfell Tower in November 2012. | Compliance | Health and Safety | Carl Stokes
Whatever steps Manse Masterdor took to cure the problem, it is reasonably clear that it persisted, at least at Grenfell Tower, which may explain why so many self-closing devices were defective or missing on 14 June 2017. | Compliance | Health and Safety | Manse Masterdor
June 2014 FRA by external assesssor said about lack of self closing mechanism, no action taken by TMO. | Compliance | Health and Safety | KCTMO
TMO did not have a system for the regular inspection and maintenance of entrance doors that might have revealed that self-closing devices at Grenfell Tower were missing or defective and prompted their replacement before the fire. | Compliance | Health and Safety | KCTMO
Salvus Management Report, dated 22 September 2009, identified the absence of adequate inspection and monitoring of premises and facilities as a hazard. It specifically identified that the monthly safety inspection did not include any formal checks on fire doors and contained a strong recommendation that the inspection sheet be revised to include formal checks on fire doors. Salvus advised that needed to be done within a month to remedy what it considered to be a breach of the TMO’s statutory obligations. | Compliance | Health and Safety | Salvas Consultant
November 2012, representatives of the LFB, the TMO, RBKC and the London Borough of Hammersmith and Fulham met to discuss responsibility for enforcing the law against leaseholders whose entrance doors were not adequately fire-resisting. | Compliance | Health and Safety | Fire Brigade
TMO’s fire safety strategy, which was completed in November 2013, did not contain the arrangements for complying with important aspects of the Fire Safety Order, including the inspection and maintenance of entrance doors to flats and self-closing devices. Janice Wray drafted with help from Carl Stokes. | Compliance | Health and Safety | Carl Stokes
Inspection checklist covered only communal fire doors and chute room doors, not the entrance doors to flats. | Compliance | Health and Safety | Carl Stokes
Made no provision for a system of regular inspection and maintenance of entrance doors and self-closing devices. | Compliance | Health and Safety | KCTMO
No evidence that before the TMO completed its fire safety strategy it gave any consideration to Mr Jack’s suggestion at the meeting on 8 November 2012 that regular inspections of self-closing devices might be combined with the annual gas safety check. | Compliance | Health and Safety | KCTMO
Janice Wray accepted that the LFB had not approved it in the past. None of that is surprising. The TMO’s approach inevitably led to irregular and infrequent inspections of the entrance doors to flats and so was inconsistent with both the LGA Guide’s recommendation for six-monthly inspections and the advice given by Andy Jack in November 2012, which Janice Wray had already accepted. | Compliance | Health and Safety | Janice Wray
Policy was inadequate because it did not ensure that entrance doors were inspected on a regular and systematic basis. It could be many years before a property changed hands and was inspected. | Compliance | Health and Safety | KCTMO
Policy of inspecting the entrance door to a flat when major work was carried out was similarly inadequate, because it did not ensure regular inspection. | Compliance | Health and Safety | KCTMO
We have seen no evidence of any such discussions until after the Adair Tower fire on 31 October 2015. We consider that her frequent references to budget restrictions as a reason for not taking necessary action across the TMO estate in relation to fire safety were based on an assumption that any request for further funds would be refused. Neither she nor anyone else appears to have made any serious effort to obtain additional resources. | Compliance | Finance | Barbara Matthews
Both before and after the fire at Adair Tower on 31 October 2015 the LFB fire safety team raised concerns with the TMO about its approach and that of Carl Stokes to ensuring that self-closing devices were fitted on entrance doors to flats. | Compliance | Health and Safety | Carl Stokes
In early September 2015, the LFB fire safety team identified during an inspection that the entrance door to Flat 41 at Adair Tower, which had not been replaced as part of the replacement programme, did not have a self-closing device. They also discovered that in his fire risk assessment of Adair Tower dated 20 February 2014 Carl Stokes had advised that self-closing devices were “not applicable” and that, although entrance doors to flats were not fitted with self-closing devices, he had not identified their absence as a concern and had not assessed the consequent risk or recommended remedial action. On 12 October 2015, the LFB issued a deficiency notice to the TMO in respect of Adair Tower based on the absence of self-closing devices. | Compliance | Health and Safety | Carl Stokes
Janice Wray suggested that she had understood from Carl Stokes that the LFB accepted that self-closing devices were not required on “nominal” doors, despite the fact that the LGA Guide said that all entrance doors to flats and any doors leading onto a protected escape route needed to have a self-closing device. | Compliance | Health and Safety | Carl Stokes
Andy Jack said in evidence that he had been shocked by the suggestion. He was also shocked that Carl Stokes, as a former fire safety officer, should have thought that entrance doors did not need to be self-closing. Nicolas Comery was similarly clear that there had been no such agreement. We accept their evidence about that each of them effectively denied that they had agreed that entrance doors did not need to be self-closing. | Compliance | Health and Safety | Carl Stokes
December 2015, the LFB fire safety team served an enforcement notice on the TMO in respect of Adair Tower and sent a copy to RBKC. They included a failure to carry out a suitable and sufficient fire risk assessment for the purposes of Article 9 because the assessment carried out by Carl Stokes did not give adequate consideration to existing and required standards for self-closing devices. They also included a failure to maintain the fire resistance of the protected route because none of the doors that opened onto it were fitted with positive-action self-closing devices. The LFB issued another enforcement notice on 18 January 2016 in respect of Hazlewood Tower (Adair Tower’s sister block) which included essentially the same alleged breaches in relation to self-closing devices. | Compliance | Health and Safety | Carl Stokes
April 2016, Janice Wray circulated papers for the TMO Health and Safety Committee meeting on 12 April 2016. They included a paper dated 4 April 2016 entitled “Review of the Fire Safety Strategy”, in which she said that it was time to review the strategy to make sure that the TMO’s policies complied with the relevant legislation and the LFB’s advice, guidance and requirements. However, for reasons which are not apparent, she did not invite the committee to consider the matters she had discussed with Rebecca Burton on 5 January 2016, namely, the need to install self-closing devices on all entrance doors and to put in place a system for the regular inspection and maintenance of self-closing devices. | Compliance | Health and Safety | Janice Wray
Mr Swindells emphasised the obligation imposed on the responsible person by Articles 11 and 17 of the Fire Safety Order to monitor and maintain fire safety systems and suggested that residents should be reminded that the device was there to protect both them and their neighbours for Lonsdale House. | Compliance | Health and Safety | Fire Brigade
Janice Wray could not explain the delay other than by saying that complying with the enforcement notices for Adair Tower and Hazlewood Tower had been time-consuming work. Given the obvious importance of the matter, that is scarcely a sufficient explanation. | Compliance | Health and Safety | Janice Wray
It is clear that Laura Johnson was not persuaded of the need to install self-closing devices over a three-year period. The minutes make that clear. Although she was right to have in mind the need to balance the expense of the proposed programme against the risks involved, her decision failed to give sufficient weight to the advice of the LFB and the nature of the risk that self-closing devices were intended to mitigate. | Compliance | Finance | Laura Johnson
November 2016, the LFB issued a deficiency notice to the TMO in respect of Grenfell Tower on the grounds that the protected escape route (corridors, lobbies and stairs) was compromised by doors that did not have self-closing devices. It also identified the doors to Flats 44 and 153 as having failed to close themselves when inspected It recommended that the deficiencies be remedied by 18 May 2017. The deficiency notice thus informed the TMO of its obligations in respect of the installation and maintenance of self-closing devices and the urgency with which they needed to be discharged. | Compliance | Health and Safety | Fire Brigade
Laura Johnson accepted that her message amounted to, or at least was interpreted by the TMO as, a direction to extend the period over which the installation programme was to be carried out and to not establish an inspection regime. The TMO did not resist. In effect, therefore, she alone decided that the installation programme should be extended. She did so without having taken any advice about the consequences for the safety of residents. She effectively accepted that financial considerations were the principal, if not sole, basis for her decision. | Compliance | Finance | Laura Johnson
It is evident from the email Laura Johnson sent to Barbara Matthews on 6 Mar 2017 that money again was the driving force behind her refusal to introduce a system of inspection and maintenance. | Compliance | Finance | Laura Johnson
The evidence indicates that neither RBKC nor the TMO fully informed the Housing Property and Scrutiny Committee (“the scrutiny committee”) about the position in respect of the installation and inspection of self-closing devices after the Adair Tower fire and before the Grenfell Tower fire. The evidence also indicates that, to the extent that the scrutiny committee was made aware of the LFB’s concerns about self-closing devices, it did not take adequate steps to investigate why those concerns had arisen or to ensure that RBKC and the TMO had adequately addressed them. | Compliance | Health and Safety | KCTMO
We have seen no evidence that the scrutiny committee took steps at that point to find out how the problems with self-closing devices had arisen, particularly in the light of the replacement of entrance doors only a few years earlier and the continuing programme of fire risk assessments. We find that lack of curiosity surprising. | Compliance | Health and Safety | KCTMO
In her report for the scrutiny committee meeting on 16 November 2016, Laura Johnson said that the works required by the Adair Tower and Hazlewood Tower enforcement notices had been completed. However, she did not refer to the need to install and inspect regularly self-closing devices across the whole of the housing stock, although by that point she had begun discussing that with the TMO. Nor were they mentioned in the TMO’s Mid Year Review of Performance which had been prepared for that meeting. Laura Johnson and Barbara Matthews attended the meeting. There is no record of any fire safety matters having been raised by either of them. | Compliance | Health and Safety | Laura Johnson
No evidence that the scrutiny committee were ever informed about the deficiency notice the LFB issued in respect of Grenfell Tower dated 17 November 2016 and the concerns it identified in relation to the maintenance of self-closing devices before the Grenfell Tower fire. | Compliance | Health and Safety | KCTMO
At the scrutiny committee meeting on 4 May 2017, following the fire at Trellick Tower on 19 April 2017, Councillor Mackover and Councillor Pascall expressed concern about the TMO’s approach to the installation of fire doors on properties owned by leaseholders. The scrutiny committee had not been briefed about the decision only a month or so earlier to spread the installation of self-closing devices over a period of five rather than three years and not to introduce a system of regular inspection and Laura Johnson did not draw it to their attention. | Compliance | Health and Safety | KCTMO
The minutes of a TMO executive team meeting on 17 May 2017 recorded that at the meeting of the scrutiny committee on 4 May 2017 Councillor Mackover had criticised the TMO’s approach to fire doors but that Laura Johnson had made it clear that RBKC did not want the TMO to inspect the front doors of flats. | Compliance | Health and Safety | Laura Johnson
Laura Johnson sent an email to Robert Black the following day in response to a question he had asked about the nature of Councillor Mackover’s concern and whether he should contact him. She said that it related to the entrance doors of leaseholders’ flats and that there was nothing in it. She recommended not contacting him. She thought that a section in the annual report would be sufficient. Robert Black agreed. | Compliance | Health and Safety | Robert Black
It is evident, therefore, that the scrutiny committee was not told about the decisions that had been made, principally by Laura Johnson, about the installation and inspection of self-closing devices before the Grenfell Tower fire. | Compliance | Health and Safety | Laura Johnson
TMO’s repair records for Grenfell Tower reveal no discernible system for giving repairs to fire doors priority over other matters. | Compliance | Health and Safety | KCTMO
Those sent to carry out repairs to self-closing devices at Grenfell Tower between 2011-2013 often simply removed them, so that doors could be opened and closed freely, but did not replace them. In the period up to 14 June 2017 Repairs Direct staff continued on occasions to remove, or offer to remove, self-closing devices or failed to identify the need to replace them when carrying out repairs to entrance doors. That occurred at Flat 26, Flat 45, Flat 126, Flat 131 and Flat 135. | Compliance | Health and Safety | KCTMO
At each of those flats the self-closing device was found to be missing on 14 June 2017, apart from Flat 26 where the resident had refused the Repair Direct workman’s offer to remove it. In our view that is indicative of a broader failure by the TMO to ensure that those carrying out repairs fully understood the importance of effective self-closing devices and ensured that repairs did not undermine the protection offered by the doors. | Compliance | Health and Safety | KCTMO
Salvus and the TMO had agreed in late 2009 at the start of programme of assessing high-risk buildings that its fire risk assessors would inspect a sample of the entrance doors to flats during each of their assessments, although they did not agree a specific number or percentage of doors to be inspected. When Carl Stokes was engaged by the TMO to assess medium-risk buildings in September 2010, it does not appear that he and Janice Wray discussed the need to inspect a sample of doors but they both clearly proceeded on understanding that he would. That expectation was ultimately recorded in the TMO’s fire safety strategy dated June 2017. | Compliance | Health and Safety | Carl Stokes
Carl Stokes 5% target of inspecting entrance doors was barely enough as part of his sample inspection strategy. In the course of four fire risk assessments he carried out at Grenfell Tower between November 2012 and June 2016 Carl Stokes identified defects in only four entrance doors. Did not look at inside of doors and his approach was fortuitous rather than planned. | Compliance | Health and Safety | Carl Stokes
Carl Stokes’s failure to identify defects on the inside of doors, particularly defective and missing self-closing devices, is in stark contrast with what others who carried out sample inspections of entrance doors at Grenfell Tower found. Leon Taylor, who carried out a sample inspection of entrance doors in the course of a fire risk assessment on 14 June 2014 found at least three self-closing devices missing, whereas Carl Stokes, who carried out a fire risk assessment on 17 October 2014, did not find any self-closing devices missing. Michelle McHugh, of the LFB fire safety team, carried out an inspection of a sample of entrance doors during her audit of Grenfell Tower on 26 October 2016 and found that three self-closing devices were defective, but Carl Stokes did not find any devices missing during his fire risk assessments in April and June 2016 or during an inspection he carried out on 18 October 2016, only a week or so before Ms McHugh. | Compliance | Health and Safety | Carl Stokes
Given the number of self-closing devices that were found to be missing or broken after the fire (some 77 out of 120), and in the light of Leon Taylor and Michelle McHugh’s findings, we think it likely that, if Carl Stokes had inspected both the inside and outside of a representative sample of entrance doors during his fire risk assessments, he would have discovered a significant number of missing or defective self-closing devices. Accordingly, we think it unlikely that he did routinely inspect the inside of doors. | Compliance | Health and Safety | Carl Stokes
Carl Stokes kept no record of which flats he had visited or tried to visit as part of his fire risk assessments or of the results of any such inspections, except in relation to the four defects he identified in his action plans. | Compliance | Health and Safety | Carl Stokes
In each of his fire risk assessments Carl Stokes stated that the entrance doors to the flats had recently been replaced with new self-closing 30-minute fire doors but he did not say that he had inspected a sample of entrance doors. Further, in his contemporaneous notes of the fire risk assessment he carried out on 20 June 2016, he recorded only the defects that he had identified on the outside of the door to Flat 24 and on the open door to Flat 112. He did not include a note of any other flats he had sought to enter, nor what he had found. That has left us in some doubt whether he did, in fact, inspect a representative sample of entrance doors during any of his fire risk assessments. | Compliance | Health and Safety | Carl Stokes
If he could not gain access to enough flats to inspect a representative sample of doors, he ought to have told Janice Wray so that she could arrange access for him. | Compliance | Health and Safety | Carl Stokes
Carl Stokes also failed to record in his fire risk assessments for Grenfell Tower problems that he knew existed in relation to self-closing devices. | Compliance | Health and Safety | Carl Stokes
We have seen no evidence that Carl Stokes ever considered the TMO’s arrangements for the inspection and maintenance of entrance doors to flats, whether as part of his fire risk assessments or otherwise, much less that he advised it that they were inadequate. When he was asked to comment on the draft strategy in early 2013, he did not tell Janice Wray that it needed to include arrangements for the inspection and maintenance of entrance doors, although the LGA Guide recommended inspections every six months and Andy Jack had referred to the need for regular inspection in the course of their conversation on 8 November 2012. | Compliance | Health and Safety | Carl Stokes
We have seen no evidence that Carl Stokes ever drew Janice Wray’s attention to the recommendation in the LGA Guide, although she said she had been aware of it. Nor did he mention it in his letter of 30 April 2011 when he drew her attention to other provisions of the draft LGA Guide which could adversely affect the replacement of doors, including the risk of residents’ removing self-closing devices. He also failed to draw it to her attention after the Adair Tower fire when there were discussions about the approach the TMO should take to self-closing devices, of which he appears to have been aware. | Compliance | Health and Safety | Carl Stokes
Chapter 42 Fire Safety Information
TMO responsible for measures of escape. Procedures for if fire occurred. | Compliance | Health and Safety | KCTMO
TMO stay put strategy. | Compliance | Health and Safety | KCTMO
Tower before cladding was entirely of concrete and non combustible. | Compliance | Health and Safety | KCTMO
No fire safety action notices. | Compliance | Health and Safety | KCTMO
Handbooks stock ran out in 2008 or 2009. | Compliance | Health and Safety | KCTMO
Janice Wray told Health and Safety Committee that residents received fire safety info in handbook but by March 2013 new handbook not likely finalised. | Compliance | Health and Safety | Janice Wray
In 2017 handbook not produced, not even in 2013 as part of Fire Safety Strategy. | Compliance | Health and Safety | KCTMO
TMO's Emergency Plan depended on great extent for residents being aware of what to do in emergency, denied residents this as per no handbook. | Compliance | Health and Safety | KCTMO
Matter of chance if tenants saw letter about fire safety as part of viewings, TMO failed to ensure that the message always reached its intended receipients. | Compliance | Health and Safety | KCTMO
Link magazine for tenants and homeowners had newsletter. Did not regulary contain fire safety information or information about evacuation strategy. | Compliance | Health and Safety | KCTMO
Janice Wray not provide consistent, clear and regular communication of fire safety advice to residents. | Compliance | Health and Safety | Janice Wray
Some website information on fire safety. | Compliance | Health and Safety | KCTMO
Eddie Daffarn advised LFB that Rydon was occupying a designated evacuation meeting point for Grenfell Tower. TMO wouldn’t have done actions unless prompted. | Compliance | Health and Safety | Eddie Daffarn
Adequate information and instruction on fire safety not provided to employees identified by Salvas in Sept 2009. | Compliance | Health and Safety | Salvas Consultant
Sept 2010 Janice Wray presented a report to TMO's Operations Committee on fire risk assessments which said nothing about fire action notices. | Compliance | Health and Safety | Janice Wray
Decision to post fire action notices was seemingly forgotten. | Compliance | Health and Safety | KCTMO
September 2010, Carl Stokes wrote to Janice Wray, at her request, about fire safety signage in the TMO’s residential buildings. He told her that, as the TMO provided fire safety information to residents in other ways, fire action notices were not required. Janice Wray accepted that advice, but she did not tell the Operations Committee or the executive team that the decision to put up fire action notices would not be carried out, though she believed that she had told her line manager. | Compliance | Health and Safety | Carl Stokes
Neither she nor Carl Stokes assessed each block to decide whether a fire action notice was required. On the contrary, the same generic approach was taken by the TMO to all its high-rise residential buildings. | Compliance | Health and Safety | Carl Stokes
LGA Guide did not say that fire action notices are never required in a purpose-built block; on the contrary, paragraph 79.1 provided in terms that a fire action notice would usually be all that would be needed by way of emergency plan for most purpose-built blocks. If Janice Wray and Carl Stokes thought that it supported a blanket decision not to put up fire action notices in any of the buildings managed by the TMO, they were mistaken. | Compliance | Health and Safety | Carl Stokes
Question of fire safety advice for residents was considered by the TMO again after the coroner published her recommendations following the Lakanal House inquests. The inquests had identified the need to find ways to advise residents about the fire procedure other than by the website, leaflets, magazines and letters. However, no effective alternative had yet been identified and fire action notices do not appear to have been discussed. On 2 May 2013, Janice Wray wrote a report for the Operations Committee about the TMO’s fire risk assessments which summarised the coroner’s recommendations following both the Lakanal House and Shirley Towers inquests, particularly as they touched upon the “stay put” strategy. The Lakanal House coroner’s recommendations were discussed at a meeting between the LFB Fire Safety team and the TMO Health & Safety team at a meeting on 15 May 2013. | Compliance | Health and Safety | Janice Wray
June 2013 Health and Safety Committee and Janice Wray not discussed or identified ways of putting up fire safety notices. | Compliance | Health and Safety | KCTMO
Dec 2015 LFB following Adair Tower fire issued enforcement notices against TMO and RBKC, one breach of Fire Safety Order that TMO procedures in the event of serious and imminent danger were inadequate. Due to no instructions about action to be taken in event of a fire had been displayed in common parts of premises. | Compliance | Health and Safety | KCTMO
Rebecca Burton advised Janice Wray about need for fire safety notices. LFB suggested action from enforcement notice. | Compliance | Health and Safety | Janice Wray
Janice Wray can fairly be criticised for seeking to justify doing the minimum in the face of the enforcement notice. | Compliance | Health and Safety | Janice Wray
Jan 2016 Councillor Marshall asked Robert Black to set out the advice that was normally given to residents of high-rise residential buildings. Robert Black responded on 15 January 2016, saying that “stay put” advice was given to residents of high-rise buildings and was available on the website, in regular fire safety articles in Link and in LFB leaflets distributed by the fire risk assessor to some dwellings. Janice Wray in April 2016 responded to Councillor Pat Mason who had written to Robert Black that articles about fire safety in Link and Homeowner, Councillor was concerned that not all residents would have had access to the internet. | Compliance | Health and Safety | Robert Black
Sept 2016 Health and Safety Committee considered putting up fire action notices in all buildings managed by TMO. Adopted risk based approach to start placing fire action notices in high-risk buildings. Far cry from what Janice Wray understood. | Compliance | Health and Safety | KCTMO
Nov 2016 LFB issued a deficiency notice for Grenfell Tower as there were no fire action notices in the common parts. Quote for fire action notices for Grenfell had been requested in Nov 2016 after Eddie Daffarn and Councillor Blakeman complained about lack of notices. | Compliance | Health and Safety | Fire Brigade
Eddie Daffarn in Nov 2016 said "KCTMO - Playing with Fire." Grenfell Action Group "only a catastrophic event would expose what he described as the ineptitute and incomptence." | Compliance | Health and Safety | Eddie Daffarn
Eddie Daffarn said residents of Grenfell had received no proper fire safety instructions from TMO. | Compliance | Health and Safety | Eddie Daffarn
November 2016, Councillor Blakeman saw the blog post and raised its contents with Robert Black. She agreed with Mr Daffarn’s point that instructions were not permanently available on noticeboards or in letters to residents (or in appropriate languages, where required) and asked whether that could be rectified. Robert Black asked Janice Wray to prepare a response. | Compliance | Health and Safety | Robert Black
Janice Wray said 30 fire action notices had been put up in Grenfell Tower in Dec 2016. | Compliance | Health and Safety | Janice Wray
Janice Wray response to Councillor Blakeman failed to mention that in Nov 2016, TMO had received a deficiency notice for Grenfell. | Compliance | Health and Safety | Janice Wray
Janice Wray’s failure to mention the deficiency notice to Councillor Blakeman mirrored Robert Black’s own failure to bring the notice to the attention of the TMO Board, a matter to which we have referred in Chapter 31. | Compliance | Health and Safety | Robert Black
December 2016, Peter Maddison asked if any of the allegations in the blog post could be considered libellous. Barbara Matthews responded indicating that she had spoken to Robert Black and that they agreed to take no action in response to it. Peter Maddison’s reaction, to seek advice about whether Mr Daffarn had libelled the TMO rather than to get to the bottom of the complaint, was telling. By this point, the TMO’s defensiveness and hostility towards the Grenfell community, at least as represented by Mr Daffarn, had sunk to a new low. | Compliance | Health and Safety | Peter Maddison
Delay in installing fire action notices should also be understood in the context of enquiries and complaints from residents of Grenfell Tower about the evacuation strategy. | Compliance | Health and Safety | KCTMO
Sept 2010 Leaseholders Association wrote to Robert Black setting out 11 areas of concern that had arisen from fire in April 2010. Letter said noone in the block had been aware of the evacuation procedure and that they had not been given information about what to do in the event of a fire in the previous 36 years. Anthony Parkes did not respond about the evacuation procedure. | Compliance | Health and Safety | Robert Black
Oct 2010, Leaseholders Association sent another letter, Anthony Parkes responded saying there was stay put strategy in place. Also fire safety information was published within magazines. | Compliance | Health and Safety | Anthony Parkes
2012, Leaseholders Association complained further via email to David Ward who was Homeownership Manager about plan to replace entrance doors to tenants flats, asking why leaseholders had not been included and lack of health and safety training or drills in case of emergency. Paul Dunkerton responded advising about stay put and this was repeated in several subsequent letters. | Compliance | Health and Safety | Paul Dunkerton
Sept 2016 Leaseholders Association sent email to Councillor Blakeman about TMO failure to organise any fire drill at Grenfell since 2012. | Compliance | Health and Safety | KCTMO
Robert Black circulated email where Janice Wray told him fire drills were not required in blocks with a "stay put" fire strategy. The purpose of fire drills, she said, was to test the procedure to be followed in the event of a fire and if that was to stay put, a fire drill would conflict with the way residents were expected to respond. Peter Maddison prepared a draft response in which he explained that Grenfell Tower maintained a “stay put” fire strategy and that, if the LFB decided that an evacuation was necessary in response to a particular incident, it would organise it. It is not clear whether that response was sent to the Leaseholders’ Association. | Compliance | Health and Safety | Robert Black
Chapter 43 The Smoke Ventilation System
Ventilation system designed to allow the passage of air through the building for ventilation and extraction of smoke in the event of a fire. Booster fans designed to be operated manually by the fire and rescue service. | Compliance | Health and Safety | KCTMO
Dampers were designed to open on the floor affected by the fire and close on all other floors, thereby allowing smoke to flow up the shaft to the opening at roof level without escaping into lobbies on other floors. | Compliance | Health and Safety | KCTMO
April 2010, smoke ventiliation system (AOV) failed to operate properly. Smoke leaked into the lobbies of eight other floors. Led to residents to believe they were trapped and call LFB. | Compliance | Health and Safety | KCTMO
Janice Wray advised Collette O'Hara of LFB system was subject to quarterly inspections by RGE Services. Most recent inspection identified "incomplete sealing" of a number of dampers. Wray advised remedial work had been delayed and not been carried out by the time of the fire. Spencer Sutcliff of LFB agreed TMO should implement interim measures in future. Also recommended TMO introduce a procedure to assess faults in fire safety systems to ensure any high-priority remedial work was completed to a strict time scale. | Compliance | Health and Safety | Janice Wray
LFB Sutfcliife said entire system be tested by an engineer because of what he described as a "catastrophic failure of the system." | Compliance | Health and Safety | KCTMO
TMO's Senior Electrical Engineer did not agree failure had been catastrophic. | Compliance | Health and Safety | KCTMO
RGE first visit likely in April 2010 said all fresh air inlet dampers were in open position and had been for some years. As a result, most of them were seized open or so contaminated that they were impossible to close and reset. If dampers were open and unable to close, smoke could spread between lobbies through the system in the event of a fire. Situation had apparently existed for a number of years before RGE's inspection. | Compliance | Health and Safety | RGE
May 2010 RGE quote of £27,280 for work to the inlet dampers to ensure that they automatically opened and closed without manual intervention. No evidence that the remedial work identified by RGE in its reported of May 2010 was ever carried out. | Compliance | Health and Safety | RGE
RGE Engineer carried out further test on the smoke ventilation system at Grenfell Tower in June 2010. Test fire dampers following recent fire and remedial works. | Compliance | Health and Safety | RGE
Asset Investment and Engineering Health and Safety Group in Aug 2010 considered feasibility of modernising the smoke extraction system. Prompted by fire in April 2010 not by RGE report in May 2010 as suggested by Janice Wray. | Compliance | Health and Safety | Janice Wray
July 2010, Grenfell Leaseholders Association made complaint about smoke ventilation system. Suggested TMO did not tell leaseholders or residents of defects in the system which had been found by RGE or the heightened risk to their safety. | Compliance | Health and Safety | KCTMO
July 2010, Leaseholders Association wrote to Geoff Payne (TMO's Head of Housing) about smoke entering lobbies from April 2010 fire. Asked what defects had been found in system and what action had been taken. Daniel Wood (TMO's Head of Homeownership) responded in Aug 2010 saying there had been a "minor fault" in the system that been identified during the service visit before the fire. Wood said that repairs had been put in hand and that, when completed, the system would be fully operational, he said problem with leaking vents had been put right. | Compliance | Health and Safety | Daniel Wood
Sept 2010, Leaseholders Association wrote to Robert Black. Requested independent investigation for safety of building. Said that if smoke ventilation system was not working it should be considered a major rather than a minor fault as Wood had described it. | Compliance | Health and Safety | Daniel Wood
Anthony Parkes replied in Sept 2010. Said seals on some vents leaked but otherwise said working at time of fire. Said fire effects not so serious had LFB fire fighters had activated smoke extract fan manually, but not known how to do so. Said system was being upgraded so would work automatically when fire alarm sounded. Parkes gave an assurance that system was regularly checked and test reports completed. | Compliance | Health and Safety | Anthony Parkes
Neither Wood or Parkes referred to RGE's report of May 2010, which had advised that inlet dampers might not operate on every activation and recommended significant remedial work. No evidence that remedial work was carried out. | Compliance | Health and Safety | Daniel Wood
Aug 2011, RGE said vents in lobbies were no longer reliable and were found to have opened at random between maintenance visits, no longer fit for purpose and needed to be replaced. | Compliance | Health and Safety | RGE
Keith Fifield had seen what RGE said. Contractors would be invited to submit tenders for the necessary work. | Compliance | Health and Safety | Keith Fifield
The required improvements to the system at Grenfell Tower were discussed at a meeting of the TMO Asset Investment and Engineering Health and Safety Group on 15 September 2011 attended by Keith Fifield and Janice Wray. The minutes of the discussion do not refer to RGE’s recent report, but in our view, given Keith Fifield’s knowledge of that report, it is unlikely that the modernisation or replacement of the system was discussed without mentioning the significant findings it contained. | Compliance | Health and Safety | Keith Fifield
Despite RGE reports in May 2010 and Aug 2011, no evidence that TMO gave any consideration implement measures to mitigate the risk presented by potential failure of smoke ventilation system to operate in the event of a fire. Despite assurance Janice Wray had given to LFB Fire Safety team after fire in April 2010 that would do so. | Compliance | Health and Safety | Janice Wray
Oct 2011, AECOM (construction industry consultancy), produced a tender for the modernisation of the system. Said current system had some dampers which leaked, making it possible for smoke from a fire on a lower floor to leak through the closed dampers on an upper floor into the lift lobby. | Compliance | Health and Safety | AECOM
Also possible one set of dampers would open at any one time, since no way of establishing whether dampers were open other than by visual inspection. Although the extractor fans would overcome these problems, they had to be started manually by LFB. | Compliance | Health and Safety | KCTMO
No evidence of risks mitigated for defects in the system pending modernisation by Janice Wray or anyone else in TMO. Although tender document was produced in Oct 2011, no work had been carried out by late 2013 when it was included in the refurbishment, not completed until April 2016. Janice Wray said work had been put back so that it could form part of the refurbishment. | Compliance | Health and Safety | Janice Wray
Fire Risk Assessor should assess risk of means of escape might be compromised by a failure of a smoke ventilation system to work. | Compliance | Health and Safety | KCTMO
PAS 79: 2012: Some smoke control systems, which, in some premises can be essential for protection of means of escape. Vital to ensure that adequate arrangements for control, testing and maintenance of such systems. Clause 16 says that fire safety management, which includes the testing and maintenance of fire protection systems, and fire protection measures hould be regarded as of equal importance. | Compliance | Health and Safety | Carl Stokes
Carl Stokes never tested or witnessed testing of the smoke ventiliation system at Grenfell Tower dyring his fire risk assessments. | Compliance | Health and Safety | Carl Stokes
Not clear why test results not provided to Carl Stokes. | Compliance | Health and Safety | Carl Stokes
Carl Stokes FRA in Dec 2010, incorrectly referred to fire in April 2010 as being in July 2010. Not mention that system had not operated as intended. Not aware or advised of leak in the system. | Compliance | Health and Safety | Carl Stokes
Dec 2010, Carl Stokes noted there were automatic opening vents but did not know whether the system had been serviced and maintained. Failure to obtain that information as part of the FRA was significant as RGE had identified defects in the inlet dampers as per May 2010 report. | Compliance | Health and Safety | Carl Stokes
Carl Stokes said that he had not been aware of RGE's concerns about the inlet dampers. | Compliance | Health and Safety | Carl Stokes
Carl Stokes FRA in Nov 2012. Third time he said not know whether system had been routinely tested or maintained, no evidence that he tried to obtain any relevant information. No comment by him about a worrying problem. Not vary his assessment of fire risk which he considered tolerable to account for the possibility that the system might not have been maintained in efficient working order. | Compliance | Health and Safety | Carl Stokes
RGE in Aug 2011 said not guarantee system could work, Stokes failure to request info for assessment especially significant in Nov 2012. AECOM tender in Oct 2011 also referred to serious defects in the system. Stokes did not more than renew his request for confirmation about system being maintained. | Compliance | Health and Safety | Carl Stokes
Nov 2012, Leaseholders Association wrote further to David Ward about concerns felt by its members being excluded from program to replace flat entrance doors in 2011-2012. Complained leaseholders had not been told after fire in April 2010 that entrance doors might not comply with safety regulations and questioned whether other health and safety equipment was in working condition and fit for purpose. Asked for copies of all reports, conclusions and recommendations relating to any investigation into the fire. | Compliance | Health and Safety | David Ward
Nov 2012, Janice Wray sent email to Paul Dunkerton containing information about the fire in April 2010. She said it would be inappropriate to provide leaseholders with copy of email she had sent to LFB Fire Safety Team after fire. Instead, she proposed telling them that smoke ventilation system had removed the smoke from lift lobby, but not worked effectively as should due to need for remedial works, all works been completed and system continued to operate effectively. | Compliance | Health and Safety | Janice Wray
Paul Dunkerton included that information in his reply to Leaseholders Association in Dec 2012. However TMO had for a long time been in possession of RGE's report on Aug 2011 which stated explicitly that it could not guarantee that system would work and AECOM's tender. Janice Wray should have asked Keith Fifield for this info. | Compliance | Health and Safety | Paul Dunkerton
In failing to give leaseholders a full and accurate account of the investigation, failed to inform them and other residents, of the operational status of the system and provided them with false assurances about the protection the system would provide in the event of a fire. | Compliance | Health and Safety | KCTMO
Janice Wray accepted she had known that system was not sure to work but took no steps at that stage to put in place any measures to mitigate risk. Janice Wray as the competent person was responsible for overseeing the TMO's compliance of the Fire Safety Order, in particular she had a responsibilty to make sure that the smoke ventilation system was either repaired or, if that was not viable, replaced and mitigating measures put in place pending its replacement. | Compliance | Health and Safety | Janice Wray
RGE further test in Oct 2013, identified same problems as in Aug 2011. Test report stated dampers were still not functioning. Not be guaranteed to work in emergency. RGE quote in May 2010 but still outstanding. No plan for immediate action due to modernising the system as part of refurbishment. | Compliance | Health and Safety | RGE
Jan 2014, Max Fordam sent email to RGE asking for test and maintenance records for smoke ventilation system, assist in formulating a submission to building control on designs of proposed new system. RGE provided maintenance report for system but not test results, unsure why RGE didnt provide these. | Compliance | Health and Safety | RGE
March 2014 LFB visited Grenfell Tower. LFB identified 25-30% of vents on smoke ventilation system were not in correct position. Concerned that would turn visit into formal audit with threat of enforcement notice. | Compliance | Health and Safety | Fire Brigade
LFB suggested to Janice Wray that chase up RGE for servicing records. | Compliance | Health and Safety | Janice Wray
Janice Wray has not advised that RGE had said that it could not guarantee system would work in event of the fire, matter of which she had been aware from at least April 2013. | Compliance | Health and Safety | Janice Wray
LFB served deficiency notice on TMO, said about quarter of dampers in smoke ventilation system were not working, which indicated that it had not been maintained in effective working order. | Compliance | Health and Safety | Fire Brigade
LFB expected remedy by May 2014. TMO couldn’t find a temporary solution. 6 months after deficiency notice, smoke ventilation system had still not been properly inspected and serviced. | Compliance | Health and Safety | KCTMO
No actual meeting with Rydon to discuss interim measures. | Compliance | Health and Safety | KCTMO
Not considered possible to carry out temporary repairs to the system. | Compliance | Health and Safety | KCTMO
Chuff Fire and Security. Oct 2014 examine smoke ventilation system but unable to test due to a fault on the fire alarm panel. Service certificate recorded that further investigation of the system was required. | Compliance | Health and Safety | Chuff
Neither Claire Williams nor Janice Wray told LFB that existing system was beyond repair, nor did they pass on info that the completion of the work was likely to be delayed beyond Christmas. No interim measures. | Compliance | Health and Safety | Janice Wray
Carl Stokes carried out FRA at Grenfell Tower on Oct 2014. He did not refer to deficiency notice where quarter of dampers not working and system not maintained in working order. Failed to convey LFB findings. | Compliance | Health and Safety | Carl Stokes
Carl Stokes did not mention that RGE had said in its service report that it could not guarantee that the system would work, not did he refer to findings on Mar 2014 that 25-30% of dampers were not working. He did not refer to Chubb not able to carry out service of the system in Oct 2014 or Bosman's email in Oct 2014 where described system as beyond repair. | Compliance | Health and Safety | Carl Stokes
Carl Stokes even when failed to address these issues said fire risk at Grenfell was tolerable. Gave misleading impression that system was operational. Should have said ventilation system was not working. Did not ask whether any measures had been put in place to mitigate immediate risk presented by the defects in existing system, nor did he recommend any. | Compliance | Health and Safety | Carl Stokes
Matthew Ramsey asked Janice Wray to ensure Carl Stokes would address concerns about system, Wray did not do this. LFB in Sept 2014 had even requested being aware of unavailability of system during modernisation work was covered in FRA. | Compliance | Health and Safety | Carl Stokes
Carl Stokes only put no on question about automatic opening vents along with any associated equipment/devices. No explanation. | Compliance | Health and Safety | Carl Stokes
Carl Stokes not record that Chubb had been unable to service system in Oct 2014. Fourth occasion Stokes did not have any information about maintenance of ventilation system. | Compliance | Health and Safety | Carl Stokes
LFB not informed by Janice Wray or Claire Williams about beyond repair system. | Compliance | Health and Safety | Janice Wray
Jan 2015 Leaseholders complained about if get new system, Maddison advised Councillor system was beyond repair and TMO was working with building control to agree a design for a system that would meet current standards. | Compliance | Health and Safety | Peter Maddison
Janice Wray and Claire Williams did not advise LFB in Jan 2015 that work on system would be expected to be complete by June 2015. | Compliance | Health and Safety | Janice Wray
Rydon FRA in Feb 2015 identified detection and alarm systems and smoke vent did not work. Claire Williams and Janice Wray didn’t review Carl Stokes quality of review. | Compliance | Health and Safety | Janice Wray
Work to modernise system did not begin until April 2015 and did not complete until April 2016. | Compliance | Health and Safety | KCTMO
Chapter 44 Lifts
Phase one established firefighters couldn’t get control of lifts which caused some residents to die. | Compliance | Health and Safety | Fire Brigade
Various policies existed on checks for lifts. Lifts should be examined usually an insurance engineer every six months and that lift maintenance contract should be established. Also lifts be checked weekly or monthly to ensure operating okay. | Compliance | Health and Safety | KCTMO
PDERS maintenance contract. Tests indicated no faults with the lifts. | Compliance | Health and Safety | PDERS
Bureau Veritas would do thorough examinations of lifts in borough every six months. Several category B and C defects to lifts. | Compliance | Health and Safety | Bureau Veritas
TMO didn’t carry out fire control switch inspection every month by its own lift engineer. | Compliance | Health and Safety | KCTMO
CCTV showed that PDERS not tested fire control switch on May 2017 but said they did so. | Compliance | Health and Safety | PDERS
Automatic fire alarm recall had been disconnected, no connection between fire alarm, smoke detection system and lifts. | Compliance | Health and Safety | KCTMO
Firefighters found Grenfell ground floor fire control switch couldn’t be operated. | Compliance | Health and Safety | Fire Brigade
Wrong size of drop key most likely reason for failure of the fire control switch to operate properly. | Compliance | Health and Safety | KCTMO
Some debris/material inside the control swtiches. | Compliance | Health and Safety | KCTMO
Chapter 45 Emergency Planning
Fire Safety Order requires routes to emergency exists and exits themselves be clear at all times, indicated by signs and lit adequately. | Compliance | Health and Safety | KCTMO
Fire Safety Order requires the responsible person to establish, and where necessary give effect to, appropriate procedures to be followed in the event of serious and imminent danger from fire and to nominate a sufficient number of competent persons to implement those procedures in so far as they relate to the evacuation of relevant persons from the premises. The procedures must, so far as is practicable, require any relevant persons exposed to a serious and imminent danger to be informed of the nature of the hazard and of the steps taken or to be taken to protect them from it. | Compliance | Health and Safety | KCTMO
Should be a suitable emergency plan. Stay put strategy was adopted. | Compliance | Health and Safety | KCTMO
Adrian Bowman responsible for emergency plan under supervision generally of Janice Wray. Serious failing that this plan wasn’t reviewed regularly. | Compliance | Health and Safety | Adrian Bowman
First part was generic plan, second contained separate sections relating to the various properties managed by the TMO, each containing a description of a particular property. | Compliance | Health and Safety | KCTMO
Subsection did not reflect any of the changes, stayed as was the position in 2002. | Compliance | Health and Safety | KCTMO
Janice Wray did not give thought to whether emergency plan contained all the information recommended in the guidance. | Compliance | Health and Safety | Janice Wray
Carl Stokes did, in the main, take PAS 79:2012 as his guide for making fire risk assessments, although his adherence to it was patchy and inconsistent. Each of his fire risk assessments for Grenfell Tower had a section headed “The Evacuation Strategy for this building” in which he noted that there was a “stay put” strategy in place and that the fire and rescue service or the TMO would organise a general evacuation of the building, if appropriate. | Compliance | Health and Safety | Carl Stokes
Stokes did not record whether there was an emergency plan specifically for Grenfell Tower that described how the TMO would contact the LFB, residents or the nursery or boxing club in the event of a fire. Nor did he record whether there was a plan which contained relevant information specific to the tower. That part of the fire risk assessment remained substantially the same between 2010 and 2016 with minor and immaterial variations. | Compliance | Health and Safety | Carl Stokes
Janice Wray and TMO never checked anything about Carl Stokes FRAs. | Compliance | Health and Safety | Janice Wray
Nov 2015 of complaints about absence of evacuation plan at Adair Tower in Nov 2015. | Compliance | Health and Safety | KCTMO
Barbara Matthews, who was co-ordinating the response to the fire, said that although RBKC had been supportive, the TMO should be more involved in RBKC’s emergency planning strategy so that everyone was aware of contact numbers and roles and responsibilities. | Compliance | Health and Safety | Barbara Matthews
As a result of the Adair Tower fire, it had become apparent to the TMO that its role in an emergency was unclear and that its Emergency Plan should be reviewed in conjunction with RBKC’s emergency plan and revised as necessary. Barbara Matthews may have looked at the plan, but she did not take any steps herself to make sure that it was brought up to date; instead, she relied on Janice Wray to do that. | Compliance | Health and Safety | Barbara Matthews
Chapter 46 Vulnerable Residents
Articles 14 and 15 of the Fire Safety Order set out the duties of the responsible person to ensure effective emergency exits and procedures when imminent danger (communal areas). | Compliance | Health and Safety | KCTMO
Article 14 for emergency routes quickly and safely. Risk assessment for any persons that require special evacuation arrangements. | Compliance | Health and Safety | KCTMO
Sleeping Guide (2007) for FRAs in relation to common parts and for FRA steps should be taken to identify people particularly at risk e.g. children, persons with disabilities. | Compliance | Health and Safety | KCTMO
Means of escape must be suitable for evacuation, responsible person may need to discuss individual needs for those with disabilities. | Compliance | Health and Safety | KCTMO
DCLG Means of Escape for Disable People supplementary guide, LGA Guide 2011, PAS 79, BS 9991:2015 Fire Safety Code of Practice. | Compliance | Health and Safety | KCTMO
TMO had duty to identify and record the presence of residents with disabilities and nature of those disabilities. | Compliance | Health and Safety | KCTMO
By June 2009, LFB concerned about failure of TMO to make adequate provision for disabled persons to escape from some of its buildings. | Compliance | Health and Safety | Fire Brigade
17th June 2009, LFB advised Janice Wray it intended to serve an enforcement notice on TMO and RBKC for FRA failures on some of their blocks. | Compliance | Health and Safety | Janice Wray
Claire Wise provided advice to Janice Wray. | Compliance | Health and Safety | Claire Wise
Jean Daintith advised Robert Black that Alexis Correa stated need for better FRA and specialist was needed. | Compliance | Health and Safety | Robert Black
Janice Wray had not sought advice about TMO's duties under Fire Safety Order or Disability Discrimination Act. | Compliance | Health and Safety | Janice Wray
Hence TMO was aware at the highest level. | Compliance | Health and Safety | Robert Black
In Sept 2009, Salvus advised TMO to establish procedures to ensure the safety of disabled or vulnerable persons in the event of a fire, recommended actions for within 3 months. | Compliance | Health and Safety | Salvas Consultant
Janice Wray felt Housing team would gather information about vulnerable residents. | Compliance | Health and Safety | Janice Wray
Carl Stokes did not check the TMO's systems for recording vulnerable residents as he thought that was beyond what was expected of him. | Compliance | Health and Safety | Carl Stokes
No editions of Link from Autumn 2009 to Spring 2017 carried any article inviting residents who were worried about ability to evacuate their homes in emergency to contact TMO. | Compliance | Health and Safety | KCTMO
Robert Black's assurances were misleading about PEEPs. First of only two PEEPs to be prepared for TMO residents was still in preparation and not completed until 18th Oct 2010, nearly 3 weeks later. Plans to produce generic and individual PEEPs were not fulfilled. | Compliance | Health and Safety | Robert Black
Nobody from RBKC asked whether TMO had completed any PEEPs which RBKC admitted was an oversight. | Compliance | Health and Safety | RBKC
Contrary to what had been said by Robert Black and Janice Wray, TMO did not regularly identify vulnerable residents. | Compliance | Health and Safety | Robert Black
LFB on 26th Sept 2012 asked TMO to prepare list of residents with additional needs to be kept close to the fire alarm control panel. Related to general needs and sheltered. Prompt by LFB not actioned by TMO. | Compliance | Health and Safety | Fire Brigade
30th Nov 2012, LFB asked Janice Wray for help in identifying vulnerable persons who might be suitable for LFB promoting sprinklers. Janice Wray advised by Carl Stokes to say to LFB that not aware of anyone so that avoid any questions being asked about why anyone who might qualify had not been identified in FRAs or received a PEEP. | Compliance | Health and Safety | Carl Stokes
Carl Stokes knew that PEEPs were required for vulnerable residents, that TMO had produced only two, and that his FRAs had not recommended any additional fire safety measures for vulnerable people. His advice amounted to a suggestion that Janice Wray should lie to the LFB. | Compliance | Health and Safety | Carl Stokes
Carl Stokes carried out six FRAs for Grenfell between Sept 2009 and June 2016. Stokes failed to consider full range of impairments that could affect residents who might be required to evacuate. | Compliance | Health and Safety | Carl Stokes
Leon Taylor carried out FRA for Grenfell in June 2014. In his FRA, Taylor put TMO should have record of all those who had special needs for evacuation, no actions taken by TMO and no PEEPs were created by TMO. | Compliance | Health and Safety | Leon Taylor
Carl Stokes for other TMO high rise buildings did not identify vulnerable persons. Section 13 of each of his FRAs first three paragraphs were identical for various towers. | Compliance | Health and Safety | Carl Stokes
Carl Stokes did not record two PEEPs for other towers in his FRAs. | Compliance | Health and Safety | Carl Stokes
Carl Stokes FRAs were inaccurate and out of date in relation to presence of vulnerable persons and were not suitable for Article 9 of the Fire Safety Order. | Compliance | Health and Safety | Carl Stokes
TMO had no formal fire safety strategy until Nov 2013. Strategy was later reviewed on 2016 and approved in June 2017, contained no reference to PEEPs for vulnerable persons. Robert Black could not remember why there had been no reference to the fire safety strategies or the Health and Safety policy to producing PEEPs. | Compliance | Health and Safety | Robert Black
None of the supporting residents draft policies relating to vulnerable residents dealt with fire safety. | Compliance | Health and Safety | KCTMO
First version of supporting residents policy took nearly two years to complete. | Compliance | Health and Safety | KCTMO
New tenants vulnerable residents not recorded properly or consistenly. | Compliance | Health and Safety | KCTMO
From 2015 onwards need to carry out 30 tenancy audits per month. | Compliance | Health and Safety | KCTMO
Some information gathered was not included in the spreadsheet from which attempts were made on night of the fire to extract information about vulnerable residents. | Compliance | Health and Safety | KCTMO
LFB on 12th March 2014 asked for a premises information box to be installed, would help LFB gather information about Grenfell. Carl Stokes strongly advised Claire Williams against installing a premises information box as Stokes felt onus should be on LFB to gather information. No good reason for Stokes to do this. | Compliance | Health and Safety | Carl Stokes
Carl Stokes further advised this installation on 4th May 2016. | Compliance | Health and Safety | Carl Stokes
TMO simply never complied with LFB's request for a secure box containing information about Grenfell, no good reason for failure to do this. | Compliance | Health and Safety | KCTMO
Carl Stokes aware of TP Tracker, he did not take into account information it contained when making his FRAs. | Compliance | Health and Safety | Carl Stokes
Information about vulnerable residents was recorded in three different places by June 2017. | Compliance | Health and Safety | KCTMO
Most important information not transferred from Capita to CRM. | Compliance | Health and Safety | KCTMO
On night of fire there were 297 people in the tower, 67 were children and 37 were adults with sensory, mobility or cognitive impairment, not recorded on tenancy records, tenancy audit documents or David Noble's spreadsheet. | Compliance | Health and Safety | David Noble
Poor processes for PEEPs for vulnerable residents. Residents also not told that they could asked to be assessed for a PEEP. | Compliance | Health and Safety | KCTMO
Janice Wray took no steps to ascertain whether resident needed a PEEP as per Elpidio Bonifacio in Flat 83, his disabilities were not recorded. | Compliance | Health and Safety | Janice Wray
Bonifaco was last person to escape from Grenfell, he was blind, elderly and unable to escape without help. | Compliance | Health and Safety | Bonifaco
A result of failure to maintain adequate record of residents vulnerabilities was that TMO was unable to provide LFB with accurate list, by time list reached LFB all those who died in the tower had already lost their lives. | Compliance | Health and Safety | KCTMO
TMO's failure to collect information about any vulnerable residents to enable PEEPs and for measures when fires occurred. Basic neglect of its obligations for fire safety. | Compliance | Health and Safety | KCTMO

## Part 6
The Refurbishment of Grenfell Tower | Issue 1 | Issue 2 | Person
KALC project influenced the appointment of Studio E as architect and describe the way in which the TMO manipulated the procurement process to avoid having to put the contract for architectural services out to public tender. Artelia was appointed by the TMO as a consultant, having acted as employer’s agent and quantity surveyor for the KALC project. | Procurement | Skills | Mark Anderson
KCTMO entered into discussions with Rydon before the procurement process had been completed leading to an agreement that, if Rydon were awarded the contract, it would reduce its price to an acceptable level. | Procurement | Contractor CIH Sponsorship | Peter Maddison
Rydon subcontractor Harley. | Subcontractor | Relationship Previously | n/a
RBKC building control did not properly scrutinise the design or choice of materials and failed to satisfy itself that on completion of the work the building would comply with the requirements of the Building Regulations. | Building Control | Materials | John Hoban
Exova was instructed by Studio E on behalf of the TMO to prepare a fire safety strategy for the building in its refurbished form. A draft was prepared but never completed. In particular, it did not include an analysis of the external wall or its compliance with functional requirement B4(1) of the Building Regulations. | Fire Safety | Materials | Exova
TMO must also bear a share of the blame for the disaster because it failed to ensure that the position of Exova was clarified after Rydon had been appointed and that the fire safety strategy was completed. | Contract | Fire Safety Strategy | KCTMO
Although the TMO as the client wanted to reduce the cost by using ACM rainscreen panels, it was the responsibility of Studio E to determine whether the use of such material would enable the building to comply with functional requirement B4(1) of the Building Regulations and advise the TMO accordingly. Its failure to recognise that ACM was dangerous and to warn the TMO against its use represented a failure to act in accordance with the standard of a reasonably competent architect. It also failed to recognise that Celotex insulation was combustible and not suitable for use on a building over 18 metres in height in accordance with the statutory guidance. Studio E therefore bears a very significant degree of responsibility for the disaster. | Principle Designer | CDM 2007/15 | Bruce Sounes
We have identified many other respects in which Studio E failed to meet the standards of a reasonably competent architect, of which the following are the most significant. It failed to ensure that Exova completed the fire safety strategy for the refurbished building or advise Rydon and the TMO that it should be required to do so. It failed to understand that it was responsible for design work carried out by sub-contractors and so did not check Harley’s designs to ensure that on completion the building would comply with the Building Regulations. It did not devise a proper cavity barrier strategy or check Harley’s designs for the cavity barriers and it failed to produce detailed drawings of the window reveals or to notice that the materials specified for the window infill panels were unsuitable. | Principle Designer | CDM 2007/15 | Bruce Sounes
Exova also bears considerable responsibility for the fact that Grenfell Tower was in a dangerous condition on completion of the refurbishment. Our most serious criticism is that it failed to produce a final version of the fire safety strategy for the refurbished building and that it failed either to draw that fact to the attention of the design team or to warn it about the potential consequences. None of those responsible for drafting the fire safety strategy visited Grenfell Tower; the only site visit by a member of Exova’s staff took place at a preliminary stage. Exova’s attitude was wholly inconsistent with the careful approach to matters affecting the safety of life to be expected of a reasonably competent fire engineer. | Fire Safety Strategy | Fire Engineer | Exova
We consider that the principal contractor, Rydon, also bears considerable responsibility for the fire. It gave inadequate thought to fire safety, to which it displayed a casual attitude throughout the project and its systems for managing the design work did not ensure that its sub-contractors and consultants properly understood their different responsibilities. Rydon itself did not understand where responsibility for individual decisions lay and as a result it failed to co-ordinate the design work properly. Rydon had an inexperienced team on the refurbishment that did not have sufficient knowledge of the Building Regulations or Approved Document B. It relied entirely on its cladding sub-contractor, Harley, to draw its attention to any errors in the design, but it did not specifically ask Harley to assess Studio E’s work. It failed to take proper steps to investigate Harley’s competence and ensure that it was competent to undertake the work and capable of providing the services required of it. It was complacent about the need for fire engineering advice and took the decision not to retain Exova without consulting the TMO, Studio E or Artelia. Its understanding of the work already carried out by Exova was superficial; as a result, it failed to realise that the fire safety strategy had not been completed. | Principle Contractor | CDM 2007/15 | Rydon
Harley itself failed in many respects to meet the standards to be expected of a reasonably competent cladding contractor and it too bears a significant degree of responsibility for the fire. It did not concern itself sufficiently with fire safety at any stage of the refurbishment and appears to have thought that there was no need for it to do so, because others involved in the project, and ultimately building control, would ensure that the design was safe. It failed to ask the kind of questions about the materials being considered that a reasonably competent cladding contractor would have asked. It was induced to buy Reynobond 55 PE panels partly by its existing relationship with Arconic and the cladding fabricator, CEP Architectural Facades, with which it was able to negotiate a favourable price. Its staff were unaware of the requirements of the Building Regulations relating to fire safety, the guidance in Approved Document B or industry guidance and did not understand the underlying testing regime. Although Celotex RS5000 (as opposed to Celotex FR5000) had not been specified, Harley accepted it for use on the tower without enquiring in any detail whether it could be safely used and did not ask any of the other members of the design team that question before doing so. Its design for the cavity barriers was incomplete and did not comply with the guidance in Approved Document B. | Cladding | Insulation | Harley
RBKC’s building control department failed to perform its statutory function of ensuring that the design of the refurbishment complied with the Building Regulations. It therefore bears considerable responsibility for the dangerous condition of the building immediately on completion of the work. The surveyor responsible for the refurbishment was overworked, inadequately trained and had a very limited understanding of the risks associated with the use of ACM panels. He failed to obtain full information about the construction of the external wall at the stage of the full plans application and did not ask whether Exova had provided a completed fire safety strategy. He knew that ACM was to be used as the rainscreen but paid little or no attention to the BBA certificate for Reynobond PE. He failed to recognise that Celotex RS5000 insulation was not a material of limited combustibility and, if he looked at any information about it, he simply accepted the assertion that it was suitable for use on tall buildings. He failed to consider whether the external wall system proposed for Grenfell Tower was the same as that tested by Celotex and said to support the use of RS5000. | Cladding | Insulation | John Hoban
The TMO must also take a share of the blame for the disaster. As the client it failed to take sufficient care in its choice of architect and paid insufficient attention to matters affecting fire safety, including the work of the fire engineer. | Client | CDM 2007/15 | KCTMO
Chapter 48 The Legislative Background
The Building Act 1984, The Building Regulations Act 2010, The Construction (Design and Management) Regulations 2007/2015. | Building Regs | CDM 2007/15 | Legislation
Approved Document B. | Approved Document B | Compliance | Legislation
Chapter 49 Industry Guidance on the Construction of External Walls
Building Research Establishment: BR 135, Building Control Alliance, Centre for Windows and Cladding Technology. | Guidance | Industry | Various
Booth Muirie Technical Guidance Note 1 | Guidance | Industry | Various
Chapter 50 Organisations Involved in the Refurbishment
The Client being the KCTMO. There were princinple persons who negotiated the contracts for the refurbishment. | Client | CDM 2007/15 | KCTMO
Mark Anderson (Interim Director of Asset Investment and Engineering) then Interim Director of Asssets and Regeneration (until Jan 2013) | Procurement | KCTMO | Mark Anderson
Peter Maddison was Director of Assets and Regneration (from Jan 2013). | Procurement | KCTMO | Peter Maddison
Paul Dunkerton was Freelance Project Manager (late 2010 to early July 2013). | Freelance | Project | Paul Dunkerton
David Gibson was Head of Capital Investment (Feb 2013 to end of June 2016). | Procurement | KCTMO | David Gibson
Claire Williams was Project Manager (from Sept 2013) | Project | Notebooks | Claire Williams
Studio E was Architect for Grenfell Tower founded by Andrzej Kuszell. Reps were Bruce Sounes, Neil Crawford and Tomas Rek | Principle Designer | Architect | Studio E
Andrzej Kuszell not had any personal experience of overcladding an occupied residential building and no personal experience of refurbishing high rise building. | Principle Designer | Architect | Andrzej Kuszell
Bruce Sounes did not have any experience of overcladding an occupied residential building, gained some experience of overcladding for Watford Woodside Leisure Centre. | Principle Designer | Architect | Bruce Sounes
Neil Crawford had some limited experience of commercial projects involving cladding and curtain walling but had not previously been involved in overcladding high rise. | Principle Designer | Architect | Neil Crawford
Tomas Rek had worked primarily in before in the education sector. | Principle Designer | Architect | Tomas Rek
Appleyards Ltd which became Artelia Ltd was Quantity Surveyor, Employer's Agent and CDM Co-ordinator for Grenfell Project, was dealing with KALC. | Employer's Agent | CDM 2007/15 | Appleyards Ltd
Simon Cash was Project Director and had overall responsibility for whole of Artelia's involvement in the refurbishment. | Employer's Agent | CDM 2007/15 | Simon Cash
Phillip Booth was employer's agent (from April 2013 to June 2015), Neil Reid from March 2015. | Employer's Agent | CDM 2007/15 | Phillip Booth
Keith Bushell was CDM Co-ordinator until Oct 2015. | CDM Coordinator | CDM 2007/15 | Keith Bushell
Mechanical and Engineering Consultant Max Fordham LLP, Andrew McQuatt and Matt Cross Smith. | Mechanical and Engineering Consultant | Compliance | Max Fordham
Stuctural Engineer was Curtins Consulting Ltd. | Curtins | Compliance | Stuctural Engineer
Exova (UK) Ltd was Fire Engineer. Used as was trusted from KALC project. James Lee, Cate Cooney, Dr Clare Barker, Terence Ashton, Dr Tony Pearson. | Fire Engineer | Fire Safety | Exova
John Rowan and Partners were the Clerk of Works. Gurpal Virdee was Managing Partner and Jonathan White was Clerk of Works. | Clerk of Works | Compliance | John Rowan
Rydon was Principle Contractor. Stephen Blake was responsible for the project. | Principle Contractor | Stephen Blake | Rydon
Rydon had employed subcontractors who were Harley Curtain Wall and Harley Facades, JS Wright and Co Ltd, SD Plastering Ltd and SD Carpentry Ltd. | Cladding | Insulation | Harley Facades
Harley Facades was contractually responsible to Rydon for design and construction of the fascade (cladding, insulation, window frames, infill panels, glazing, cavity barriers). | Cladding | Insulation | Harley Facades
Harley Facades subcontracted Kevin Lamb (construction drawings), CEP Architectural Facades and Osborne Berry Installations Ltd. | Cladding | Insulation | Harley Facades
Building Control included John Allen, John Hoban, Paul Hanson and Jose Anon. | Surveyors | Compliance | John Hoban
Chapter 51 Origins of the Grenfell Tower Project
2009 report by Urban Initiatives Ltd proposed demolition of Grenfell Tower due to appearance. | Appearance | Cladding | Urban Initiatives
Laura Johnson told Cllr Feilding-Mellen that there was an immediate need to decide whether to invest in Grenfell Tower and reassured him that such investment would not preclude the possibility of regenerating the wider estate in the future. | Appearance | Investment | Laura Johnson
RBKC began work on KALC in 2010. Laura Johnson responsible for project. | KALC | Experience | Laura Johnson
Sept 2011, Studio E won via OJEU the design of the KALC project. Studio E retained Exova as sub-consultant. | KALC | Experience | Studio E
Chapter 52 The Appointment of Studio E
Inquiry states that priority was cost savings over other considerations. | Costs | Savings | Studio E
Peter Wright met with Andrzej Kuszell on 9th Dec 2011 about Grenfell, Kuszell felt it to be an exploritory meeting. | Meeting | Experience | Andrzej Kuszell
Mark Anderson felt Studio E formally engaged in Feb 2012. Cllr Coleridge being driver for Studio E aswell as from all other RBKC Officers. RBKC's earnest wish. | Meeting | Experience | Mark Anderson
Laura Johnson like Mark Anderson felt that RBKC would have challenged the TMO if decided not to use the KALC team. | Selection | Appointment | Laura Johnson
Grenfell Tower was Studio E’s first residential high-rise cladding project and yet Mr Anderson told us that no steps had been taken before it was appointed to find out whether it had any experience of a project of that kind. He accepted that that was an obvious question and could not explain why no one had asked it. | Selection | Appointment | Mark Anderson
Anderson sought to ensure avoiding public procurement process for Studio E. Need to have Studio E cap their fees so as to avoid OJEU. | Selection | Appointment | Mark Anderson
Kuszell felt limit of £174,000 would result in Studio E doing more work than the fee would cover. No evidence of these concerns raised with TMO. | Procurement | Fees | Andrzej Kuszell
Proposal of fee of £323,000 for all stages of work, paid before and after novation as to avoid OJEU. | Procurement | Fees | Andrzej Kuszell
The report went on to state that the novation of the Grenfell Tower design team to Leadbitter (the principal contractor for KALC and at that time the proposed principal contractor for the Grenfell Tower project) after the planning stage would be compliant with EU procurement rules because the Grenfell Tower project had been included in the OJEU notice relating to the KALC project. However, that statement was wrong, as no mention of the Grenfell Tower project had been made in the OJEU Notice relating to the KALC project. | OJEU | Procurement | KCTMO
By Dec 2012, Studio E had already issued invoices totalling £174,000. No procurement process, no member of firm interviewed. | Procurement | Fees | Studio E
It is hard to see how Mr Anderson could possibly have thought that it was permissible for the TMO to rely on the procurement process undertaken by RBKC for the KALC project to justify its appointment of Studio E on the Grenfell Tower refurbishment, but if he did, he was obviously mistaken. | Selection | Appointment | Mark Anderson
On 11 November 2013, Bruce Sounes sent Peter Maddison by email a revised set of contractual documents. | Contract | Appointment | Bruce Sounes
By 20 November 2013 the terms of Studio E’s appointment appear to have been agreed in principle but Mr Sounes could not recall whether a letter of appointment had ever been signed and Studio E was unable to find a copy of an agreement. Given the inability of either party to produce a signed copy of the terms of appointment, we think it very unlikely that a formal written agreement between Studio E and the TMO was ever signed. | Contract | Appointment | Bruce Sounes
It is clear to us that Studio E was appointed as lead consultant. As such, it had a duty to advise on the need for, and the scope of services to be provided by, consultants, specialists, sub-contractors or suppliers and to monitor the work of other consultants. | Contract | Appointment | Studio E
The RIBA Standard Conditions obliged Studio E to exercise reasonable skill, care and diligence in accordance with the normal standards of the architectural profession when performing its services. | RIBA | Skills | Studio E
By failing for purely financial reasons to follow the proper procurement process, the TMO deprived itself of the opportunity to appoint a firm of architects with relevant skills, knowledge and experience. | Procurement | Skills | KCTMO
In his email to Mr Kuszell dated 29 February 2012 Mr Sounes described Studio E as a “little green on process and technicality”. He therefore suggested “some rapid CPD” (i.e. continuing professional development). | Competence | Skills | Bruce Sounes
Both Mr Kuszell and Mr Sounes accepted that, given Studio E’s lack of relevant experience, if a competitive procurement process for architectural services had been undertaken in relation to the Grenfell Tower project, it was unlikely that Studio E would have qualified for appointment. | Competence | Skills | Studio E
Chapter 53 Planning the Refurbishment
19th April 2012 initial budget for full cost of works at £6m. | Budget | Costs | Finance
2nd May 2012 Simon Cash wrote to Mark Anderson offering to perform quantity surveying, employer's agent and CDM Co-ordinator services. | Quantity Surveying | CDM | Simon Cash
21st Aug 2012 Mark Anderson confirmed TMO wished to appoint Artelia to carry out functions as per 2nd May 2012. | Procurement | Artelia | Mark Anderson
23rd Jun 2014 Artelia and TMO executed a formal deed of appointment incorporating RICS standard terms. | Procurement | Artelia | Mark Anderson
Based on estimates provided by Studio E, Curtins Consulting and Max Fordham, between June and Dec 2012, Chweechen Lim prepared cost budgets as Quantity Surveyor for Artelia which came to between £7.8m and £9.6m. 2nd Design Team meeting on 24th May 2012. | Quantity Surveying | Artelia | Chweechen Lim
3rd Design Team meeting on 7th June 2012, Mark Anderson funding as £6m to estimate of £7.8m but Anderson expected further funds to be made available. | Budget | Costs | Mark Anderson
Increased by Dec 2012 to £9.6m due to changes to the scope of works and corrections of errors in measurements. | Budget | Costs | Mark Anderson
In mid Dec, Lim had costed the project at £9.28m. Artelia and Studio E requested savings via reducing scope or by value engineering. | Budget | Costs | Studio E
TMO had planned to use Leadbitter Group from KALC via IESE (Improvement and Efficiency in the South East) framework agreement as alternative to procurement. | Procurement | Costs | Leadbitter
Efforts by Anderson to persuade the TMO to appoint Leadbitter continued until at least Nov 2012. | Procurement | Costs | Leadbitter
Leadbitter could not agree final account for KALC, Laura Johnson advised wouldn’t use Leadbitter for Grenfell project due to this on 3rd Jan 2013. | Procurement | Costs | Laura Johnson
IESE framework is two stage, select contractor from eight on framework list then negotiate with that contractor to agree a price. Leadbitter already chosen so needed to agree price. | Procurement | Costs | Leadbitter
Leadbitter indicated Artelia's cost estimate for project to be £2m too low. Mohit Kotecha as a Quantity Surveyor estimated £12.6m. Lim and Kotecha met. | Procurement | Costs | Leadbitter
Artelia attempted to test cost assessments by approaching various contractors who had procurement framework agreements with RBKC. | Procurement | Costs | Artelia
At suggestion of Peter Maddison in Apr 2013, Artelia also approached Rydon, even though they were not in any available framework agreements. | Procurement | Costs | Peter Maddison
By Apr 2013 considered cladding together with the crown and construction of the new windows could be reduced in costs. | Procurement | Costs | KCTMO
Artelia was to provide formal advice on how to proceed with Grenfell project, exactly a year after the first project team meeting. | Procurement | Costs | Artelia
Status report by Artelia on 23rd Apr 2013 recommended that TMO should retain Leadbitter as principle contractor. Maddison confirmed budget of £8.5m. | Procurement | Costs | Artelia
On 21st May 2013, Johnson overruled Maddison in no longer keen to appoint Leadbitter, value for money was more important to RBKC (according to Robert Powell). | Procurement | Costs | Laura Johnson
Decision to put contract out for tender again. Powell's email from 'programme' to 'value for money.' Finding lower cost contractor to that of Leadbitter. | Procurement | Costs | Robert Powell
On 24th May 2013, Artelia made addendum to their report to show value for money to be the key driver. Powell to Cash described this as 'political lubrication.' | Procurement | Costs | Artelia
Value for Money Project Brief was approved by TMO on 6th June 2013 (with some adjustments). Maddison said to Artelia to change Addendum to show new procurement = VFM. | Procurement | Costs | Peter Maddison
Artelia firmly recommended using EU procedure rather than framework agreement and criticisms watered down of TMO with focus on Leadbitter. | Procurement | Costs | Artelia
Cash reluctant to amend criticisms of the TMO by Artelia but under pressure by Maddison due to either 'strong' or 'frank' influence of Maddison. | Procurement | Costs | Peter Maddison
David Gibson's email to Claire Williams said "TMO had to twist Artelia's arms quite hard' so that a revised report could be made. TMO pressured Artelia. | Procurement | Costs | David Gibson
20th Jun 2013 Maddison relied on the advice expressed by Artelia for TMO board on 20th Jun 2013. Board agreed new procurement for £9.78m cost. | Procurement | Costs | Peter Maddison
Jenny Jackson lead the new procurement process with Artelia's assistance. TMO published notice of intention to award contract on 20th Aug 2013. | Procurement | Costs | Artelia
22 expressions of interest with only 5 potential bidders returning responses to the Pre-Qualification Questionnaire. | Procurement | Costs | KCTMO
Mulalley & Co, Keepmoat, Durkan, Rydon and Wates Construction, passed Pre-Qualification evaluation. Leadbitter did not tender. | Procurement | Costs | KCTMO
Wates and Keepmoat pulled out, other three submitted tenders. Rydon's was significantly lower than Durkan and Mulalley. | Procurement | Costs | Rydon
Confirmed Rydon was lowest price and achieved highest score on quality. All prices for external façade were substantially higher than Artelia's estimate. | Procurement | Costs | Rydon
Evaluation was 40% on price, 60% on quality of which 55% was attributed to written submissions and 5% to interview. Rydon's was most competitive. | Procurement | Costs | Rydon
Residents not invited to contribute questions about programming or quality, even though those matters would have affected them. | Procurement | Costs | KCTMO
Cllr Blakeman suggested to Maddison on 21st Feb 2014 that some residents should attend interviews with those who had submitted tenders. | Procurement | Costs | Peter Maddison
Only a few residents were involved in the process. | Procurement | Costs | Peter Maddison
Artelia sought TMO's permission to carry out a value engineering exercise with Rydon around mid Mar 2014. | Procurement | Value Engineering | Rydon
On 18th Mar 2014, TMO and Rydon agreed that if Rydon were awarded the contract it would reduce its price. | Procurement | Value Engineering | Rydon
TMO considered internally that a reduction could be achieved through the "value engineering" clauses in the proposed building contract. | Procurement | Value Engineering | Rydon
TMO and Rydon discussions took place when procurement process had not completed, TMO could not provide any reasonable justification. | Procurement | Legal Breach | Rydon
Those involved in the meeting knew or should have known that what they were doing was improper. | Procurement | Legal Breach | Rydon
Simon Lawrence explained to Mike Albiston of Harley that Rydon was alive to the risk that other prospective main contractors might challenge procurement process on the grounds that they had not been given a similar opportunity to engage in the value engineering process. | Procurement | Legal Breach | Simon Lawrence
Steve Blake said that he never considered the potential for challenge by other contractors, and denied having any knowledge of Lawrence's concerns. | Procurement | Legal Breach | Steve Blake
18th March 2014 was organised by Blake and he was driving force at Rydon behind the value engineering. | Procurement | Value Engineering | Steve Blake
No thought at all given in asking RBKC to increase the budget so that would meet Rydon's tender price. In July 2013 RBKC did increase from £6m to £9.7m. | Procurement | Costs | RBKC
In July 2014, RBKC had agreed to increase budget to £10.3m, without any apparent reluctance or obvious opposition from within the cabinet. | Procurement | Costs | RBKC
On 18th Mar 2014, Rydon was told it had won the contract. 27th Mar 2014, Maddison presented paper to TMO board, he recommended entering a 'pre-contract arranagement with Rydon' to reduce price in particular by changing cladding material and securing government funding for energy efficiency. | Procurement | Costs | Peter Maddison
Maddison said he had confidence in Rydon's pricing and that any problems with the budget would be addressed during the pre-contract period. Maddison disagreed with minutes. | Procurement | Costs | Peter Maddison
Based on Maddison's assurance, TMO board agreed to appoint Rydon as principle contractor. Agreed to cover prelim work up to £350k and £9.7m inclusive of fees. | Procurement | Costs | Peter Maddison
On 19th Jun 2014, Johnson requested budget increase to £10.3m as including contingency, cabinet agreed with executive decision issued by Cllr Feilding Mellen in Aug 2014. | Procurement | Costs | Laura Johnson
Rydon and the TMO were seeking to persuade the planning committee to accept riveted fixing for cost reasons. In the event, however, the committee insisted on the cassette version. | Cladding | Costs | Rydon
On 28th Feb 2014, Artelia offered for TMO to review and advise on decisions made by principle contractor. Due to process called 'novation.' | Novation | Costs | Artelia
Risk that a design agreed with employer before the contractor appointed may be watered down as a result of commercial pressures. | Novation | Costs | Artelia
In early Feb 2014, TMO and Artelia via Jenny Jackson were negotiating amendments to Artelia's appointment. | Procurement | Costs | Artelia
Artelia proposed Richmal Hardinge be appointed as she was an architect and had acted as client design adviser to RBKC on KALC and had drafted Grenfell proposal. | Procurement | Costs | Artelia
Hardinge proposed she would provide a 'Design Compliance Report' before the contract was awarded. Also would review contractor drawings but exclude any M&E issues. | Procurement | Costs | Artelia
Gibson and Williams on behalf of TMO agreed to appoint a client design adviser on 15th Jul 2014. | Procurement | Design Advisor | David Gibson
However on 29th Aug 2014, TMO decided to perform the role of client design adviser itself. Williams set out TMO's reasons including cladding and M&E were under guarantee. | Procurement | Design Advisor | Claire Williams
TMO overestimated its ability to scrutinise the design work and chose to overlook fact that no one within TMO had experience of project involving high rise cladding. | Procurement | Design Advisor | Claire Williams
TMO's decision not to appoint a client design adviser at modest expense seen as foolish and reflected over confidence to manage design projects itself. | Procurement | Design Advisor | Claire Williams
Chapter 54 Fire Safety Strategies, the Contribution of Exova
Exova was the fire engineer for the Grenfell Tower refurbishment. Instructed by Studio E before for the KALC project. | Procurement | Fire Safety | Studio E
Exova instructed by KCTMO to work on the Grenfell Tower but reported to Studio E, no fresh tender or selection exercise for fire engineering services for the project. | Procurement | Fire Safety | KCTMO
Exova appointed as was seen as known and trusted due to its KALC project work. For some reasons Exova's services were not transferred to Rydon. | Procurement | Fire Safety | KCTMO
Fire engineering is “the application of scientific and engineering principles, rules, and expert judgment, based on an understanding of the phenomena and effects of fire and the reaction and behaviour of people to fire, to protect people, property and the environment from the destructive effects of fire.” | Principle | Fire Safety | Exova
The creation of an effective fire safety strategy therefore calls for high standards of skill, knowledge and professional experience. Protection and preservation of life. | Principle | Fire Safety | Exova
Good fire safety strategy should address all relevant design questions for fire safety including "surface spread of flame requirements for surface materials", "fire compartmentation requirements, including fire-stopping and cavity barriers" and "external fire spread". FIA guidance note also makes clear that work of fire engineer will often be linked to RIBA stages. | Principle | Fire Safety | Exova
Dr Lane evidence whereby any reasonably competent fire engineer instructed to produce fire safety strategy would have appreciated that they were a "designer" within the meaning of the CDM Regulations 2007. As a designer preparing a fire safety strategy, a fire engineer is under a duty to take reasonable steps to avoid forseeable risks to health and safety of any person liable to be affected by the construction work, including the residents of any occupied building undergoing refurbishment work. | CDM | Fire Safety | Barbara Lane
Apr 2012 Studio E began to send Exova information about the Grenfell Tower refurbishment project, including architectural drawings. | Architect | Fire Safety | Studio E
19th Apr 2012 James Lee attended a design team meeting at which Bruce Sounes made it clear that refurbishment would include the overcladding of the entire building. | Design | Cladding | Bruce Sounes
03rd May 2012 Sounes sent email to Terence Ashton and James Lee, site photos and setting out likely scope of project. Requested fee proposal from Exova. | Design | Fire Safety | Exova
09rd May 2012 Ashton response quoted £3,300 for RIBA Stage C and £5,300 for RIBA Stages D-E. Artelia accepted on behalf of KCTMO on 1st Nov 2012. | RIBA | Fire Safety | Terence Ashton
Throughout May 2012 further exchanges between Sounes and Ashton. Lee visited tower on 29th May 2012. | Survey | Fire Safety | James Lee
11th Jun 2012 Lee sent Sounes fee proposal for production of an existing fire safety strategy (relate to existing building's state). Detailed scope of work for fee of £2,865. | Survey | Fire Safety | James Lee
Lee left Exova on 20th July 2012 before proposal had been accepted. | Survey | Fire Safety | James Lee
26th Jul 2012, Dr Clare Barker, a Principle Consultant at Exova, attended a Grenfell project meeting at request of Sounes. No existing fire safety strategy existed. | Fire Safety Strategy | Fire Safety | Clare Barker
Dr Barker in late Jul 2012 aimed for existing fire safety strategy to Studio E by 16th Aug 2012. She instructed Cate Cooney on 7th Aug 2012 to produce first draft. Cooney had produced existing fire safety strategies for only a small number of buildings since joining Exova, wasn't sure how many of those had been for high-rise residential blocks. | Fire Safety Strategy | Fire Safety | Cate Cooney
Cooney had limited information from Barker and also not had the Significant Findings and Action Plan of the 2010 FRA, nor did she ask for them. | Fire Safety Strategy | Fire Safety | Cate Cooney
9th Aug 2012 Sounes confirmed to Cooney there was no fire-fighting lift. Shortly after she received a copy of the FRA dated 29th Dec 2010 prepared by Carl Stokes which wrongly described the lifts as "fire fighting lifts". Cooney saw inconsistency but preferred FRA of Stokes. Cooney should've clarified and this was a mistake by her. | Fire Safety Strategy | Fire Safety | Cate Cooney
Does not seem like Lee and Cooney had any discussions, some photos were made available to her, Cooney had not visited Grenfell for survey. | Fire Safety Strategy | Fire Safety | Cate Cooney
Barker only member in Exova engaged on Grenfell that qualified as Chartered Engineer, her involvement was limited to cursory review of draft existing Cooney's fire safety strategy. | Fire Safety Strategy | Fire Safety | Clare Barker
Cooney did not provide Barker with FRA or Sounes exchanges, provided Barker with draft existing fire safety strategy. | Fire Safety Strategy | Fire Safety | Cate Cooney
Cooney appeared to have completed work hurriedly for the task. Barker did not give that much of a detailed response to Cooney. | Fire Safety Strategy | Fire Safety | Cate Cooney
Barker as she hinted, had deliberately posted the time she spent on it to another project for a different client, that would have been a serious failing in billing and quite improper. | Fire Safety Strategy | Fire Safety | Clare Barker
30th Aug 2012 Sounes sent email to Ashton with copy to Barker saying needed to go through draft Existing Fire Safety Strategy, no discussion ever took place. | Fire Safety Strategy | Fire Safety | Bruce Sounes
Confusion and unclear if Barker, Ashton or Cooney was responsible. Draft Existing Fire Safety Strategy sent to Sounes on 16th Aug 2012 was never finalised and review intended to verify assumptions it contained and provide missing information did not take place. | Fire Safety Strategy | Fire Safety | Bruce Sounes
10th Sep 2012 Ashton and Sounes did not consider Existing Fire Safety Strategy in any detail at all. Ashton did not view completion of Existing Fire Safety Strategy as his responsibility. | Fire Safety Strategy | Fire Safety | Terence Ashton
Existing Fire Safety Strategy was based on an extremely brief (two-hour) site visit, no site inspection notes, fee of £2865 plus VAT charged for 3 1/2 days work. | Survey | Fire Safety | Exova
Dr Lane considered that four to six weeks work would have been more appropriate, no evidence that Mr Lee inspected the fire compartmentation. | Survey | Fire Safety | James Lee
Information available to Ms Cooney had been too limited to enable her to draft an effective fire safety strategy for the existing building. | Fire Safety Strategy | Fire Safety | Cate Cooney
Cooney should have listed all the information, setting out clearly what was needed in order to analyse the building properly. That would have included relevant fire safety policies, fire safety management policies and maintenance records. | Fire Safety Strategy | Fire Safety | Cate Cooney
Exova had not identified within draft Existing Fire Safety strategy any of the shortcomings or assumptions in the 2010 fire risk assessment by Carl Stokes. | Fire Safety Strategy | Fire Safety | Carl Stokes
Lane was critical of Cooney's failure to ask for significant findings which formed part of Mr Stokes 2010 fire risk assessment. | Fire Safety Strategy | Fire Safety | Cate Cooney
Nor had Exova explained steps it had taken to satisfy itself that contents of 2010 fire risk assessment were based on an accurate assessment of Grenfell. | Fire Safety Strategy | Fire Safety | Cate Cooney
Document did not adequately identify what further investigation was needed. | Fire Safety Strategy | Fire Safety | Cate Cooney
Document did not state whether means of escape were sufficient to satisfy requirements of Article 14 of the Fire Safety Order. | Fire Safety Strategy | Fire Safety | Cate Cooney
Did not tell KCTMO was action needed ot be taken under the Fire Safety Order in response to the existing condition of the building, in particular to condition of the doors, inoperability of smoke control system and status of the lifts. | Fire Safety Strategy | Fire Safety | Cate Cooney
No assessment of the width of the stairs or of the performance of the front doors to the flats, the doors to the stair or the lift doors. (Cooney not understanding that to fall within the scope of her instructions). | Fire Safety Strategy | Fire Safety | Cate Cooney
No sketches or drawings were provided to enable the reader to understand how the text related to the building. | Fire Safety Strategy | Fire Safety | Cate Cooney
Document contained no consideration of the characteristics of the people who occupied the building and evaluation of the needs of those who required assistance to evacuate in the event of a fire. | Fire Safety Strategy | Fire Safety | Cate Cooney
Document contained material errors and omissions that should never have been made by a competent fire engineer undertaking this sort of work, such as assumptions that there was a firefighting and evacuation lift. Errors of this kind should have identified by any competently conducted peer review. | Fire Safety Strategy | Fire Safety | Cate Cooney
Information available to Cooney was so limited, should have carried out a site visit, significant omissions, not least because they deprived Exova of a proper understanding of the means of escape from the tower. | Fire Safety Strategy | Fire Safety | Cate Cooney
Doubt that Cooney properly understood full extent of her task. Although fee proposal stated purpose of Existing Fire Safety Strategy was to inform the fire safety risk assessment and fire risk management plan, her understanding was that it was only one of a number of documents that would be used for that purpose. | Fire Safety Strategy | Fire Safety | Cate Cooney
Draft Existing Fire Safety Strategy failed to give clear advice of a kind that could affect or influence the management plan. | Fire Safety Strategy | Fire Safety | Cate Cooney
Cooney appeared to think that her role was simply to state whether the design of the building as it stood complied with the Building Regulations, not to provide information that would inform the management of fire safety. | Fire Safety Strategy | Fire Safety | Cate Cooney
Dr Barker's review of the draft was rushed, cursory and superficial, little better than rubber stamp. | Fire Safety Strategy | Fire Safety | Clare Barker
Mr Ashton asked Dr Barker whether she was taking over the project, no reply was received. Dr Barker seems to have thought that he had assumed responsibility for the work from early September. However he failed to take any steps to complete the document, apparently in the understanding that she had retained responsibility for it. Serious failure in Exova's management processes. | Fire Safety Strategy | Fire Safety | Terence Ashton
Explains why Ashton did not discuss draft with Sounes, but it does not excuse his failure to carry the work forward. | Fire Safety Strategy | Fire Safety | Terence Ashton
Neither Exova, Studio E or KCTMO appears to have asked why the document was no more than a draft or when completed version would be available. | Fire Safety Strategy | Fire Safety | Exova
Exova failed, Existing Fire Safety Strategy ought to have provided a precise record of the baseline condition of the fire safety at Grenfell. | Fire Safety Strategy | Fire Safety | Exova
Without understanding the existing condition of the building, it was impossible to understand full extent of fire safety refurbishment. | Survey | Fire Safety | Exova
Document failed to record the condition of the building in its existing state and did not provide a reliable baseline for creation of fire safety strategy for the refurbishment. | Survey | Fire Safety | Exova
Cooney also involved in some of the other fire safety aspects of the refurbishment. | Fire Safety Strategy | Fire Safety | Cate Cooney
Sounes asked her to advise on the introduction of residential units on the mezzanine floor of the building for the purpose of a submission to RBKC's planning department the following week. | Fire Safety Strategy | Fire Safety | Cate Cooney
Cooney sent Andrew Martyn (senior consultant at Exova) an email to which she attached plans showing layout of the new flats. | Fire Safety Strategy | Fire Safety | Cate Cooney
Email of the existing condition of the building raised concerns about fire safety, proposed refurbishment would increase concerns, and proposals could be altered to make them satisfactory from perspective of building control but would remain a risk that approval would be refused because of dissatisfaction with the fire-fighting shaft and the means of escape. | Fire Safety Strategy | Fire Safety | Exova
Cooney denied use of word "massage" had been intended to mean anything more than "change". | Fire Safety Strategy | Fire Safety | Cate Cooney
Cooney denied any suggestion that she had used the word in the sense of manipulation or sleight of hand in order to get the designs past building control. | Fire Safety Strategy | Fire Safety | Cate Cooney
Accepted that Cooney's intention was to propose substantive changes to the design to make it more acceptable to building control in accordance with the Building Regulations. | Fire Safety Strategy | Fire Safety | Cate Cooney
Her proposal was to introduce "new measures" to reduce the risk of building control's refusing approval. | Fire Safety Strategy | Fire Safety | Cate Cooney
Her view "that the refurbishment was making a crap condition worse". | Fire Safety Strategy | Fire Safety | Cate Cooney
Given seriousness of the concerns we would have expected Exova to have communicated them directly to the TMO, short of standard for a reasonable competent fire engineer. | Fire Safety Strategy | Fire Safety | Exova
Problem in a building with a single stair and limited smoke exhaust to the lobbies. | Fire Safety Strategy | Fire Safety | Exova
Culture of Exova of "making things work and getting things through". Approach in getting building control approval than on people's safety. | Fire Safety Strategy | Fire Safety | Exova
Cooney's email of 10th Sep 2012 to Mr Ashton "existing ventilation system is questionable and overall scheme makes existing conditions worse by adding the additional risk of 2, no extra residential floors to the building, proposed to upgrade the ventilation system, but the standard it will achieve is unknown". Significant approvals risk with the current proposals. | Fire Safety Strategy | Fire Safety | Cate Cooney
Mr Ashton did not visit the tower, recommended by Sounes in May 2012 that should for the Design Note, Ashton said "he had other priorities". | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton only became familiar with tower due to drawings by Studio E. Did not look at Mr Lee's photographs and did not have Mr Lee's notes. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton no conversations with Mr Lee about building layout or plans to overclad, no formal handover, made no enquiries of TMO building maintenance team before his work. | Fire Safety Strategy | Fire Safety | Terence Ashton
If Mr Ashton did actions he failed then may have got important information e.g. smoke control system not functioning, lifts not firefighting lifts. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton did not make use of planning drawings which Mr Sounes had sent to him. | Fire Safety Strategy | Fire Safety | Terence Ashton
Five functional requirements to fire safety in Schedule 1 of Building Regulations 2010. Design note only dealt with B1 (Means of Warning and Escape) and B5 (Access and Facilities for the Fire Service). | Building Regulations | Fire Safety | Exova
Design Note had no analysis of B4 and no reference to cladding. | Design Note | Fire Safety | Exova
Design Note indicated that existing smoke control system for lobbies did not comply and needed to be refurbished/modified. Didn't describe condition of system. | Design Note | Fire Safety | Exova
Mr Ashton did not spell out in Design Note that there was significant risk that proposals would not receive building control approval. | Design Note | Fire Safety | Terence Ashton
Mr Ashton did not in Outline Fire Safety Strategy advise that sprinklers might be necessary, not discussed. Design Note serving residential accommodation should not also serve non-residential accommodation, it might be necessary to provide sprinkler or water mist systems to boxing club/office suite. | Design Note | Fire Safety | Terence Ashton
Dr Lane critical of Design Note to RIBA Stage C with respect to fire safety, produced in haste for deadline. | Design Note | Fire Safety | Barbara Lane
Design Note only dealt with B1 and B5, inadequate guidance to design team on all aspects of fire safety. | Design Note | Fire Safety | Exova
Mr Ashton not aware that Outline Fire Safety Strategy needed to be issued as same time as the other RIBA Stage C reports. | Fire Safety Strategy | Fire Safety | Terence Ashton
Nowhere in Issue 1 of the Outline Fire Safety Strategy did Exova state that the refurbishment included overcladding of the building | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton was well aware by that time this constituted an important feature of the works. | Fire Safety Strategy | Fire Safety | Terence Ashton
The document contained no reference to the application of requirement B3 to the external wall (unseen spread of fire in concealed spaces). | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton already had some information about the external wall build-up, having received a draft of potential work packages from Adrian Jess of Studio E. | Fire Safety Strategy | Fire Safety | Terence Ashton
Studio E produced RIBA Stage C report on 31st Oct 2012 including Mr Ashton, later on during day Exova sent Issue 1 of Outline Fire Safety Strategy to Studio E. | Fire Safety Strategy | Fire Safety | Terence Ashton
If Mr Ashton had read the Stage C report carefully, he would've seen that tower was to be overclad with various options being considered including zinc and aluminium, he would also have seen Celotex FR5000 was proposed as insulation in external wall. | Fire Safety Strategy | Fire Safety | Terence Ashton
16th Nov 2012, Studio E sent Mr Ashton link to File Transfer Protocol of current drawings. Mr Ashton did not see this, regrettable. | Fire Safety Strategy | Fire Safety | Terence Ashton
Dr Lane said Outline Fire Safety Strategy would expect reasonably competent fire engineer to set out, as bare minimum, statutory guidance relating to insulation, cavity barriers, and external surface, with references to Approved Document B. | Fire Safety Strategy | Fire Safety | Barbara Lane
Requires making clear the performance required of each of the separate elements of the external wall. | Fire Safety Strategy | Fire Safety | Barbara Lane
Exova could properly have made it clear that it had no information about the proposed cladding. | Fire Safety Strategy | Fire Safety | Terence Ashton
Considered that to express even a provisional opinion without the benefit of any information about the cladding was unacceptable. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton nor anyone else at Exova had any information about the proposed cladding, no attempt made to analyse proposals for external wall. | Fire Safety Strategy | Fire Safety | Terence Ashton
Exova had no basis for expressing an opinion, even provisionally, that proposed work would have no adverse effect on the building in relation to external fire spread. | Fire Safety Strategy | Fire Safety | Terence Ashton
Such a statement was bound to lead Studio E and TMO to assume that, unless it was later withdrawn or modified, they could be confident that the building would comply with functional requirement B4 and be safe for occupation. | Fire Safety Strategy | Fire Safety | Terence Ashton
Dr Lane said this fell well short of standards expected of a competent fire engineer. | Fire Safety Strategy | Fire Safety | Barbara Lane
After Issue 1 of Outline Fire Safety Strategy in Oct 2012, Mr Ashton took lead with building control for fire safety aspects of Grenfell. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton sent Issue 1 of Outline Fire Safety Strategy directly to John Allen on 31st Oct 2012. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton organised meeting at Kensington Town Hall on 6th Nov 2012 with Mr Jess and Mr Allen and Dave Gammon (latter two of RBKC Building Control). | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton said RBKC Building Control could be difficult to deal with. | Fire Safety Strategy | Fire Safety | Terence Ashton
Unlikely overcladding was discussed or even mentioned. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton met Building Control again on 17th Sep 2013, again unlikely overcladding was discussed. | Cladding | Fire Safety | Terence Ashton
Issue 2 of the Outline Fire Safety Strategy 24th Oct 2013, written by Mr Ashton and reviewed by Dr Tony Pearson (Senior Consultant). | Fire Safety Strategy | Fire Safety | Terence Ashton
Produced following a meeting with building control on 17th Sep 2013. | Fire Safety Strategy | Fire Safety | Terence Ashton
Studio E's Stage D report had included Issue One of Exova's Outline Fire Safety Strategy at Appendix D, Mr Ashton unaware of this. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton had not also read Stage C report, hence why neither of the reports was referred to in Issue 2 of the Outline Fire Safety Strategy. | Fire Safety Strategy | Fire Safety | Terence Ashton
If Mr Ashton had read the Stage D report, he would have seen the reference to the zinc composite rainscreen proposed for upper levels, cladding images and celotex FR5000 reference. Mr Ashton out of step. | Fire Safety Strategy | Fire Safety | Terence Ashton
Dr Pearson had not seen on Issue 2 of Outline Fire Safety Strategy the minutes of discussions with building control and draft Existing Fire Safety Strategy. | Fire Safety Strategy | Fire Safety | Tony Pearson
Dr Pearson unaware of RIBA process the report was being written for. | RIBA | Fire Safety | Tony Pearson
Dr Pearson did not know Studio E had issued its Stage C report in Oct 2012 and Stage D report in Aug 2013. | Fire Safety Strategy | Fire Safety | Tony Pearson
Issue 2 of the description of the refurbishment had been amended but not made reference to overcladding of the tower. | Cladding | Fire Safety | Tony Pearson
Mr Ashton said Exova had still not given any consideration to the cladding, drawings on Issue 2 not show any details of external wall construction. | Cladding | Fire Safety | Terence Ashton
Dr Pearson not aware at that time that refurbishment included overcladding not any knowledge of arrangements proposed at top of the tower. | Cladding | Fire Safety | Tony Pearson
Explains why Dr Pearson had no concern about the treatment in the report of functional requirement B4. | Cladding | Fire Safety | Tony Pearson
Exova not referred to performance requirements of external wall or external fire spread. | Cladding | Fire Safety | Exova
Dr Pearson unaware that Mr Ashton had no experierence of advising on cladding work on high-rise residential buildings. | Cladding | Fire Safety | Terence Ashton
Dr Pearson failed to notice that the document incorrectly stated that the floors should provide at least 60 minutes' fire resistence. | Cladding | Fire Safety | Tony Pearson
No changes were made to section covering functional requirement B3 (internal fire spread), still no guidance on cavity barriers. | Fire Safety Strategy | Fire Safety | Exova
Dr Pearson not concerned that second issue of Outline Fire Safety Strategy failed to identify concealed spaces or places where cavity barrier would be needed. | Fire Safety Strategy | Fire Safety | Tony Pearson
Mr Ashton irritated by mixed use issue for non residential and residential merging of the stairs as highlighted by Dr Pearson, fundamental breach of Building Regulations. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton's attitude in hoping building control would not notice above fell below standard expected of competent fire engineer. | Fire Safety Strategy | Fire Safety | Terence Ashton
When Mr Ashton produced Issue 3 of the Outline Fire Safety Strategy in Nov 2013, he retained the statement that “sharing means of escape between residential and non-residential accommodation is not endorsed by current statutory guidance”, but deleted from section 3.1.1 the statement that the proposals represented “a continuation of the existing principles for means of escape in the building and therefore do not create a non-compliance with the requirements of the Building Regulations”. | Fire Safety Strategy | Fire Safety | Terence Ashton
Studio E sent Issue 2 of the Outline Fire Safety Strategy to building control by email on 25th Oct 2013. John Allen responded on 11th Nov 2013, saying that the information submitted was not adequate to enable an effective consultation to be had with the fire authority. Mr Ashton thought that building control’s concerns related to Max Fordham’s work in designing the smoke control system, and that it was therefore Max Fordham’s responsibility to provide whatever additional information was required. There is nothing in the email to suggest that building control considered the proposals to be unacceptable because they failed to address functional requirements B3 and B4. | Fire Safety Strategy | Fire Safety | Terence Ashton
Dr Lane said that she would have expected a reasonably competent fire engineer about to produce a fire safety strategy for RIBA Stage E to have asked for the Stage D report for use as a reference guide and to check the sections that were relevant to its work. In her opinion Mr Ashton’s failure to obtain the latest information at that stage of the design process fell short of what could be expected of a reasonably competent fire engineer who could be expected to obtain any information needed to complete its work. | RIBA | Fire Safety | Barbara Lane
Exova’s failure to review the statement in relation to functional requirement B4 was again the subject of criticism by Dr Lane, who was critical of its failure to provide the guidance that in her view should have been included in Issue 1. | Fire Safety Strategy | Fire Safety | Barbara Lane
We find it very surprising that no one at Exova recognised that the statement relating to functional requirement B4 had not been properly resolved. Mr Ashton’s explanation that he had not been provided with the information he needed in order to deal with it was in our view a poor excuse. | Fire Safety Strategy | Fire Safety | Terence Ashton
Correspondence with Studio E before Issue 3. Tomas Rek of Studio E sent an email to Mr Ashton asking him to confirm that the rainscreen cavity barriers were to have 60 minutes’ fire resistance to match that of the compartmentation. Mr Ashton’s response on 4 Nov 2013 was brief, stating simply that cavity barriers needed to have only 30 minutes’ fire resistance. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton did not check Approved Document B before giving that advice because, he claimed, he had known the answer off the top of his head. Nor did he consider it necessary to advise Mr Rek of the performance requirements set out in Approved Document B for the external wall or the required locations of cavity barriers. Although he did not have any details of the rainscreen to which Mr Rek had referred, he did not ask for further information since he assumed that it might be forthcoming in the not too distant future. | Fire Safety Strategy | Fire Safety | Terence Ashton
Issue 3 of the Outline Fire Safety Strategy was produced on 7 Nov 2013, less than two weeks after Issue 2. It had been prepared by Mr Ashton and reviewed by Mr McEleney. The stated reason for the revision was to take into account comments from the design team. The document was said to be based upon discussions held with the design team and building control and on unidentified fire access and fire strategy drawings produced by Studio E. Exova did not provide a set of fire strategy drawings to accompany Issue 3. | Fire Safety Strategy | Fire Safety | Terence Ashton
Dr Lane was critical of that omission, and explained that anyone reading the report would need both the detailed information on the drawings and the narrative in the report in order to understand the basis for the fire safety design. | Fire Safety Strategy | Fire Safety | Barbara Lane
Again, Exova failed to specify for which RIBA stage the document had been written. Mr Ashton thought that it was another version of one intended for Stage D, but Mr Sounes said it had related to Stage E. Mr Ashton had still not seen either the Stage C or Stage D report. | RIBA | Fire Safety | Terence Ashton
The introduction to Issue 3 described the refurbishment works and, as in the case of Issues 1 and 2, made no mention of the overcladding. The wording of the section covering B4 (external fire spread) also remained the same. Mr Ashton explained that nothing had changed since the previous issue because he still had not been given the details of the external wall. He said that Exova had been disengaged from the design team for a number of months between Issues 1 and 2 and that the project had “gone a bit cold”. He had been expecting a discussion, but none had taken place by the time the document had been produced. | Cladding | Fire Safety | Terence Ashton
By contrast, Mr Sounes said he had expected Mr Ashton to ask if he needed any further information to enable him to provide the advice covered by Exova’s Fee Proposal, including any necessary drawings, details or specifications. In oral evidence, Mr Ashton accepted that Exova should have pursued Studio E more vigorously for information about the external walls, but he rejected the suggestion that retaining the original wording without any clarification was an abdication of its responsibilities as fire strategy consultant for the project. | Cladding | Fire Safety | Terence Ashton
In common with Issue 2, Issue 3 did not describe the fire performance materials needed to comply with functional requirement B4, nor did it set out the fire safety standards for the construction of external walls, which, according to Dr Lane, was the minimum Exova should have provided by way of advice. | Cladding | Fire Safety | Barbara Lane
Accordingly, it did not make it clear that the guidance in paragraph 12.7 of Approved Document B required any insulation product used in the external wall to be of limited combustibility. Mr Ashton explained that omission by saying that he did not include performance requirements as a matter of course in every report. He accepted that he had taken no steps before the production of Issue 3 to ascertain whether the cladding would or would not be likely to have an adverse effect on the building in relation to fire spread. | Insulation | Fire Safety | Terence Ashton
Similarly, Issue 3 contained no guidance on the need for cavity barriers nor any reference to the performance requirements for cavity barriers within external walls as set out in section 9 and paragraph 12.8 of Approved Document B, despite the fact that Tomas Rek had sought guidance on that very matter only days earlier. | Cavity Barrier | Fire Safety | Terence Ashton
Dr Pearson said that if he had been the author of the report he would have included a lengthy summary of the existing strategy, but Mr Ashton was not aware that the Existing Fire Safety Strategy (even though only in draft form) was intended to be the baseline from which the Outline Fire Safety Strategy was to be developed. | Cladding | Fire Safety | Terence Ashton
When addressing the means of escape and functional requirement B1, Mr Ashton advised that the design of the smoke control system would be covered in a separate report by Max Fordham. No performance requirements for the new smoke control system were set out, nor was the role of the system specified. | Smoke Control | Fire Safety | Terence Ashton
Issue 3 of the Outline Fire Safety Strategy did state that for the walkway, mezzanine and ground floor levels and in the lobby to the boxing club and community room, automatic opening vents of 0.4m² in area would be provided. As Mr Ashton accepted, that did not comply with the guidance in Approved Document B, because the size of the opening vents did not comply with BS5588-5:2004, but it was the best that could be achieved. He did not expressly refer to that shortcoming in the strategy because he had discussed it with building control, which appeared to be happy with it on that basis. | Fire Safety Strategy | Fire Safety | Terence Ashton
Similarly, there was no reference in the section dealing with functional requirement B1 to the fact that the width of the stairs at 1040mm was 60mm less than the 1100mm stated in Approved Document B, although Mr Ashton had been aware of the fact, having advised on the question by email in Oct 2013. He accepted that it could have been added to the narrative discussion in the report, but did not consider that to be necessary, since it was not practicable to alter the stairs, which in his view were perfectly adequate. | Fire Safety Strategy | Fire Safety | Terence Ashton
The strategy contained no advice that might have assisted the TMO in discharging its duties under the Fire Safety Order or any information about how the active and passive fire safety systems would need to be maintained in order to ensure compliance with the legislation. Nor did it contain any acknowledgement of the fact that the mixed-use nature of the building might result in there being more than one responsible person. Mr Ashton considered that that would be more appropriately addressed in a fire safety management plan. | Fire Safety Strategy | Fire Safety | Terence Ashton
Similarly, there was no consideration in the strategy of the means of escape for those in the tower with disabilities because Mr Ashton did not think that the law required designers to consider their position. He had therefore not asked for information about who was living in the building or who might be living there in the future. He said that he would not have expected to be given that information by the TMO unless there had been some particular reason to consider it, for example, if the building had been purpose-built for people with disabilities. | Fire Safety Strategy | Fire Safety | Terence Ashton
Issue 3 was the last version of the Outline Fire Safety Strategy produced by Exova for the Grenfell project and represented the culmination of its work on the refurbishment up to and including RIBA Stages D and E. Exova produced nothing commensurate with RIBA Stages E or F. | RIBA | Fire Safety | Exova
In the event, Exova never did produce a final version of the fire strategy. Mr Ashton did not consider Issue 3 to be the final version and accepted that a detailed fire strategy would have dealt with all the functional requirements from B1 to B5. He acknowledged that Issue 3 did not deal with a number of subjects, including an analysis of the external wall in relation to functional requirement B4. | Fire Safety Strategy | Fire Safety | Terence Ashton
He said that his intention at the time had been to produce the final version once he had received the necessary information from the design team; but he never asked Studio E for that information and allowed the matter to drift in the absence of any request from Studio E for a complete analysis. He did not regard completion of the fire safety strategy as a priority and he had a lot of other work on his hands at the time. | Fire Safety Strategy | Fire Safety | Terence Ashton
In retrospect he thought it surprising that he had had no contact with Studio E to discuss a compliance check of the design for the external wall, but he did not consider that it would have been appropriate for him to tell the TMO that further work was required. In the event, Exova never told Studio E or Rydon that further work needed to be done on the Outline Fire Safety Strategy. | Fire Safety Strategy | Fire Safety | Terence Ashton
Issue 3 of the Outline Fire Safety Strategy was expressly incorporated into the Design and Build Contract between the TMO and Rydon. Although Mr Ashton was aware that a document of that kind would usually be provided to the main contractor for information at the tender stage, he was not specifically aware that in this case it had been incorporated into the building contract. | Fire Safety Strategy | Fire Safety | Terence Ashton
Studio E also included Issue 3 of the Outline Fire Safety Strategy in the full plans application that was submitted to building control on 29 Sep 2014. Mr Ashton was not aware of that at the time, but he knew that it was standard practice to do so. | Fire Safety Strategy | Fire Safety | Terence Ashton
He also knew that it was unusual, when the work to a building was to include overcladding, for a fire safety strategy which did not deal with functional requirement B4 to be included in a full plans application. He said that it would have been “nice” if the final version had contained such an analysis, but it had not been included because it had not been considered. | Fire Safety Strategy | Fire Safety | Terence Ashton
Issue 3 of the Outline Fire Safety Strategy was produced at RIBA Stage E. According to Dr Lane, that was the time for the production of the final fire safety strategy which should have recorded the detailed proposals for the development, together with the promised analysis. However, Issue 3 did not represent any material advance on Issue 2 and Exova failed to produce any detailed and comprehensive fire safety strategy at any stage during the project. In Dr Lane’s opinion Issue 3 wholly failed to provide the fire safety design guidance required by the design team, the client and the contractor. | CDM | Fire Safety | Barbara Lane
Exova failed to provide any guidance on the performance standards for the external wall. Dr Lane described that as a serious omission, but in truth it was more than that; it represented a fundamental failure by Exova to provide the services for which it had contracted. The fact that the reports were provided to the architect rather than the lay client does not excuse that failure. Although Studio E was at fault in failing to ask questions about the Outline Fire Safety Strategy in any of its forms, and particularly in failing to ask Exova to provide a concluded opinion on functional requirement B4(1), that does not excuse Exova for failing to seek the information needed to complete its work or make it clear that without it an essential part of the strategy was missing. | Cladding | Fire Safety | Studio E
It was also of importance for Exova to draw attention to the fact that any insulation materials in the external wall should be of limited combustibility if the designers were following the guidance in paragraph 12.7 of Approved Document B. If that had been expressly stated, others engaged on the project, including Rydon and the TMO, might have thought twice about their choice of insulation. Again, the fact that others were unaware of that requirement does not exonerate Exova. | Insulation | Fire Safety | Exova
Given his acknowledgement that the overcladding was, in his own words, “a fairly significant part of the design”, his failure to include it in the description of the project and his subsequent failure to consider that aspect of the refurbishment fell below the standards to be expected of a reasonably competent fire engineer. | Cladding | Fire Safety | Terence Ashton
None of the issues of the Outline Fire Safety Strategy contained any reference to the need for cavity barriers. When Mr Ashton prepared Issue 3 in Nov 2013 he had had his attention specifically drawn to the fact that there was to be a rainscreen cladding system in an email from Tomas Rek on 1 Nov 2013. That email ought to have alerted Mr Ashton to the need to address cavity barriers in the fire safety strategy, since it should have been clear to him that the design team needed his help in understanding the basic performance requirements for the external wall. In those circumstances we consider that Mr Ashton’s failure to address cavity barriers and their locations fell below the standard of a reasonably competent fire engineer. | Cavity Barrier | Fire Safety | Terence Ashton
Regardless of whether it had mentioned the matter to Rydon, Artelia should have drawn the attention of the TMO to the fact that Exova’s work had not been completed but failed to do so. At no time did Mr Booth or anyone else at Artelia alert the TMO to the need to ensure that the fire safety strategy had been completed by a suitably qualified fire engineer. The safety of the cladding was therefore never considered by a fire engineer | Cladding | Fire Safety | Artelia
During numerous meetings on the project between Apr and Oct 2014 Rydon expressed an intention to engage Exova as consultant fire engineer, as is formally recorded in the minutes of those meetings, but no one on behalf of Rydon contacted Exova for that purpose. In the event, Rydon did not appoint Exova as a consultant and there is no evidence that anyone from Exova attended any design team meetings after 6 Sep 2012. | Fire Engineer | Fire Safety | Rydon
However, between 1 Apr 2014, when Rydon was proposed as principal contractor and 24 Mar 2016, Exova continued to provide advice to Studio E, Rydon and its subcontractors on aspects of fire safety and Mr Ashton was sent or copied in to at least 40 emails. | Fire Safety Strategy | Fire Safety | Exova
Rydon’s attitude towards advice from Exova is evident from an email sent by Simon Lawrence to Neil Crawford on 19 Sep 2014. Mr Lawrence had noticed Exova’s inclusion in an e-mail chain and had questioned its continued involvement in the project. He wrote: “I know that they provided information in the tender for KCTMO but I don’t know if they are still working for them. I know that we haven’t employed them. So if you are getting some free advice then great otherwise we will need to look at this.”At this point, according to Simon Lawrence, Rydon had not decided whether a fire consultant was needed. It wanted to understand the strategy relating to the lower four floors before making a decision about the services they needed and wanted to obtain the views of building control, which it regarded as a “resource." During Progress Meeting No. 4 on 21 Oct 2014 Rydon again indicated that it would appoint a fire consultant and the item remained on the agenda because Artelia retained it as a matter calling for decision by Rydon. | Fire Engineer | Fire Safety | Rydon
By the time of Progress Meeting No. 5 on 18 Nov 2014, however, the reference to Rydon’s intention to appoint a fire consultant had disappeared from the minutes. Claire Williams did not notice that and said she would have expected Artelia, as Employer’s Agent, to pick it up. Philip Booth said that the usual practice was for an item to remain on the minutes until it had been completed or resolved and that he could not recall how that particular item had been allowed to disappear. | Fire Engineer | Fire Safety | Rydon
Bruce Sounes recalled a conversation with Simon Lawrence in Mar or Apr 2014 during which Mr Lawrence had said that Rydon typically did not engage fire consultants on the basis that the fire safety strategy had been established by the client’s team. Mr Lawrence did not recall that conversation, but agreed that it was a fair description of how Rydon typically dealt with such matters and did not quarrel with the substance of Mr Sounes’ evidence, which we accept. He explained that Rydon did not normally engage fire consultants because it was building control’s responsibility to raise any concerns over matters of that kind. | Fire Engineer | Fire Safety | Rydon
Mr Lawrence told us that Rydon had been looking for advice from a fire safety consultant only in relation to the lower four floors of the tower, but he accepted that there was nothing in the documents to suggest that it had drawn any distinction for that purpose between the restructuring of the lower four floors and the installation of the cladding. We therefore think it unlikely that that distinction was present to Mr Lawrence’s mind in 2014. He said that Rydon had made a positive decision not to appoint a fire safety consultant when it became clear that the lower four floors were not going to present a significant problem, but there was no evidence of when or how that decision was made or by whom. Stephen Blake told us that he and Simon Lawrence had decided not to appoint Exova as a consultant because it had already produced a fire safety strategy and because it was the responsibility of Studio E to make sure that it contained all the necessary information. | Fire Engineer | Fire Safety | Rydon
We think it likely that Rydon decided not to engage Exova, or any other fire safety consultant because it did not think that it needed to do so in its own interests. Rydon did not tell the TMO or Studio E that it had decided not to appoint a fire consultant and it seems that the matter then disappeared from sight. Artelia and the TMO should both have been aware that Rydon had not appointed a fire consultant and Artelia should have obtained a formal decision from Rydon and recorded it, together with the reasons for it, pursuant to its obligation to monitor Rydon’s performance. | Fire Engineer | Fire Safety | Rydon
The failure to ensure the effective involvement of a fire engineer in the project following the appointment of Rydon as principal contractor was in our view one of the most serious flaws in the design and execution of the refurbishment. When Rydon was appointed as principal contractor the TMO continued to retain Exova, but neither the TMO nor Artelia appears to have understood clearly what services it was expected to provide or to whom. Artelia’s duties included understanding where additional works by third parties were required. Artelia ought to have made it clear to the TMO that Exova’s work had not been completed, that Rydon had not appointed anyone to finish it and that the TMO itself would therefore have to ensure that it was completed. For its part, the TMO, ought to have clarified Exova’s position and ensured that the fire safety strategy was completed. | Princple Contractor | CDM | Rydon
Exova received no formal confirmation from the TMO that its services were no longer required, but Mr Ashton said that in his experience it was not unusual for Exova’s services not to be retained in that situation. We are surprised that Exova allowed client relations to be managed in such a casual manner, but the fact is that Mr Ashton never thought to ask for clarification of Exova’s position, even though he was still being asked for advice on various matters from time to time on an ad hoc basis. | Contract | Fire Safety | Terence Ashton
Despite approving the invoices which Exova submitted to the TMO, it did not dawn on Claire Williams that Rydon had not appointed a fire consultant. | Fire Engineer | Fire Safety | Claire Williams
Drawing number 1279 SEA (06) 120 also referred to “aluminium composite TBC”, but, despite not being familiar with composite materials, Mr Ashton did not ask what that meant. | Cladding | Fire Safety | Terence Ashton
Mr Ashton's advice was wrong insofar as it suggested that cavity barriers were required only if the insulation were combustible. In order to comply with Approved Document B cavity barriers were required around the windows and at the top of the walls, regardless of the type of insulation used. He also failed to point out that in a building of over 18 metres in height the insulation should be of limited combustibility in order to comply with paragraph 12.7 of Approved Document B. Mr Ashton accepted that his response could have been more clearly worded but in our view that suggests that he had not understood the significance of the nature of the insulation. | Cavity Barrier | Fire Safety | Terence Ashton
The drawings provided to Mr Ashton by Studio E also showed horizontal cavity barriers only between the windows and not around the window frames. He did not notice that omission, despite his understanding that Approved Document B contained clear guidance on the importance of cavity barriers around windows | Cavity Barrier | Fire Safety | Terence Ashton
Later the same day Neil Crawford sent another email to Mr Ashton attaching a datasheet for Celotex RS5000. He asked whether Daniel Anketell-Jones was right in thinking that, because the insulation was rated Class 0, cavity barriers were not required around the windows. Mr Ashton did not open the attachment and therefore did not read the datasheet. That was a serious error on his part. A reasonably competent fire engineer would have done so and, having read the datasheet, would have explained to Mr Anketell Jones that Class 0 did not denote limited combustibility. | Cavity Barrier | Fire Safety | Terence Ashton
It did not occur to him to ask Mr Crawford what type of rainscreen cladding panel was being proposed or to tell him that the Outline Fire Safety Strategy needed to be revised. | Cladding | Fire Safety | Terence Ashton
Mr Ashton had already received indications from a number of sources that Celotex RS5000 was being proposed for use on the tower but had apparently failed to absorb the information. If he had opened the datasheet and obtained advice from colleagues in Warrington with specialist knowledge of materials and their reaction to fire, it is likely that he would have alerted the design team to the risks involved. | Insulation | Fire Safety | Terence Ashton
Dr Lane was clear that Mr Ashton should have known that the insulation did not comply with the guidance contained in Approved Document B and that cavity barriers were missing. She said that they were “red flags” which should have prompted him to consider how the external wall was being assessed and how it could comply with functional requirement B. | Insulation | Fire Safety | Terence Ashton
Clash of evidence of Mr Ashton confirming various things to that what Mr Crawford describes, a lot of informality. | Fire Safety Strategy | Fire Safety | Terence Ashton
All those involved in the exchanges, including Exova, should have realised that the sections of the strategy relating to functional requirements B3 and B4 needed to be completed and that detailed and definitive guidance was required. Even if Mr Ashton could not complete that work without further information, at the very least he should have warned the project team and the TMO, his client, that important work was outstanding and that the current version of the strategy was materially incomplete. We can see no good reason why he did not do so and are satisfied that in failing to do so he fell short of the standard required of a reasonably competent fire engineer. | Fire Safety Strategy | Fire Safety | Terence Ashton
Dr Lane’s view, this correspondence should have prompted Mr Ashton to ask for the information he needed to complete the Outline Fire Safety Strategy, but regrettably it did not do so. Mr Ashton did not consider that aluminium rather than zinc was being proposed. | Cladding | Fire Safety | Terence Ashton
Mr Ashton's failure to read down the short chain also meant that he failed to notice the reference to aluminium cladding cassettes and continued to labour under the misapprehension that the rainscreen panels would be composed of zinc. | Cladding | Fire Safety | Terence Ashton
If Mr Ashton had included in the Outline Fire Safety Strategy the minimum requirements in Approved Document B for satisfying functional requirement B4, those questions might not have arisen. Moreover, the design team might have been alerted to the need to analyse in more depth the choice of materials for use in the external wall of the tower. | Cladding | Fire Safety | Terence Ashton
The sections of the detailed fire safety strategy relating to functional requirements B3 and B4 should have answered those questions, given that there was clearly confusion within the design team about the difference between fire stops and cavity barriers. In this case there was a need for the fire engineer to explain what they were, what they were for, and where they needed to be incorporated into the building. | Cavity Barrier | Fire Safety | Terence Ashton
Those and some later exchanges with the design team in Sept 2014 should again have led Mr Ashton to realise that the fire safety strategy needed to be revised. As an absolute minimum he should have drawn attention to the fact that it was incomplete and asked for confirmation that he could complete it. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton did not identify the locations where cavity barriers were required in the external wall and he did not identify the performance criteria for the external wall set out in section 12 of ADB. | Cavity Barrier | Fire Safety | Terence Ashton
Mr Ashton said that his reference to the failure of the rainscreen in the event of a fire reflected his understanding that, although debris would fall from the building, the fire would not spread externally through the cladding as zinc is non-combustible. | Cladding | Fire Safety | Terence Ashton
Mr Ashton said that it did not occur to him in late Mar 2015 to revise the Outline Fire Safety Strategy because nothing he had seen had given him any cause for concern. He had not realised that the designers had been planning to use unsuitable materials. In any event, although it had been in his mind that he might need to revise it in due course, he still did not have enough information from Studio E to enable him to do that. He accepted however that a reasonably competent fire engineer should have informed his client that the outstanding work on the Outline Fire Safety Strategy needed to be completed now that further information had become available about the design of the external wall and the choice of materials. | Fire Safety Strategy | Fire Safety | Terence Ashton
The correspondence illustrates the confusion within the design team between cavity barriers and fire stops. It also demonstrates the failure of Mr Ashton and Exova to provide clear, coherent advice on the minimum relevant performance requirements for the external wall as a whole, including the identification of cavity barriers and the locations at which they should be fitted. | Cavity Barrier | Fire Safety | Terence Ashton
On 19 Oct 2015, Claire Williams and Terence Ashton exchanged a series of emails relating to the changes that had been made to the layout of the lower floors of the tower and on 21 Dec 2015 Andrew Bridges of R J Electrics also sent an email to Mr Ashton and Dr Pearson referring to major changes to the lower four floors. | Fire Safety Strategy | Fire Safety | Terence Ashton
Those messages should have prompted Mr Ashton to review the Outline Fire Safety Strategy, but unfortunately it did not occur to him to do so. | Fire Safety Strategy | Fire Safety | Terence Ashton
We find it surprising that neither the TMO, nor Studio E nor Rydon ever pressed Exova to revise its drafts or produce a final version of either the Existing Fire Safety Strategy or the Outline Fire Safety Strategy. As a result of that, and as a result of Mr Ashton’s failure to ensure that he obtained the information required to enable him to complete the task, Exova never did complete either of the two pieces of work on Grenfell Tower for which it had been retained. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton said that David Hughes of Rydon had never asked for the fire strategy to be brought up to date. | Fire Safety Strategy | Fire Safety | Terence Ashton
It did not occur to Mr Ashton that a completed fire safety strategy for the building was needed for the purposes of the health and safety file required by the CDM Regulations. | CDM | Health and Safety File | Terence Ashton
Exova’s work on the fire safety strategies made it a “designer” under the CDM Regulations. It therefore had a duty to avoid foreseeable risks to the health and safety of any person liable to be affected by the refurbishment work. Mr Ashton should have appreciated that. | CDM | Designer | Terence Ashton
Crap condition worse by Cate Cooney. | CDM | Designer | Cate Cooney
Mr Ashton’s response to Dr Pearson’s identification of a “rather fundamental” non-compliance with statutory guidance, in which he expressed the hope that building control would not identify the problem. The latter comment revealed an approach to fire safety that we consider irresponsible. | Fire Safety Strategy | Fire Safety | Terence Ashton
Exova final version of the much-needed Outline Fire Safety Strategy was never produced and that it failed either to draw that fact to the attention of the design team or to warn it about the potential consequences, despite having numerous opportunities to do so. | Fire Safety Strategy | Fire Safety | Terence Ashton
Exova peer review was poor. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton failed to comply with ISO 9001. | Fire Safety Strategy | Fire Safety | Terence Ashton
Mr Ashton himself had no formal training in fire engineering, no previous experience of overcladding high-rise buildings, and very little knowledge of cladding materials. | Fire Safety Strategy | Fire Safety | Terence Ashton
If Exova had asked a fire engineer with experience of overcladding high-rise residential buildings to manage the project, the critical importance to fire safety of the components of the external wall might have been recognised. Mr Ashton was effectively unsupervised in this work. The only Chartered Fire Engineer involved in the project at Exova was Dr Barker, whose contribution to the work was negligible. | Fire Safety Strategy | Fire Safety | Clare Barker
Exova failed with disability evacuation requirements. | Disability | Fire Safety | Terence Ashton
Exova’s failure to identify the significant fire safety risks introduced by the refurbishment was not only inadequate but positively dangerous. In order to complete its work it should have identified the nature of the proposed rainscreen, and as a result its combustible nature, and also the unsuitability of the combustible insulation and window infill panels, as well as the absence of cavity barriers in key locations. We have therefore come to the view that Exova bears considerable responsibility for the fact that Grenfell Tower was in a dangerous condition on completion of the refurbishment | Materials | Fire Safety | Exova
Chapter 55 The Choice of ACM PE Rainscreen Panels
Early part of 2012 Bruce Sounes began to think of aluminium as an alternative because it was light, presented a limited risk of corrosion and was available in a variety of colours. | Materials | Fire Safety | Bruce Sounes
Mr Sounes met Geof Blades of CEP Architectural Facades on 11 April 2012 to discuss potential cladding options, but they did not talk about the fire performance of any of the elements of the cladding. | Materials | Fire Safety | Bruce Sounes
Later that month Mr Sounes suggested Alucobond ACM panels as a possible option for the rainscreen, although he knew that at that stage RBKC’s Planning Department did not care for aluminium on aesthetic grounds. | Materials | Fire Safety | Bruce Sounes
In Jul 2012, Studio E sent Paul Dunkerton at the TMO a technical data sheet on a VM Zinc composite panel with a fire retardant core, although Bruce Sounes had not considered whether it complied with the Building Regulations or the guidance contained in Approved Document B. | Materials | Fire Safety | Bruce Sounes
On 7 Aug 2012 at a pre-application meeting with the Planning Department, Mr Sounes suggested zinc cladding, which was considered by the planning officer present to be acceptable. | Materials | Fire Safety | Bruce Sounes
On 16 Oct 2012, Mr Blades arranged an introductory meeting between himself, Mr Sounes and Deborah French of Arconic. Mr Sounes thought that they had discussed the fact that Grenfell Tower was a high-rise residential block, but the others did not remember that. | Materials | Fire Safety | Geof Blades
On 31 Oct 2012 Studio E issued its Stage C report, which included options for rainscreen materials, including zinc composite and aluminium. Although the Stage C Report addressed Approved Document L (Conservation of fuel and power) in detail, no detailed analysis of a similar kind was included in relation to Approved Document B. | Materials | Fire Safety | Bruce Sounes
On 7 Dec 2012 Mr Sounes suggested that aluminium might be a better choice than zinc on aesthetic grounds. | Materials | Fire Safety | Bruce Sounes
Jan 2013, Mohit Kotecha of Leadbitter emailed documents to Geof Blades for cost estimation purposes. They included an outline specification showing VMZ composite zinc panels as the rainscreen. Despite that specification, Mr Blades provided a quotation pricing only Reynobond Zinc Patina finish ACM and not the specified VMZ composite zinc panels. Although the price quoted included a full facade design service, Mr Blades did not consider whether the panels were suitable for use on a building over 18 metres in height. | Materials | Fire Safety | Geof Blades
CEP was promoting Reynobond because it had a commercial interest in doing so. | Materials | Commission | Geof Blades
On 1 Feb 2013, Leadbitter costed the saving to be made by using aluminium panels at £300,000. | Materials | Commission | Leadbitter
Studio E had long held a preference for a Proteus Honeycomb zinc product, but it was under significant pressure from the TMO to specify a cheaper alternative to zinc. | Materials | Cost | KCTMO
CEP reinforced the impression held by Studio E that Reynobond PE was a suitable material for use on Grenfell Tower, although he had only limited knowledge of the regulatory regime governing the use of such products and, at that stage, only a limited understanding of the way in which Reynobond PE reacted to fire. | Materials | Fire Safety | Bruce Sounes
In our view CEP should have taken steps to ensure that a person in the position of Mr Blades understood the behaviour, particularly in response to fire, of the products it supplied and had a general understanding of the regulatory regime that applied to them. In fact, he believed, quite wrongly, that “Class 0” was synonymous with “limited combustibility”. | Materials | Fire Safety | Geof Blades
Following the meeting, Mr Sounes felt that it might be possible to switch from zinc to ACM. At the request of Mr Blades, Ms French sent samples of various Reynobond panels directly to Adrian Jess at Studio E between 22 Mar and 8 Apr 2013. Further samples were sent between the beginning of Mar and the end of Jun 2014. | Materials | Fire Safety | Deborah French
Studio E did not make any enquiries about Harley, nor did it investigate the construction of the external walls of the buildings involved in any of those projects. | Materials | Fire Safety | Studio E
On 17 Apr 2013, Studio E gave the TMO details of a number of alternative materials to zinc that could be used as a rainscreen, most of which were ACM. | Materials | Fire Safety | Studio E
By June 2013 Mr Blades had become aware that an ACM panel with a fire resistant (“FR”) core was available and realised that it would perform better in a fire. However, he consistently promoted Reynobond 55 PE and accepted in evidence that he had relied on its Class 0 classification in the BBA certificate without having a working knowledge of the Building Regulations. | Materials | Fire Safety | Geof Blades
In Jun 2013, Studio E was given a copy of Artelia’s Draft Revised Project Brief, which stated that the primary driver of the project was value for money. However, despite the fact that ACM was likely to be a cheaper option, Studio E still preferred zinc. | Materials | Fire Safety | Artelia
In Jul 2013, following a meeting with Councillor Rock Feilding-Mellen, Bruce Sounes prepared a document describing a range of materials and fixing methods that could be used to provide a rainscreen for insulated cladding. Both zinc and ACM panels were illustrated, but the document did not mention fire safety. Studio E submitted a revised planning application to RBKC in Jul 2013 in which the proposed zinc composite rainscreen remained unchanged. | Materials | Fire Safety | Bruce Sounes
On 20 Aug 2013, Studio E completed a revised Stage D report which included Rheinzink panels for the rainscreen with ACM panels as an alternative. The Rheinzink panel was not combustible. | Materials | Fire Safety | Bruce Sounes
On 27 Sept 2013, Sounes and Rek met Ray Bailey and Mark Harris of Harley about options, costs and technical details for Grenfell. | Materials | Fire Safety | Bruce Sounes
Mark Harris said that Harley had indicated to Studio E that Harley’s clients were frequently forced to use ACM because it was the cheapest product available and that Harley had used ACM on tower blocks more than any other product. Ray Bailey claimed not to have expressed a preference for ACM and Tomas Rek did not recall any particular preference being expressed by Harley. | Materials | Fire Safety | Ray Bailey
Studio E and Harley discussions not discussed fire safety at all. | Materials | Fire Safety | Studio E
Mr Sounes still preferred zinc or a zinc composite material. He told Harley that Studio E was looking seriously at Nedzink (a zinc composite panel) but, when he reported back to the TMO with Harley’s rough estimate of £3 million based on zinc rainscreen cassettes, he pointed out that in Harley’s experience budgets often forced clients to adopt face-fixed ACM. Peter Maddison responded asking whether Harley had given a similar cost estimate for aluminium rainscreen. | Materials | Fire Safety | Bruce Sounes
On 7 Nov 2013, Mr Sounes forwarded his email exchange with Harley about the cost of different cladding options to Chweechen Lim of Artelia. At that stage Artelia was preparing the OJEU tender documentation and on 11 Nov 2013, Ms Lim told Mr Sounes that she would include ACM in the tender contract sum analysis and ask contractors to provide an optional cost for zinc panels to ensure that tenderers provided costs for both types. | Materials | Fire Safety | Chweechen Lim
Ms Lim noted that Harley’s quoted costs were higher than Artelia’s cost plan and were also higher than the TMO’s budget. | Materials | Fire Safety | Bruce Sounes
Mark Harris responded to Bruce Sounes some two weeks later on 21 Nov 2013. He failed to answer Mr Sounes’ question about the rate for Nedzink, but he gave standard rates for ACM cassette and face-fixed panels. The email makes clear the close business relationship between Harley and Arconic, which led Harley to press for Reynobond panels to be used. By Dec 2013 Harley was seeking prices for Arconic’s Reynobond ACM panels and by the spring of 2014 it had become committed to their use on the project. | Materials | Commission | Harley
Planning permission for the refurbishment was granted on 10 Jan 2014, subject to conditions, including a requirement that the materials to be used on the external face of the building be approved in writing by RBKC. On 15 Jan 2014 Arconic provided a quotation to CEP for Reynobond 55. Although silent about the composition of the core, Deborah French accepted that as a standard product it would have been polyethylene. | Materials | Fire Safety | Arconic
Mr Blades confirmed that Harley had asked him to quote only for Reynobond. Following the receipt of the quotation, Harley sent its own quotation to Rydon on 29 Jan 2014, which did not include VM Zinc as an option. | Materials | Fire Safety | Harley
The TMO agreed to the inclusion of ACM options in the NBS Specification for two reasons: first, because it wanted priced options, as RBKC’s Planning Department had not yet granted consent for any specific type of rainscreen; second, because it had in mind that it might consider options that were less expensive than zinc in order to reduce the cost. Peter Maddison denied that the inclusion of ACM had been driven by the TMO; he said that the TMO had included the ACM options on the advice of its professional design team and in the understanding that it was compliant with all the regulations. We accept his evidence about that. | Materials | Fire Safety | Peter Maddison
Studio E had drafted the NBS spec, not checked materials complied with Building Regulations or Approved Document B guidance. Assumed compliance based on other projects aswell appearance. Studio E didn’t ask Exova, or any other fire engineer, to review the NBS nor did Studio E think if ACM was appropriate. | Materials | Fire Safety | Studio E
We are satisfied that Studio E did not consult Exova on the use of ACM rainscreen panels. Until the night of the fire Mr Sounes was unaware that ACM panels could be produced with different cores, some fire retardant and some not. Indeed, he was unaware that any of the materials referred to in Harley’s quotation might be available in fire-rated versions and simply did not think about the fire performance of the ACM panels. None of those involved in the refurbishment at Studio E or Harley scrutinised the BBA certificate relating to Reynobond 55 PE properly. | Materials | Fire Safety | Bruce Sounes
Studio E, Harley and Rydon, everyone involved concentrated on the appearance of the rainscreen panels to the complete exclusion of their fire performance. | Materials | Fire Safety | Bruce Sounes
Between 2006 and 2011, Rydon had carried out two other cladding projects with Harley as contractor. | Experience | Fire Safety | Rydon
Although in each case the core of the panels was unmodified polyethylene, there was one difference: the panels used were face-fixed (i.e. riveted to the supporting rails), whereas the Reynobond panels installed at Grenfell Tower were cassette-fixed. | Materials | Fire Safety | Rydon
Rydon and Harley remained in close contact throughout the procurement process relating to the Grenfell Tower project and it is clear that they approached it as a team, so much so that Rydon’s tender included notes on the background and experience of three of Harley’s employees, Daniel Anketell-Jones, Mark Stapley and Robert Maxwell. | Materials | Fire Safety | Rydon
CEP had worked with Harley on ten previous projects, including the Chalcots Estate and Ferrier Point projects, but the Grenfell Tower refurbishment was the only project it had undertaken with Harley using ACM panels in cassette form. | Experience | Fire Safety | CEP
At the time of the formal procurement process Rydon also had an existing relationship with the TMO and there had been at least some discussion within Rydon of the project and its connection with Peter Maddison before 5 April 2013. | Procurement | Relationship Previously | Rydon
Stephen Blake, Rydon’s Refurbishment Director, had known Peter Maddison and Sacha Jevans of the TMO since about 2000, having met them at various conferences. Although he had not seen either of them regularly, they had kept up a direct line of contact, as Simon Cash of Artelia recorded in an email in Oct 2015 and as was broadly confirmed by both Mr Maddison and Ms Jevans. | Procurement | Relationship Previously | Steve Blake
The housing conference to which Mr Blake referred took place between 4 and 6 March 2014 in Brighton. According to Mr Blake, the “senior representatives” of the TMO were either Mr Maddison or Ms Jevans, but both of them denied having spoken to Rydon about the tender. | Procurement | Relationship Previously | Steve Blake
The tender interviews for the project were due to take place on 7 Mar 2014 and in our view the email speaks for itself. However it came about, it is clear to us that Rydon was given an indication of the likely outcome of the tender process while it was still going on. No other contractor was afforded the same benefit. | Procurement | Relationship Previously | Steve Blake
When he gave evidence Mr Maddison accepted that he had telephoned Mr Henton on 10 Mar 2014, after the TMO had interviewed all the potential contractors, to tell him that Rydon was in first position. The next day Mr Henton sent an email to Alan Sharrocks and Simon Lawrence telling them that, subject to a small amount of value engineering, he expected Mr Maddison to recommend to the TMO board the following week that Rydon be appointed as principal contractor for the refurbishment. | Procurement | Relationship Previously | Peter Maddison
Mr Blake had not been included in Mr Henton’s email and he was unable to say why that was, or how the conversation between Mr Henton and Mr Maddison had come about. He was asked whether at that time (11 Mar 2014) he had understood that Rydon’s appointment would be conditional on its willingness to accommodate the TMO’s desire for value engineering and initially told us that he had not known that at the time. However, he had in fact been sent a draft of the email on 10 Mar 2014 by Sandra Guest, Mr Henton’s assistant, who had asked him to give her the names of the Rydon employees who had been involved in the bid. | Procurement | Relationship Previously | Rydon
Despite his prevarication, it is clear that Mr Blake had been in direct contact with Mr Maddison on or before 10 Mar 2014 about the results of the tender, because at 7.10pm on 10 Mar 2014 he had written to Mr Henton to tell him as much. | Procurement | Relationship Previously | Peter Maddison
Having been shown the contemporaneous documents, Mr Blake ultimately accepted that he had been aware by 10 Mar 2014 at the latest that the TMO required significant reductions in the cost of the project by way of “value engineering” if it was to go ahead. | Procurement | Relationship Previously | Steve Blake
On 12 Mar 2014 Mr Blake sent an email to various Rydon employees telling them that Rydon would be asked by the TMO to find some savings in addition to those identified in the tender. Mr Maddison said that he had spoken to Mr Blake to establish that Rydon was prepared to work with TMO to value engineer the project once the contract had been awarded. | Procurement | Relationship Previously | Steve Blake
When asked about that exchange Mr Blake originally denied having spoken to Mr Maddison on 12 Mar 2014, but having been shown the contemporaneous documents he was forced to accept that his previous evidence had been untrue, though he said he had had no recollection of the emails. | Procurement | Relationship Previously | Steve Blake
Mr Blake also accepted that he and Mr Henton had had personal and private access to the top decision-makers on the project at the TMO. | Procurement | Relationship Previously | Steve Blake
Mr Blake insisted that their relationship with Mr Maddison and Ms Jevans had not influenced the tender process. Peter Maddison did not score the tenders; that was done by Artelia, Jenny Jackson and the TMO, each of whom provided their own independent scoring, and Rydon came top. However, we are satisfied that Mr Maddison and Ms Jevans played an important part in ensuring Rydon’s appointment, both in providing information to Rydon about the tender and in negotiating with it so that its appointment would proceed. | Procurement | Relationship Previously | Peter Maddison
Rydon costing error of £212,000. On 11 March 2014, Katie Bachellier, one of Rydon’s estimators, had written to Mr Blake to tell him of the error. Mr Blake’s response was to look for a way to claw back the loss that would otherwise be made. That had significant repercussions. | Procurement | Costs Error | Steve Blake
13th Mar 2014, Maddison sent email to David Gibson, copies also to Claire Williams and Jenny Jackson, confident that Mr Blake would reduce gap in budget by £270,000. | Procurement | Costs Error | Peter Maddison
Later on on 13th Mar 2014, Gibson sent email to Mr Blake to achieve saving of around £800,000, spreadsheet of cladding saving as £243,000 (aluminium new). | Procurement | Costs | David Gibson
£800,000 and £200,000 costing error meant £1m for Rydon to save even before formal contract award. | Procurement | Costs Error | Rydon
Mr Blake understood that Rydon would be awarded contract if could get the savings Gibson requested, Blake could see no reason that this could not be achieved. | Procurement | Costs | Steve Blake
Upon Gibson's email, Blake contacted Harley. Mark Harris advised by Mr Blake that Rydon had been informed "off the record" that in pole position. | Procurement | Tip Off | Steve Blake
Mark Harris sent Rydon, Harley's analysis of savings. "Compliant bid" £3,736,595 together with two alternative window systems and four alternative claddings systems. | Materials | Costs | Mark Harris
Zinc (cassette-fixed) = £157,385. Zinc (riveted) = £279,764. Cassette Fixed ACM = £419,627. Riveted ACM = £576,973. | Materials | Costs | Mark Harris
Stephen Blake and Simon Lawrence both said that by that time it had been accepted by Harley and Rydon that ACM panels would be used if planning permission could be obtained. | Materials | Fire Safety | Steve Blake
A meeting took place during the evening of Tuesday 18 Mar 2014, attended by Mr Lawrence, Mr Blake and Ms Bachellier on behalf of Rydon and Mr Gibson, Mr Maddison and Claire Williams on behalf of the TMO, at which they discussed how the project could be brought within the TMO’s revised budget. Mr Blake said that he could not recall the meeting in any detail, but he did remember that Rydon and the TMO had discussed the need to find a significant amount of savings to enable the scheme to meet the TMO’s budget. | Materials | Costs | Steve Blake
Procurement issues and value engineering after Rydon awarded contract. "Secret Offline Meeting." Simon Cash of Artelia uncomfortable with this approach. | Procurement | Offline Meeting | Simon Cash
After offline meeting, solicitior said procurement could be challenged. Maddison sent email to Jevans, Williams and Gibson that this was low challenge and low risk of success. | Procurement | Value Engineering | Peter Maddison
We do not accept Peter Maddison’s characterisation of the discussions. Their clear purpose, which was understood by both the TMO and Rydon, was to achieve a reduction in the cost of the project that would be reflected in the contract price. Specific areas of savings were identified and figures were discussed. | Procurement | Value Engineering | Peter Maddison
We do not accept that Peter Maddison thought at the time that the “offline” discussions were consistent with the rules governing the procurement process; indeed, in answer to a question from the Chairman he accepted that they “did not strictly comply with the letter of the process.” That, of course, explains why the meeting was described as “offline”, i.e. secret. Secrecy was essential so far as both the TMO and Rydon were concerned because transparency might defeat its object. | Procurement | Offline Meeting | Peter Maddison
On 17 Mar 2014, Philip Booth of Artelia had drafted a letter to Rydon formally notifying it of its status as the preferred bidder. Substantial amendments were made to the wording by Ms Jackson later that evening. The amended version, dated 18 Mar 2014, was sent to Rydon at 5.55pm, some time after the “offline” meeting had ended. Although Artelia had been aware of the process that the TMO proposed to adopt, there is no evidence that Artelia had been aware of the meeting itself and it is likely that it sent the letter on the instructions of Mr Gibson or Mr Maddison. | Procurement | Contract | Artelia
The letter referred to certain conditions, but said nothing about value engineering or the need to find substantial (or indeed any) cost savings. Unsurprisingly, the letters sent to the unsuccessful bidders the same day did not refer to the contact between the TMO and Rydon. | Procurement | Offline Meeting | Artelia
Simon Lawrence reported to Mark Harris on 19 Mar 2014 that Rydon had been confirmed as the preferred contractor for the refurbishment, although the decision was yet to be formally approved. Mr Harris recorded in his log that Rydon was “keen to push this job down the face-fixed ACM route with standard colour finish”. | Materials | Fire Safety | Simon Lawrence
He immediately contacted Deborah French of Arconic to procure samples of ACM rainscreen that would appear similar to zinc but at a lower cost. In the weeks and months that followed, there were extensive discussions between Harley, Arconic, Studio E, Rydon and CEP about the use of ACM rainscreen cladding, but they related only to its cost and appearance certainly, there were no discussions about its reaction to fire. Peter Maddison’s diary entry for 19 Mar 2014 suggests that he had been advised by the TMO’s solicitors to agree with Rydon that the negotiations and the contract price should both be kept confidential. | Procurement | Fire Safety | Peter Maddison
20 Mar 2014, Katie Bachellier sent Peter Maddison and others at the TMO a summary of Rydon’s value engineering proposals in the form of two documents entitled “VE Options 18.03.14” and “Cladding VE Options 18.03.14. | Procurement | Value Engineering | Peter Maddison
VE Options saving of £862,041. | Procurement | Value Engineering | Peter Maddison
Cladding VE savings as: Zinc (Cassette-Fixed) = £100,406, Zinc (Riveted) = £202,372, Cassette-Fixed ACM = £293,368, Riveted ACM £376,175. | Procurement | Profit | Peter Maddison
Figures lower than what Harley had given Rydon on 14th Mar 2014. | Procurement | Value Engineering | Harley
Mr Blake conceded that Rydon had seen the change of Rainscreen as an opportunity to generate additional profit for itself. | Procurement | Profit | Steve Blake
Arconic held a certificate issued by the BBA in respect of Reynobond Architecture Wall Cladding Panels, the most recent version of which, at the time of the refurbishment, was dated 14 Jan 2008. Astonishingly, at no stage of the project did anyone at Rydon, Harley or Studio E examine the certificate with any care with a view to understanding how ACM panels with unmodified polyethylene cores might react to fire. | Materials | Fire Safety | All
Deborah French gave Mr Harris a copy of the BBA certificate on 23 Apr 2014 and he passed it straight on to Simon Lawrence, apparently without giving it any consideration. Simon Lawrence sent a copy to Mr Sounes the same day and also arranged for a copy to be provided to Mr Blake on or around 6 May 2014 as part of a pack of documents relating to a meeting with RBKC’s Planning Department. | Certificates | Fire Safety | Mark Harris
Mr Sounes did not spend long looking at the certificate; indeed he said that it had not been his practice to read the whole of a BBA certificate for any product that he was planning to recommend for a project. He admitted that he had never read section 6 of the Reynobond certificate, which related to the fire performance of the panels, and said that investigating their fire performance had not been a concern at that stage. | Certificates | Fire Safety | Bruce Sounes
Mr Sounes was not aware of the distinction between the fire retardant (FR) and unmodified polyethene (PE) versions of the product and he never discussed the matter with Harley or CEP. For his part, Neil Crawford could not remember having looked at the BBA certificate before the fire and we think it unlikely that he did so. No one at Studio E sought any guidance on the meaning or effect of the BBA certificate from Exova, Rydon, Harley, Arconic or anyone else. | Certificates | Fire Safety | Bruce Sounes
Although Simon Lawrence may have looked at the BBA certificate generally, he did not study it in any detail and did not pay any attention at all to the section relating to fire performance. He did not ask Harley to check the test evidence on which the certificate was based, nor did he ask it whether the panels being proposed for use on the tower were in all respects the same as those described in it. Rather, he appears simply to have assumed that ACM panels generally were suitable for use on the tower because Rydon and Harley had previously worked together to install similar panels on the Chalcots Estate and Ferrier Point projects. | Certificates | Fire Safety | Simon Lawrence
Mr Blake said that there had been no discussions at all within Rydon about which, if any, of the routes to compliance for external walls in Approved Document B had been adopted. no one at Rydon gave any meaningful consideration at any stage to the part of the certificate that dealt with the fire performance of the ACM panels used on Grenfell Tower. | Certificates | Fire Safety | Steve Blake
As for Harley, Ray Bailey had read the BBA certificate in 2008 at the time of the Chalcots Estate project and did not read it in detail again. He accepted that Harley was obliged to examine certificates such as the BBA certificate in order to satisfy itself that the products that were being used on the tower were appropriate, but he said he had only been concerned to ensure that the BBA certificate confirmed that the panels had a Class 0 rating. He was not aware that that classification did not extend to the smoke silver polyethylene cored panels that had been selected for use | Certificates | Fire Safety | Ray Bailey
Ms French, who sold the cladding for Arconic, said that this fundamental lack of curiosity in the reaction of the panels to fire was more normal than otherwise. | Certificates | Fire Safety | Deborah French
The approach of RBKC’s Building Control Department was much the same. Mr Allen accepted scrutinising certificates such as the BBA certificate and the test data referred to within them was a core function of a Building Control officer, but Mr Hoban did not look beyond the first page of the BBA certificate with its reference to Class 0. The reliability of a BBA certificate was accepted without question by RBKC’s Building Control Department, but it was not Mr Hoban’s practice to read BBA certificates in any detail. | Certificates | Fire Safety | John Hoban
Geof Blades was aware of the existence of the BBA certificate and thought (wrongly) that it stated that Reynobond 55 PE panels had achieved a Class 0 fire rating, having failed to notice that only the FR version was said to have passed both the BS476-6 and BS476-7 tests. He did not appreciate that the certificate did not in that respect cover panels with an unmodified polyethylene core. He also thought, quite wrongly, that Class 0 was synonymous with limited combustibility and failed to consider whether the nature of the core might affect its compliance with the Building Regulations. He had no understanding of the ways in which cladding systems could be shown to comply with the Building Regulations and Approved Document. | Certificates | Fire Safety | Geof Blades
From Mar 2014 onwards, the attention of Studio E, Rydon, Harley and the TMO turned to obtaining approval from the RBKC Planning Department for the material to be used on the external walls of the tower. From that time, the only product that was proposed for use was Reynobond 55 PE ACM panels, i.e. with unmodified polyethylene cores. The only remaining questions were about colour and whether the fixing system should be cassette or rivet. | Materials | Planning Permission | All
On 1 Apr 2014, a meeting was held to introduce the TMO to Rydon, as the main contractor for the project. The minutes of that meeting record that the TMO was told that there was a potential saving of up to £376,175 to be made if the material used for the rainscreen were changed from zinc to ACM and if rivet fixings were used. Rydon did not tell the TMO that Harley was willing to reduce the cost of the rainscreen by as much as £576,000 for face-fixed ACM and if, as the minutes tend to suggest, the TMO was given to understand that the sum of £376,175 reflected the full amount of the reduction available from Harley, that was clearly false and was known by Rydon to be false. | Procurement | Profit | Rydon
Simon Lawrence listed what he described as “agenda points” for the meeting, including, in particular, a proposal for changing the rainscreen from zinc to ACM. He intended to argue that ACM was not inferior to zinc. Mr Lawrence saw Rydon as an advocate for ACM against a reluctant planning committee because it had used ACM successfully on previous occasions. He thought it was in everyone’s interests for ACM to be accepted, because there was a risk that, if it were not, the project might not go ahead at all. As we have already noted, Rydon also had a powerful financial interest in the choice of ACM. | Materials | Profit | Simon Lawrence
When Mr Lawrence briefed Mr Blake before the meeting, he told him that the ACM panels they proposed to use had a Class 0 rating, but there was no discussion about their fire performance at the meeting. Indeed, he could not remember any discussion about the fire safety of the panels at all. Mr Blake said that he had not been aware of any consideration having been given to the fire performance of ACM panels at any time between May and October 2014, when final planning permission was obtained. | Materials | Fire Safety | Steve Blake
RBKC’s Planning Department was principally concerned with two matters: the colour of the panels and the method of fixing. There is no evidence that the TMO, Rydon or Harley was aware that the method of fixing might affect the reaction of the panels to fire, but it did affect the appearance of the facade and was therefore regarded as an important aesthetic consideration. Bruce Sounes said that his own examination of the technical documents provided by Arconic concentrated on the colour charts because the focus at that time had been on the building’s appearance. When one of the councillors, Rock Feilding-Mellen, intervened in the debate in July 2014, the only issues on which he commented were fixing method and colour, with a heavy emphasis on the latter. | Materials | Planning Permission | Bruce Sounes
The Planning Department had a clear preference for a cassette rather than a riveted system. On 23 May 2014, Simon Lawrence sent an email to Stephen Blake and Zak Maynard, in which he expressed his concern that the planners would accept only cassette-fixed panels on aesthetic grounds. His concern stemmed from the fact that Rydon stood to gain far less from the use of a cassette system than a riveted system. | Materials | Profit | Simon Lawrence
On 17 July 2014, representatives of the planning committee visited Grenfell Tower to view a mock-up of the cladding. Arconic supplied Reynobond ACM rainscreen for the purpose free of charge to CEP, which fabricated it. On 31 Jul 2014 the TMO informed Rydon that the planning department had approved ACM rainscreen cladding using cassette fixings and formal planning permission was granted for those panels in “smoke silver” on 25 Sep 2014. | Materials | Planning Permission | CEP
Once Reynobond 55 PE ACM panels had been approved, attention turned to their fabrication by CEP. Harley placed four orders with CEP for ACM panels to be used on the facade and crown of the tower, on 13 Mar 2015, 6 Jul 2015, 8 Jul 2015 and 9 Nov 2015. Harley placed separate orders for the fabrication of the windows, in Oct 2014 and Feb and May 2015. | Materials | Fire Safety | CEP
Prior awareness of combustibility. The most significant event, in our view, was the fire which occurred on the night of 16 Jan 2012 at Taplow House on the Chalcots Estate. Employees of Rydon and Harley, including Stephen Blake, attended Taplow House on 17 Jan 2012 to inspect the damage, including the damage to the ACM panels. A report produced by Harley on 17 Jan 2012 found that the fire had melted the windows of the flat in which it had started and had damaged the cladding, but had been prevented from spreading more widely into the cladding system (and in turn to other flats) by the cavity barriers around the windows. Mr Blake was pictured in the report pointing to the cavity barrier system around the damaged window. | Prior Awareness | Fire Safety | Steve Blake
The inspection revealed that the ACM panels had distorted as a result of being exposed to heat and smoke, and the report contained photographs showing that they had been seriously damaged, having melted and warped. The abseil report was circulated to, amongst others, Mr Blake, Ray Bailey and Daniel Anketell-Jones. Despite the contents of the report, Mr Blake appears to have told David Hughes (of Rydon) that he had no concerns about the safety of ACM panels arising from the Taplow House fire. Ray Bailey told us that the fire at Taplow House had demonstrated to Harley that ACM would burn and he accepted that Harley’s failure to implement the lessons it had learnt from Taplow House in the designs of the windows at Grenfell Tower had been an error. | Prior Awareness | Fire Safety | Ray Bailey
On 13 May 2013, Deborah French of Arconic wrote to Geof Blades, Neil Wilson and Roy Fewster of CEP to alert them to press reports of a fire in a building in the UAE that had been overclad with ACM rainscreen panels. Mr Blades knew as a result of those exchanges that ACM panels with unmodified polyethylene cores were combustible. | Prior Awareness | Fire Safety | Geof Blades
Ms French’s email followed a message to CEP a few days earlier from Richard Geater, the UK sales representative of Alucobond’s, another producer of ACM panels, which referred to the Tamweel Tower fire in Dubai and described the problems that had been encountered there with the use of cheap ACM panels with polyethylene cores. Those messages ought to have prompted Mr Blades to reconsider whether it was safe to use Reynobond PE on any high-rise building in the UK, including Grenfell Tower, but regrettably he did not do so. | Prior Awareness | Fire Safety | Geof Blades
On 7 Oct 2014, Daniel Anketell-Jones attended the Annual General Meeting and Members’ Meeting of the Centre for Window and Cladding Technology (CWCT), at which a presentation was given by Sarah Colwell discussing the regulatory requirements and testing regimes for the construction of facades. It is clear from the slides used at that presentation that the combustibility of rainscreen facades was discussed, including the large number of cladding fires that had affected high-rise buildings in other countries. Daniel Anketell-Jones said that he had no specific recollection of being at that presentation; he thought he had been there but that he had not been concentrating. | Prior Awareness | Fire Safety | Daniel Anketell-Jones
It is unlikely to be a coincidence that on 8 Oct 2014, the day after that meeting, Samuel Anketell-Jones, a junior design engineer at Harley and Daniel Anketell-Jones’s brother, sent Deborah French of Arconic an email asking for information about Reynobond ACM panels with a fire-resistant mineral core. Daniel Anketell-Jones told us that when he had proposed the cladding for Grenfell Tower he had not realised that Reynobond ACM panels were available with a fire-resistant core. (Ray Bailey said that he had been aware that two kinds of panel were available as a result of reading the BBA certificate but had assumed that they performed in similar ways and that neither he nor anyone else at Harley had ever asked Deborah French about it.) Although it is not clear to which of Harley’s projects the email related, it suggests quite strongly, particularly when viewed together with the information shared at the CWCT meeting, that Harley knew more than it was willing to admit about the availability of a fire-resistant version of the Reynobond panel and the dangers of using ACM with an unmodified PE core. | Prior Awareness | Fire Safety | Ray Bailey
In an email of 27 Mar 2015, Daniel Anketell-Jones wrote to Ray Bailey saying, “There is no point in ‘fire stopping’, as we all know; the ACM will be gone rather quickly in a fire!” On 31 March 2015, Terence Ashton wrote to Neil Crawford saying, amongst other things, that it was difficult to see how a fire-stop would stay in place in a fire involving external flaming as it would cause the zinc cladding to fail. Mr Crawford agreed, expressing the view that “metal cladding always burns and falls off.” Later the same day, he relayed Mr Ashton’s opinion to Simon Lawrence. It is clear that Mr Lawrence read Mr Ashton’s comments because he responded, “Excellent. That looks positive. | Prior Awareness | Fire Safety | Daniel Anketell-Jones
Mr Ashton said that he had meant to say that metal rainscreen would not burn, but that if windows connected to metal cladding failed, the panels themselves would fall off the building in that area, not that they would actually burn. We do not accept that evidence. In our view he was aware that ACM panels would burn, but at the time he was still under the impression that the panels were to be zinc. | Prior Awareness | Fire Safety | Terence Ashton
We agree with the view expressed by Deborah French in a witness statement given to the Metropolitan Police that it would have been obvious to anyone that polyethylene was plastic and flammable. We are satisfied that Mr Crawford and Mr Anketell-Jones knew that ACM was combustible; Mr Lawrence may not have known, but ought to have taken the trouble to find out after he had been asked about the reaction of the panels to fire by Claire Williams in her email of 12 Nov 2014. | Prior Awareness | Fire Safety | Deborah French
On 12 Nov 2014, Claire Williams wrote to Philip Booth and Nick Valente of Artelia asking, amongst other things, whether in the light of the fire at Lakanal House there was any requirement for materials to be flame retardant. Later the same day she sent an email to Simon Lawrence referring to Lakanal House and asking him to clarify the fire retardance of the new cladding. | Prior Awareness | Fire Safety | Claire Williams
We think that Simon Lawrence simply failed to take any action at all in response to the email, possibly because he did not understand its significance, that Ms Williams did not pursue it, and that no one in the design team gave any consideration to the question she had raised, despite the fact that it was of real importance. | Prior Awareness | Fire Safety | Simon Lawrence
We are unable to regard the evidence of Mr Gibson and Ms Williams on this matter as reliable. We find the evidence of Mr Booth persuasive: as employer’s agent, he was required to ensure that meetings were properly and fully recorded for the benefit of the TMO. If such an important assurance had been given at the meeting, he would have noted it. We consider it very unlikely that a paper document was produced and distributed at a meeting if no paper or electronic copy of it could be found, either on Artelia’s systems or among the records or documents of any other party. Contrary to the assertions of Ms Williams that there is a gap in the minutes for Feb 2015, there is none. Gibson supported by Williams asserted that Mr Lawrence had assured him that the rainscreen was completely inert and would not burn at all as per this there is no record. | Prior Awareness | Fire Safety | Artelia
The matter does not end there, however. Ms Williams made no reference at all to any such assurance in her first statement; it was not until she made her second statement, produced after she had seen Mr Gibson’s statement, that she first mentioned it. Ms Williams said that she simply had not remembered the conversation with Mr Lawrence when she made her first statement, but it is difficult to understand how such an important matter could have escaped her mind. Moreover, she said that she had not recalled Mr Lawrence’s assurance when she became aware of the fire on 14 Jun 2017. Again, that is difficult to understand. If she had been told that ACM panels were inert and would not burn, that assurance would surely have come to mind as soon as she became aware of the disaster. | Prior Awareness | Fire Safety | Claire Williams
Finally, it is worth bearing in mind that Ms Williams sought an assurance of a similar kind in two emails sent on 12 Nov 2014. In the first, she told Mr Booth that she wanted to ensure that the flame retardance of the ACM panels was raised. In the second, her “Lakanal moment” email to Mr Lawrence, she said that she was writing to get clarification on the fire retardance of the new cladding. If Mr Lawrence had already given her a clear assurance before 12 Nov 2014, we think it unlikely that either of those messages would have been sent, or, if sent for other reasons, that she would not have referred to it. If the assurance was given after 12 Nov 2014 (as Ms Williams and Mr Gibson suggested), we think that she would have recalled telling Simon Lawrence that she had asked for the same information some months before but had not received a response. In the light of all the evidence we do not accept that Mr Lawrence gave Mr Gibson and Ms Williams any assurance of the kind they described. | Prior Awareness | Fire Safety | Claire Williams
Chapter 56 The Choice of Insulation
Two insulating products were ultimately used in the construction of the external wall of Grenfell Tower, Celotex RS5000 (“RS5000”) and Kingspan Kooltherm K15 (“K15”). RS5000 was a polyisocyanurate (“PIR”) rigid foam board insulation. K15 was a phenolic (“PUR”) rigid foam board insulation. Both were combustible, with a short time to ignition. Neither RS5000 nor K15 met the limited combustibility guidance in paragraph 12.7 and table A7 of Approved Document B; and neither of them had been tested in accordance with BS 8414 in combination with the other materials intended for use on the tower. | Materials | Fire Safety | Suppliers
It follows that the system had not been shown to meet the criteria set out in BR 135. No alternative way of establishing compliance with the Building Regulations, e.g. by way of a desktop report or a holistic fire-engineered solution, had been followed. The use of those products was therefore contrary to official and industry guidance and, as the Chairman found in his Phase 1 report, the external wall of the building as a whole, including the insulation, was combustible and did not adequately resist the spread of fire over the walls. The use of those materials was therefore a clear breach of functional requirement B4(1) of the Building Regulations. | Materials | Fire Safety | Suppliers
Celotex FR5000 was the insulation product specified in the contract between the TMO and Rydon. It was specified by Studio E in the NBS Specification in Nov 2013, which formed part of the Employer’s Requirements. However, the origins of that decision can be traced back to early in the previous year. | Materials | Fire Safety | Studio E
Max Fordham was instructed to assist the design team in establishing environmental design criteria, including U-values, ventilation openings and other matters, in order to advance the design of the cladding. On 18 Jun 2012, Matt Smith of Max Fordham sent an email to Bruce Sounes asking what U-value Studio E was seeking to achieve. Andrew McQuatt of Max Fordham understood that Mr Smith had written that email to prompt Studio E to suggest its own U-value, assuming that Studio E as architect was designing the whole system and that Max Fordham did not have the power to specify any of the elements of the cladding. The email was intended to stimulate a dialogue with Studio E about the overall design, including the U-value. In response, Mr Sounes instructed a colleague to send Max Fordham drawings of the likely build-up of the cladding system. | Materials | U Value | Max Fordham
Max Fordham suggestion of a U-value of 0.15 W/m2Kw was twice the efficiency to that of official guidance. | Materials | U Value | Max Fordham
Approved Document L whereby permissable to depart from U-value that was functionally and technically feasible. | Materials | U Value | Max Fordham
Neither Max Fordham or Studio E checked the proposed U-value against the fire safety guidance of Approved Document B to see whether a higher U-value would have to be accepted in order to comply with the guidance on insulation contained in paragraph 12.7. | Materials | Approved Document B | Studio E
Mr Sounes on 5th July 2012 asked Rockwool about mineral wool insulation. Neither Studio E or Max Fordham considered using Celotex or any polymeric material. | Materials | Fire Safety | Bruce Sounes
Mr Sounes found that would need 450mm of Duo Slab for U-value. He did not ask Max Fordham or anyone else to check his calculations and he did not check Approved Document L to see what U-value the guidance required. | Materials | Approved Document L | Bruce Sounes
It was Studio E’s responsibility, as lead consultant and lead designer, to assess the feasibility of that U-value in the context of its initial design of the cladding system. | Materials | Fire Safety | Bruce Sounes
A reasonably competent lead consultant and lead designer would not have considered itself limited in any way in its selection of materials or the design of the cladding system by suggestions made by the M & E consultant. | Materials | Fire Safety | Bruce Sounes
It was Studio E’s responsibility as architect and lead designer to decide what U-value was feasible and appropriate. | Materials | Fire Safety | Bruce Sounes
Matt Smith’s calculation did not include any thermal bridging considerations, because Max Fordham did not have any more specific details of the design of the cladding to enable him to do so. It was Andrew McQuatt’s own view that Mr Sounes’ analysis may have been based on rather pessimistic assumptions. | Materials | Fire Safety | Bruce Sounes
Mr McQuatt knew that the Kingspan rigid insulation board would be a thinner product and thought that it would be appropriate to wait to see what Kingspan said in response to Bruce Sounes’ email of 5 July 2012 before commenting further. | Materials | Fire Safety | Bruce Sounes
On 6 July 2012 Bruce Sounes sent an email to Matt Smith to tell him that Kingspan had recommended 200mm of its phenolic foam product to achieve the required U-value. He also attached to his email a product datasheet for a mineral wool insulation manufactured by Superglass Insulation Ltd called “Cladding Mat 37”, but that was rejected because it was thought that too great a thickness would be required. | Materials | U Value | Bruce Sounes
Mr Sounes did not ask Max Fordham to obtain from Rockwool a formal calculation of the thickness of material required, so apart from Matt Smith’s “quick calculation” no attempt was made at any stage to determine precisely what thickness of mineral wool would be required to achieve a U-value of 0.15 W/m2K. | Materials | U Value | Bruce Sounes
Andrew McQuatt understood the email from Mr Sounes to mean that he had decided that the maximum thickness for the insulation should be 200mm. He thought that Mr Sounes’ calculations formed part of a bigger picture; he did not question it because he assumed that Studio E had chosen it as the best thickness for a wide range of reasons. | Materials | U Value | Andrew McQuatt
On 16 August 2012 Andrew McQuatt sent Mr Sounes his calculations and attached the product datasheet for Celotex FR5000. In order to do his U-value calculation, Mr McQuatt had needed to use the lambda value of an insulation product. In his mind there was little difference between the rigid board insulation products marketed by Kingspan and those sold by Celotex, so he went to the Celotex website and looked at a datasheet for a solid insulation board, FR5000. He obtained the lambda value from the datasheet and sent it to Mr Sounes so that he could see the source of the information he had used. He thought that Celotex FR5000 was the only type of product that would provide the required thermal performance at a thickness that could realistically be accommodated. | Materials | U Value | Andrew McQuatt
Celotex FR5000 was a polyisocyanurate (PIR) product. The datasheet made no reference to its being suitable for use as part of a cladding system nor did it state that it was suitable for use on buildings with a storey above 18 metres in height. It did not say that FR5000 was a product of limited combustibility, but it did say that it had Class 0 fire performance throughout the entire product in accordance with BS 476. | Materials | Fire Safety | Andrew McQuatt
Andrew McQuatt did not give any thought to the fire performance of Celotex FR5000 before he sent his email to Bruce Sounes on 16 August 2012. Mr Sounes had suggested both the Rockwool product and the Kingspan product and Mr McQuatt thought that the use of Kingspan had already been established. Since Studio E had proposed a Kingspan product as an option from the outset, he had thought there was nothing wrong with using it or, by extension, Celotex FR5000. He accepted that he would have been just as likely to put forward the Kingspan product if he had obtained the lambda value of one of their foam boards instead of a Celotex product. | Materials | Fire Safety | Andrew McQuatt
At the time, Andrew McQuatt was not aware of the guidance given in Approved Document B about insulation materials and their combustibility, nor could he recall with any certainty having heard the expression Class 0. He was not aware of industry guidance on the construction of external walls and insulation materials and had never had cause to look at the guidance published by the Centre for Window and Cladding Technology (CWCT). He was aware that there were different types of insulation and he knew that Kingspan produced a solid board rather than a mineral wool product, but that was really the extent of his knowledge. No one had suggested to him that phenolic or PIR foam insulation boards were not appropriate for use in the external walls of buildings above 18 metres in height. | Materials | Fire Safety | Andrew McQuatt
The suggestion made by Andrew McQuatt in his email of 16 August 2012 that a PIR insulation product might be used did not give Bruce Sounes any cause for concern. He told us that PIR and phenolic insulation boards had become all but standard by that time and that PIR products were widely used in the industry, which reassured him about their suitability. Mr Sounes thought that Celotex FR5000 was suitable for use as part of the cladding system partly because it had been used in the past by Max Fordham in what he had understood to be similar circumstances, but he took no steps to find out whether Max Fordham had ever used FR5000 in the past in the external wall of a building over 18 metres in height. | Materials | Fire Safety | Bruce Sounes
He could not recall having read the datasheet for Celotex FR5000 when he was working on the project, nor did he recall noting at the time that it was rated Class 0, but if he had been aware of that it would have served only to increase his confidence in its use, because he understood that if a product was rated Class 0 it was, as he put it, “not hazardous”. Mr McQuatt did not realise that Studio E had understood his email of 16 August 2012 as a tacit endorsement of the safety of FR5000 for use on the building, but there is no reason why he should have done so, given that his expertise did not extend to fire safety and he had not been consulted about that. | Materials | Fire Safety | Bruce Sounes
Mr McQuatt wrote a Sustainability and Energy Statement in respect of the project dated 17 August 2012, which made it clear that the recommended U-value far exceeded that required by the Building Regulations. At Tables 2.2 and 2.3 of the report, Celotex FR5000 was identified as the insulation for the spandrels and columns. When he received it, Bruce Sounes did not pause to consider whether mineral wool could be used to produce a U-value which, although higher, still complied with the regulations. | Materials | Fire Safety | Bruce Sounes
On 10 October 2012, Max Fordham issued its RIBA Stage C report. Andrew McQuatt drafted most of it, with a contribution from Matt Smith. The information contained in the Sustainability and Energy Statement was repeated on page 12 of the report. Mr McQuatt explained that FR5000 had been referred to in the Stage C report solely because it delivered the U-value required at the thickness sought. | Materials | Fire Safety | Andrew McQuatt
Max Fordham’s Stage C report makes no reference to fire safety because its practice was to advise on questions of fire safety only to the extent that they affected the work that the building services engineer was specifying. We therefore infer that, as Max Fordham was not responsible for choosing the insulation, it did not regard itself as responsible for giving advice in the Stage C report about its use, whether in relation to fire safety or otherwise. | Materials | Fire Safety | Max Fordham
Studio E issued its own RIBA Stage C report on 31 October 2012. It incorporated Max Fordham’s Stage C report and referred to Celotex FR5000 as the chosen insulation. Before issuing the report, Bruce Sounes did not ask Exova or Max Fordham or any other specialists to advise on the suitability of using Celotex FR5000 in the cladding system or whether its use would comply with the Building Regulations. | Materials | Fire Safety | Bruce Sounes
In January 2013, Adrian Jess sent a draft of Studio E’s Stage D report to Leadbitter, which at that stage was expected to become the principal contractor for the project. It showed EPS (expanded polystyrene) insulation at the lower levels of the tower behind rainscreen panels. On 21 January 2013 Juan Medina, Framework Design manager for Leadbitter, sent Mr Jess an email asking whether Studio E had checked with building control whether EPS insulation could be used on a tower of that kind. Mr Medina understood that EPS was a combustible material and was not allowed as part of a rainscreen cladding system. He suggested that phenolic insulation should be used instead. The email was copied to Studio E and is therefore likely to have been seen by those at Studio E who were working on the project, including Bruce Sounes. | Materials | Fire Safety | Bruce Sounes
Although the discussion concerned the lower levels of the tower, it shows that Studio E was on notice from January 2013 that building control might not allow combustible insulation to be used in a rainscreen cladding system. That warning by Leadbitter ought to have prompted Studio E to pay close attention to the fire performance of the insulation materials that it had proposed for the project. However, from the documents available to the Inquiry, it does not appear that the warning resulted in any discussion of that kind within Studio E. | Materials | Fire Safety | Bruce Sounes
Studio E issued its final Stage D report on 20 August 2013, which proposed the use of Celotex FR5000. Between issue of its Stage C and Stage D reports there were no communications between Studio E, Max Fordham, Exova, or any other specialist about the safety of using FR5000 product or how it reacted to fire. | Materials | Fire Safety | Bruce Sounes
On 25 October 2013, Tomas Rek commented in an internal email to Bruce Sounes that Max Fordham’s U-values were “OTT”, i.e. excessive. Tomas Rek thought he had had a discussion with Mr Sounes about it, but he could not recall what Mr Sounes had said. Bruce Sounes did not remember any discussion of that kind. In any event, no further attempts were taken by Mr Rek to address his concerns. Mr Sounes thus missed the opportunity properly to understand Mr Rek’s concerns about the U-values and to check with Max Fordham whether they needed to be quite so ambitious. | Materials | Fire Safety | Bruce Sounes
We think it unlikely, however, that Bruce Sounes asked whether rigid foam insulation was acceptable for use on Grenfell Tower. If it had been sufficiently important in his mind for him to have done so, it is likely that Ray Bailey would have made some response and that he would have remembered what it was. It is also likely that there would have been some reference to it in the contemporaneous documents. Asking about the safety of PIR would not have been consistent with Mr Sounes’ understanding of its suitability in general or with his lack of curiosity about the fire safety of the products he proposed to use in the cladding system. | Materials | Fire Safety | Bruce Sounes
in the case of the insulation to be applied to the external concrete walls Studio E made a proprietary specification; in other words, in all three versions of the NBS Specification Celotex FR5000 was specified as the product to be used. However, that was subject to the qualification that the product could be substituted by a similar or equal alternative. The contract preliminaries provided that if a contractor wished to suggest an alternative product it was required to provide reasons for that substitution to the client. The NBS Specification was not unusually prescriptive and was no more detailed or prescriptive than specifications commonly written by Studio E. | Materials | Fire Safety | Bruce Sounes
Before specifying the product, neither Tomas Rek nor Bruce Sounes had investigated whether the use of Celotex FR5000 on a building above 18 metres in height complied with either the Building Regulations or the guidance contained in Approved Document B. Mr Sounes had not asked Max Fordham that question and he did not revisit it when overseeing the writing of the NBS Specification. Similarly, Mr Sounes did not seek advice from Exova about the suitability of FR5000 for use in the refurbishment before the NBS Specification was prepared. | Materials | Fire Safety | Bruce Sounes
Bruce Sounes said that Studio E would not usually seek to satisfy itself that all materials and products complied with the regulatory requirements before submitting a full plans application to building control. In his view it would be a waste of time to do so, because the contractor under a design and build contract might subsequently propose a change or building control might take a different view of their suitability. He said it was not common practice to do a full assessment of the suitability of products at RIBA Stages D or E. Mr Sounes did tell us, however, that before the submission of the full plans application to building control in August 2014, he had been reasonably confident that the materials specified in it complied with the Building Regulations and Approved Document B, because all the products had (as he believed) been used before in similar circumstances, either by Studio E itself or others. However, the steps he had taken to investigate precisely what had been used and in what circumstances were negligible. | Materials | Fire Safety | Bruce Sounes
Following the submission of the full plans application to building control there was no subsequent occasion on which Studio E would check whether the materials complied with the Building Regulations. Mr Sounes said that, because this was a design and build project, once the contract had been awarded the architect was, as he put it, “sidelined” so that Studio E was not policing what other people were doing. That, however, ignores the role played by Studio E after it had been engaged by Rydon. For the reasons we have explained below and in Chapter 63, it should have given further consideration to whether the insulation complied with the Building Regulations, but failed to do so. | Materials | Fire Safety | Bruce Sounes
At the time he prepared the NBS Specification, Tomas Rek did not know that the fire performance of each of the components of the cladding would need to be considered. | Materials | Fire Safety | Tomas Rek
It became clear during his oral evidence that his knowledge of Approved Document B was very limited. He was not familiar with the various different routes to compliance described in paragraph 12.5 of Approved Document B, or the definition of what would constitute a material of limited combustibility, or the guidance in paragraph 12.7. He could not recall having checked the requirements for external walls contained in Approved Document B when drawing up the specification. Nor could he recall talking to anyone at Studio E about which route to compliance with the Building Regulations it had taken in respect of the refurbishment of the external wall. | Materials | Approved Document B | Tomas Rek
The insulation to be used as part of the cladding was specified in clause H92/776 of the NBS Specification. Within section H92/776 of the RIBA software in use at the time for compiling an NBS Specification, the details were left blank for completion. Upon selecting clause H92/776, two tabs would appear: tab G, “Guidance” and tab H, “Manufacturers”. Under tab H there is a list of manufacturers available for selection derived from the NBS Plus database. At the time of drawing up the specification for the thermal insulation in November 2013, four manufacturers appeared in tab H: Kingspan with its K15 Kooltherm product, Knauf, Rockwool and Siderise. No Celotex product was listed under tab H. | Materials | Fire Safety | Studio E
Accordingly, in order to specify Celotex FR5000 it was necessary for the writer to enter the product manually. When Celotex FR5000 was manually entered under clause H92/776 a message appeared informing the compiler that that product had been authorised for an alternative clause, clause P10.1523 Clause P10 was the section covering insulation fitted between rafters. It would therefore require a conscious decision to enter FR5000 under that section of the NBS Specification despite the warning. | Materials | Fire Safety | Studio E
When a person drawing up the specification for clause H92/776 clicked on the dropdown box next to the entry for “Manufacturer”, the software would prompt him to select “mineral wool to BS EN 13162” as the only option and then provide a list of four manufacturers. If the writer did not wish to select a mineral wool product, that entry would have to be manually overridden. That is what happened here. Mineral wool was manually overridden and Celotex FR5000 was manually typed in at clause H92/776 of the NBS Specification. | Materials | System Override | Studio E
Clauses H92/220 and H92/310 of the NBS Specification stipulated that the contractor was to comply with CWCT Standard for Systemised Building Envelopes, including Part 6, which related to fire performance. It is not clear whether Mr Rek put that requirement into the NBS Specification. Although he knew that CWCT had published guidance, he had not read it and was not familiar with it. Nor was he familiar with the guidance issued by the Building Control Alliance (BCA). | Materials | Fire Safety | Tomas Rek
Tomas Rek would normally have expected tenderers to check that FR5000 complied with the CWCT performance requirements, but he did not do so himself. He said that if the material specified did not comply with that standard there would be a conflict which would have to be resolved. | Materials | Fire Safety | Tomas Rek
The NBS Specification was not sent to either Exova or Max Fordham for them to comment on the inclusion of FR5000 (or indeed at all). Bruce Sounes did not look to Exova to provide detailed checking of the specification because he did not consider that to be the focus of its work, which was to produce the fire safety strategy. | Materials | Fire Safety | Bruce Sounes
Following the inclusion of FR5000 in the NBS Specification, no further consideration was given to it during the procurement process or before award of contract to Rydon in March 2014. | Materials | Fire Safety | Bruce Sounes
Mr Roome of Celotex then familiarised himself with Approved Document B and knew that there were particular requirements relating to high-rise buildings. He knew that if one wanted to follow the guidance in Approved Document B, a PIR product could be used in the external wall of a high-rise building only if it was of limited combustibility or formed part of a system that had undergone a BS 8414 test and met the criteria in BR 135. He was also aware that FR5000 and other PIR products were neither materials of limited combustibility nor had been tested in a system that had undergone a BS 8414 test and met the criteria in BR 135. They could therefore not be used in the external walls of buildings above 18 metres in height consistently with the guidance contained in paragraphs 12.5-12.7 of Approved Document B. He knew that there was a distinction between Class 0 materials and materials of limited combustibility and was aware of the tests which a material needed to pass to obtain that classification. On 28 April 2014, his colleague Jonathan Roper sent him information about the FR5000 range of products and the BS 8414 testing regime. | Materials | Fire Safety | Jonathan Roome
In about April 2014 Mr Roome became aware that Celotex was seeking to develop an insulation product that could be marketed for use in buildings above 18 metres in height. He understood that the new product (which was formally launched as RS5000 in August 2014) was an equivalent product to Kingspan’s K15, if not better. As we have already explained, RS5000 was simply FR5000 re-marketed with the supposed benefit of having successfully met the BR 135 criteria in a particular wall construction, but that fact was not known to Mr Roome, who had been led to believe by his seniors in the marketing department that it was a brand new product. | Materials | Fire Safety | Jonathan Roome
On 10 June 2014 Mr Roome telephoned Ben Bailey of Harley to discuss another of Harley’s projects, Merit House. Ben Bailey wanted to know if Celotex had an alternative to Kingspan K15 that might be used at Merit House. Mr Roome said that because Merit House was a building above 18 metres in height Celotex did not have a suitable product, but that he would contact Harley once Celotex’s 18 metre fire test was in hand. That was a reference to a BS 8414 test using RS5000 which had been carried out 2 May 2014, the results of which were awaited together with the BR 135 classification report. | Materials | Fire Safety | Jonathan Roome
By June 2014 Jonathan Roome was aware that Harley had been awarded two new overcladding projects in London and between early June and the end of August 2014 Celotex saw Harley as a potential customer for RS5000. | Materials | Fire Safety | Jonathan Roome
As a result of his conversation with Mr Roome on 10 June 2014, Ben Bailey knew that Celotex did not then have any insulation products available that could be used on buildings above 18 metres in height. When he began work on the Grenfell Tower project he read through those parts of the NBS Specification which he considered relevant to Harley’s work. It did not occur to him, however, to question the specification of FR5000, despite knowing that Celotex did not have a suitable product. | Materials | Fire Safety | Ben Bailey
According to Ben Bailey, Jonathan Roome was very keen to stay in contact about the RS5000 product and to secure two overcladding projects, including the Grenfell Tower refurbishment. | Materials | Fire Safety | Jonathan Roome
RS5000 was launched at a meeting on 5 August 2014 attended by a number of Celotex’s employees, including Jonathan Roome. It was made clear to him that the reason RS5000 had (supposedly) been created and brought to market was for use on buildings above 18 metres in height and the communications strategy was to emphasise that it could be used on buildings of that kind. Mr Roome was provided with documents to pass on to potential customers, including a product data sheet for RS5000, a document entitled Rainscreen Cladding Compliance Guide and a document entitled Rainscreen Cladding Specification Guide.The purpose of the documents was to present RS5000 as a new product suitable for the insulation of buildings above 18 metres in height, which is what Mr Roome thought it was. | Materials | Fire Safety | Jonathan Roome
Having seen the documents, Mr Roome knew that RS5000 could not satisfy the requirements of paragraph 12.7 and table A7 of Approved Document B because it was not a material of limited combustibility. The construction of the system that had been tested on 2 May 2014, apparently successfully, was discussed at the presentation on 5 August 2014, from which he understood that the classification of RS5000 under BR 135 applied only to the system as tested and not to its individual components. He also knew that RS5000 could be used only in cladding systems that were identical to the system tested. | Materials | Fire Safety | Jonathan Roome
On 6 August 2014, Mr Roome sent Ben Sharman of Harley an email about RS5000 to which he attached a product comparison document, the rainscreen cladding compliance guide, the product datasheet and a rainscreen cladding datasheet. In his covering email he said, “I have the pleasure of informing you as of yesterday we have now launched the first PIR Board To Successfully Meet The Performance Criteria in BR 135 For Insulated Rainscreen Cladding Systems, Therefore Acceptable For Use In Buildings Above 18m in Height”. | Materials | Fire Safety | Jonathan Roome
Jonathan Roome had taken that wording from a document prepared by Celotex’s marketing team. It did not include the qualification that RS5000 was suitable for use on high-rise buildings only as part of a cladding system that was identical to the system that had been tested and therefore was, as he accepted, potentially misleading. | Materials | Fire Safety | Jonathan Roome
In his email of 6 August 2014 Mr Roome asked to visit Harley’s offices to present the new product. Neither he nor any of Harley’s witnesses could recall the precise date or circumstances in which that had occurred, but various conversations took place between Mr Roome, Daniel Anketell-Jones, and Ben Bailey about RS5000. | Materials | Fire Safety | Jonathan Roome
As at August 2014, Celotex was working on two projects for Harley (neither of them high-rise buildings) and Jonathan Roome hoped that Celotex could secure more work from Harley. | Materials | Fire Safety | Jonathan Roome
Ray Bailey said that because RS5000 was a new product, Harley had wanted to be sure that it was safe and suitable for the Grenfell Tower project. He said that Celotex had been keen to emphasise that it complied with BS 8414 and was suitable for buildings over 18 metres in height. | Materials | Fire Safety | Ray Bailey
Ray Bailey was wrong in thinking that Celotex products were materials of limited combustibility. | Materials | Fire Safety | Ray Bailey
Daniel Anketell-Jones knew nothing about the BS 8414 test or BR 135 classification and did not form any view about whether testing under those regimes meant that RS5000 could be used on Grenfell Tower. He did not trouble to read the RS5000 sales literature and did not see the qualifications and warnings. | Materials | Fire Safety | Daniel Anketell-Jones
Jonathan Roome did not discuss with anyone at Harley the differences between FR5000 and RS5000, despite the fact that FR5000 rather than RS5000 had been included in the NBS Specification which Mr Anketell-Jones had seen. Similarly, Mr Roome did not point out to anyone at Harley that RS5000 could be used only on buildings over 18 metres in height if the cladding system corresponded exactly to the one that had been tested. Neither Harley nor Celotex made a comparison between the cladding system tested and the cladding system proposed for Grenfell Tower. | Materials | Fire Safety | Jonathan Roome
Jonathan Roome accepted that the limited relevance of the BS 8414 test involving RS5000 was important and that it was important that Harley understood it. He accepted, however, that he had not specifically drawn Mr Anketell-Jones’s attention to it. His excuse was that Mr Anketell-Jones was a specialist and that he had thought he understood it from the information contained in the marketing literature Harley had been given. Mr Roome did not insist on seeing the composition of the cladding system proposed for Grenfell Tower to enable him to advise Harley whether RS5000 was suitable, nor did he point out to anyone at Harley that FR5000 might not be safe to use on buildings over 18 metres in height. Harley did not ask Mr Roome for information about the BS 8414 test beyond that which was contained in the marketing literature and Mr Roome did not volunteer any. | Materials | Fire Safety | Jonathan Roome
When Mr Crawford started work on the project, therefore, FR5000 was the insulation product included in the NBS Specification. Neil Crawford could not recall whether Mr Sounes had told him that FR5000 had been specified as the insulation to be used within the external facade, but it is likely that he had read Max Fordham’s Stage C report and had seen the reference to it there. Handover from Mr Sounes to Mr Crawford. | Materials | Fire Safety | Neil Crawford
Neil Crawford had some recollection of having seen the product datasheet for FR5000 but could not recall when he first saw it. At all events, he did not take any steps to check it when he learnt that FR5000 had been specified for use in the external wall. | Materials | Fire Safety | Neil Crawford
On or around 28 August 2014 Mr Anketell-Jones and Mr Roome discussed those calculations. Mr Roome recorded their discussions in a note in which he recorded that Mr Anketell Jones had said that the calculations had been performed using FR5000 but that he needed to use RS5000 at a thickness of 150mm. That is the first reference we have seen to the use of RS5000 in place of FR5000 at Grenfell Tower. | Materials | Fire Safety | Daniel Anketell-Jones
Studio E had specified FR5000, not RS5000, and Mr Anketell-Jones, like others at Harley, had no reason to think that they were the same product, especially in circumstances where Mr Roome himself thought that they were not. | Materials | Fire Safety | Jonathan Roome
The NBS Specification had been completed in January 2014, about eight months before the launch of RS5000. Studio E could not have checked the suitability of RS5000 before the NBS Specification had been finalised because the product did not then exist under that name. We reject Mr Anketell-Jones’ evidence about his reason for adopting RS5000 in place of FR5000. | Materials | Fire Safety | Daniel Anketell-Jones
It is unlikely that Jonathan Roome expressly advised Harley that RS5000 was suitable for Grenfell Tower, but he accepted that he knew Grenfell Tower was over 18 metres in height and that he might well have told Mr Anketell-Jones that the product was suitable for use on such buildings because it was the only product available for that application. | Materials | Fire Safety | Jonathan Roome
There had been no conversations between Harley and Celotex which could justify his coming to that view; indeed, quite the opposite. He thought that RS5000 was a new product, not least because that was exactly what Jonathan Roome had told him. For his part, Mr Roome did not know otherwise, having been induced to think that RS5000 was indeed a new product by those at Celotex who briefed the marketing department. In circumstances where RS5000 was being marketed as a new product there is no credible basis on which Mr Anketell-Jones could have thought that it was the same as FR5000 and that there was therefore no need to investigate its fire performance. | Materials | Fire Safety | Daniel Anketell-Jones
Change from FR5000 to RS5000 ought to have led Harley to investigate why FR5000 had originally been specified, why RS5000 was being substituted and whether it was a suitable product for use on the tower | Materials | Fire Safety | Daniel Anketell-Jones
We do not accept Mr Anketell-Jones’ explanation of his role at Harley; in particular, we do not accept that it was as limited as he suggested | Materials | Fire Safety | Daniel Anketell-Jones
Neil Crawford merely confirmed, he said, that there was a typographical error in the NBS Specification; he therefore assumed that Studio E had checked the suitability of RS5000. | Materials | Fire Safety | Neil Crawford
The difficulty with Ben Bailey’s evidence is, again, that the last version of the NBS Specification was dated 30 January 2014, some eight months before the launch of RS5000. Studio E therefore cannot have intended to specify RS5000. | Materials | Fire Safety | Ben Bailey
If Ben Bailey did have a conversation with Neil Crawford of the kind he described, he did not tell anyone at Harley about it. Nor did he mention it in his witness statement. Neil Crawford did not mention any such conversation and there is no indication in the documents that Studio E expected RS5000 to be used. For those reasons we do not accept Ben Bailey’s evidence on that matter. | Materials | Fire Safety | Ben Bailey
None of the other Harley witnesses and none of the Studio E witnesses suggested that Neil Crawford, or anyone else at Studio E, had been informed of the change from FR5000 to RS5000 or that Studio E had accepted RS5000 for use on Grenfell Tower, as Mr Bailey maintained. We are therefore unable to accept Ray Bailey’s evidence on this question. We conclude that Studio E never investigated the suitability of RS5000 for use at Grenfell Tower and did not accept its use. | Materials | Fire Safety | Ray Bailey
Looking at the evidence as a whole, we are satisfied that Jonathan Roome did tell Daniel Anketell-Jones that RS5000 was suitable for use in buildings above 18 metres in height. That was consistent with Celotex’s communications strategy and with the evidence given by both Mr Anketell-Jones and Mr Roome himself. We think it unlikely, however, that Mr Roome gave any assurance that RS5000 was suitable for use in the specific cladding system being proposed for Grenfell Tower. | Materials | Fire Safety | Jonathan Roome
None of the witnesses could recall any conversation with Celotex about the proposed construction of the external wall and, at least in September 2014, Mr Roome had not seen any relevant drawings or specifications. He therefore had no basis for giving any specific assurance. Indeed, given the presence in the marketing literature of the warning that the BR 135 classification applied only to the system as tested, we think it unlikely that Mr Roome would have given an assurance of that kind in circumstances where there was a risk that someone in the design team might eventually read it and challenge him. | Materials | Fire Safety | Jonathan Roome
No one at Harley read the marketing literature carefully or sent it to Studio E or Exova to comment on. Harley did not ask Celotex or Studio E whether a desktop study had been done to support the use of RS5000 and did not inquire whether any other members of the design team had asked for a desktop study or other assessment to support the proposed system. Daniel Anketell Jones simply accepted what Jonathan Roome had told him about the suitability of RS5000 for use on buildings above 18 metres in height and assumed that it complied with the relevant statutory requirements. On that basis he told Mr Roome that RS5000 was needed for use at Grenfell Tower | Materials | Fire Safety | Daniel Anketell-Jones
Although Jonathan Roome was canny enough to avoid giving any specific assurance to Harley that RS5000 was suitable for use on Grenfell Tower, we think he suspected that Harley had not understood the warning in Celotex’s marketing literature. He certainly never drew Harley’s attention to it, which was consistent with Celotex’s marketing strategy to downplay it and tuck it away in the small print. | Materials | Fire Safety | Jonathan Roome
After a discussion everyone agreed to check their calculations. Neil Crawford did not know why Rydon had wanted to recheck the U-values; he understood that they had been derived from Max Fordham’s advice but did not recall in any detail how the target had been established. Daniel Anketell-Jones and Kevin Lamb also attended that meeting and Mr Anketell-Jones checked the U-values by making another calculation using the “BuildDesk” software. This time he used RS5000 in the calculation, but that did not prompt him to consider its fire safety. | Materials | Fire Safety | Daniel Anketell-Jones
We do not accept Mr Anketell-Jones evidence. We think he drafted the request in his role as Harley’s design manager, part of which did involve considering the fire performance of the external walls which Harley was designing. On 17 September 2014, Daniel Anketell-Jones sent a formal Request for Information to Rydon and Studio E about the extent to which horizontal fire breaks were required within the cladding. In summary, Harley believed that horizontal firebreaks might be required at every floor level but not in the area between the windows, because there was no “chimney effect” at that location. | Materials | Fire Safety | Daniel Anketell-Jones
Neil Crawford sent the request to Terence Ashton of Exova and asked him to comment on Daniel Anketell-Jones’ “interpretation”. Exova was then provided with some Harley drawings and Mr Ashton replied on 18 September 2014 saying that if the insulation in the cavities behind the rainscreen cladding were combustible it would be necessary to provide cavity barriers even if there was no continuous cavity from the top to the bottom of the building. As we have explained in Chapter 54, that advice was incorrect in so far as it implied that combustible insulation could be used provided cavity barriers were installed. | Materials | Fire Safety | Terence Ashton
Neil Crawford sent that email on to Daniel Anketell-Jones the same day. Mr Anketell Jones said that he had read Mr Ashton’s response but formed no view about it. He did not question why Mr Ashton appeared to be linking the combustibility of the insulation to the requirement for cavity barriers. Mr Anketell-Jones replied to Mr Crawford and Rydon the same day saying that because the insulation was Class 0, he thought that a fire barrier (i.e. a cavity barrier) in those locations would not be necessary and asking for confirmation. He attached the RS5000 product datasheet to his email. That appears to have been the first time that Studio E had been informed of the change from FR5000 to RS5000. | Materials | Fire Safety | Daniel Anketell-Jones
We do not accept that Mr Anketell-Jones was as naïve and ignorant as he pretended. In that email, he was giving his opinion of the fire classification of the insulation (Class 0) and whether that meant that fire barriers were necessary in certain locations. It reflects his view of what was meant by Class 0. He said he had not checked his opinion with any of his colleagues or against any published guidance because he was concerned only with matters of structural engineering. It is certainly true that he did not check his opinion with anyone else or against any available guidance, but we doubt whether he made any positive decision not to do so. | Materials | Fire Safety | Daniel Anketell-Jones
Daniel Anketell-Jones said that he had looked at the product datasheet, had seen that RS5000 was rated Class 0, and had passed that on to Studio E and Rydon. Neil Crawford then asked Mr Ashton to provide his view on whether Class 0 insulation obviated the need for cavity barriers in certain locations. In response Mr Ashton pointed out that a material which has a Class 0 rating is not necessarily non-combustible although the reverse is invariably true and that it was therefore necessary to prevent the spread of fire from one flat to the flat above. It was not clear from the information he had been given whether there was a continuous cavity from top to bottom in any part of the cladding, irrespective of the type of insulation. | Materials | Fire Safety | Terence Ashton
Mr Anketell-Jones did not give any consideration to Mr Ashton’s advice that, in summary, a Class 0 insulation may not be sufficient for fire safety. Even having read that advice, it did not occur to him to question whether RS5000 was suitable, as he continued to believe that RS5000 had already been approved by Studio E, building control, and the fire engineer. | Materials | Fire Safety | Daniel Anketell-Jones
We have already concluded that Daniel Anketell-Jones’ professed understanding was wrong and that RS5000 had not been checked for suitability by Studio E, nor had Studio E confirmed that RS5000 was suitable for use at Grenfell Tower. Mr Anketell-Jones’ belief that the fire engineer had already approved RS5000 makes little sense, given that Exova itself was inquiring about the type of insulation to be used in the external wall. It is clear that Exova did not know what insulation it was proposed to use and so could not have already approved it. Accordingly, we reject Mr Anketell-Jones’ evidence that he thought that RS5000 had already been approved by Exova. In fact, at no stage did he raise with anyone at Rydon, Studio E or Exova the combustibility of the insulation, nor did he take any steps following the Request for Information to investigate whether RS5000 complied with the Building Regulations or the guidance in Approved Document B. | Materials | Fire Safety | Daniel Anketell-Jones
Although Neil Crawford was right to refer some of those questions to Exova, he regarded himself as little more than a post-box and failed to ask himself the question whether the switch to RS5000 was appropriate for Grenfell Tower. Once Studio E had been put on notice that an apparently new product was being proposed, it should have ensured that its fire performance was appropriate. | Materials | Fire Safety | Neil Crawford
Mr Crawford admitted that he had effectively taken it on trust from Harley that it was. He also said that he had read the Celotex literature and was convinced that it was suitable for use, but, if he did read it, he failed to notice that the product was not of limited combustibility or that the system that Celotex had tested was not the same as the one intended for installation on the tower. We accept Mr Hyett’s opinion that Studio E’s approach fell below the standards to be expected of a reasonably competent architect exercising reasonable skill and care. | Materials | Fire Safety | Neil Crawford
Mr Roome did not tell Mr Anketell-Jones that RS5000 could not be used on any of Harley’s projects unless the cladding system was, in each case, exactly the same as the one that had been tested. Mr Roome accepted that Mr Anketell-Jones had either not read the warnings or had misunderstood them (or even intended to ignore them), but denied that he had realised that at the time. | Materials | Fire Safety | Jonathan Roome
Mr Anketell-Jones understood that RS5000 was not suitable for all rainscreen applications and that the suitability of the product had to be determined in relation to each building individually. Despite his professed understanding, and despite the nature of the questions being asked by the client on the other project, however, he did not consider it important to check whether the proposed system was the same as the one that had been tested. He should have known by January 2015 that whether RS5000 was suitable for use in a particular application depended entirely on whether the proposed system corresponded precisely with the one tested, but he assumed, wrongly, that it depended on how the particular fire consultant or building control officer interpreted the information | Materials | Fire Safety | Daniel Anketell-Jones
BRE Classification Report, the thermocouple data from the test (showing the maximum temperatures recorded during testing) and the RS5000 product information sheet, not discussed by Mr Anketell -Jones or Mr Roome. | Materials | Fire Safety | Jonathan Roome
Most natural reading of the emails sent by Mr Anketell-Jones on 16 and 20 January 2015 is that he knew that the construction of the external wall was critical when assessing the suitability of RS5000 for the purposes of fire safety. That has led us to doubt his attempts to play down the extent of his knowledge about fire performance testing and the importance of his role within Harley on the Grenfell project. We are satisfied that he understood more about the technical aspects of fire safety than he was prepared to admit and as design manager he should have been responsible within Harley, together with others, for checking the fire performance of the products used in the external wall. | Materials | Fire Safety | Jonathan Roome
It is a matter of serious concern, therefore, that he made no comparable efforts to check the suitability of RS5000 for use on the Grenfell Tower project, but merely assumed it without any investigation. He said that he had not read the 12-page BRE report or the thermocouple data Mr Roome had sent to him on 21 January 2015 and had not sent it to Kevin Lamb, Studio E, or anyone else because he thought that had already been done and that it was not Harley’s responsibility to do it. | Materials | Fire Safety | Daniel Anketell-Jones
Again we cannot accept his evidence on that point. These exchanges occurred almost a year after the final issue of the NBS Specification. If he believed that RS5000 was a new product, Mr Anketell-Jones cannot have thought that the technical information he had obtained from Celotex had been in Studio E’s possession when it specified the insulation material almost a year earlier. We consider that at that point, if not before, Mr Anketell-Jones ought to have conducted his own research and, if necessary, asked Celotex, Studio E or Rydon whether RS5000 was suitable for use at Grenfell Tower. | Materials | Fire Safety | Daniel Anketell-Jones
Celotex was aware of the differing technical sophistication of potential buyers and that it realised that the market for RS5000 was likely to be limited to those who lacked expertise or expert advice or who did not understand, or had not bothered to investigate, the fire performance of RS5000. That reflects a deeply cynical view that there were ignorant or reckless contractors in the market of whom advantage could be taken without any regard for the safety of occupants. Certainly there is no evidence that the safety of residents played any part in Celotex’s thinking on how to sell RS5000, at least when it came to Grenfell Tower. Tier 1, tier 2 and tier 3 customers for Celotex. | Materials | Fire Safety | Celotex
Celotex regarded Harley as a Tier 3 customer and exploited its willingness to accept what it was told and its lack of interest in understanding when RS5000 could be used safely. It refrained from correcting Harley’s misunderstanding and encouraged it to pursue the purchase regardless of the product’s suitability for the project in hand. That was not the behaviour to be expected of an honest and plain-dealing manufacturer. | Materials | Fire Safety | Celotex
Mr Roome turned a blind eye to the failure of Daniel Anketell-Jones to ask the sort of questions in relation to Grenfell Tower that he had asked in relation to a different project in January 2015. Celotex recognised that Harley was ill-informed, or was acting recklessly, and exploited its lack of interest in the circumstances in which RS5000 could safely be used. | Materials | Fire Safety | Daniel Anketell-Jones
Although it provided Harley with some technical information, it deliberately refrained from any attempt to ensure that Harley was fully informed about the suitability of RS5000, an approach that was entirely consistent with its marketing strategy. | Materials | Fire Safety | Jonathan Roome
No one at Harley expressly told Mr Roome that the rainscreen was to be Reynobond ACM and it did not occur to him that the construction of the external wall might be different from that tested in May 2014. | Materials | Fire Safety | Daniel Anketell-Jones
Mr Roome gave no consideration to the fact that Harley thought it was permissible to use 150mm of RS5000 as opposed to 100mm and did not turn his mind to the fact that the calculations based on 200mm or 160mm of RS5000 meant that the system proposed for Grenfell Tower would not be the same as that tested and would therefore not be covered by the BR 135 classification. | Materials | Fire Safety | Jonathan Roome
We do not accept Ray Bailey’s evidence on that point. We doubt that he was deliberately seeking to mislead us; it is more likely that he had persuaded himself of the truth of a story he had told himself ever since the fire. We are satisfied, however, that Harley did not ask Celotex for a formal assessment of the kind he described and was not given one, let alone an unqualified assurance that RS5000 was suitable for use in the external wall construction proposed for Grenfell Tower, although it certainly allowed Harley to obtain that impression, and knew it. When pressed Mr Bailey himself accepted that he did not know whether Celotex had provided any such assessment. | Materials | Fire Safety | Ray Bailey
Ray Bailey knew that the classification report based on the BS 8414 test applied only to the system tested and he knew that that system differed from the system proposed for Grenfell Tower. It is hard to understand, therefore, on what basis he could possibly have thought that RS5000 was suitable for use in the external wall system at Grenfell Tower. For its own part, Harley cannot avoid responsibility for its own failures by blaming Celotex for not telling it what it should have known or discovered for itself. | Materials | Fire Safety | Ray Bailey
On 8 April 2015 Jonathan Roome sent BCA Technical Guidance Note 18, issue 0 to Daniel Anketell-Jones. Mr Anketell-Jones said that he had not previously seen it and had not read through it. The additional information should have led him to look again at the documentation sent to him by Celotex in August 2014, but he did not do so. | Materials | Fire Safety | Daniel Anketell-Jones
We do not accept that Mr Roome formed any view at the time about how Harley intended to demonstrate compliance with the Building Regulations or that he cared. He suspected that Harley had either not read or not understood the warning in the Celotex marketing literature and pursued the sale regardless of the consequences. | Materials | Fire Safety | Jonathan Roome
SIG was one of a small number of major distributors of Celotex and other insulation products and supplied RS5000 for use at Grenfell Tower. SIG invoiced Harley for its first order of RS5000 on 1 April 2015. | Materials | Fire Safety | SIG
Mr Roome proposed that Grenfell Tower could be used as a case study because it was one of the first major projects in which RS5000 was being used on a building above 18 metres in height. Despite intending to publish a leaflet describing the product and its use on the tower, Mr Roome did not ask Mr Bailey what the rainscreen was to be. Ben Bailey knew that RS5000 had not been widely used before, but he did not realise that Grenfell Tower was being treated by Celotex as a flagship project for the use of the product, although the very suggestion that it be treated as a case study might have alerted him to that fact. | Materials | Fire Safety | Jonathan Roome
Kingspan K15 insulation was used in substitution for RS5000 on Grenfell Tower from time to time when Harley encountered problems with the supply of RS5000. It was used in much smaller quantities than RS5000, but the amount was not insignificant. | Materials | Fire Safety | Harley
K15 was not included in the NBS Specification and no substitution of materials described in the Employer’s Requirements or Contractor’s Proposals was permitted without the prior written consent of the TMO. It was Rydon’s responsibility to obtain that consent, but it failed to do so in relation to the substitution of K15 for RS5000. | Materials | Fire Safety | Rydon
Harley and Rydon never advised Mr Sounes or Mr Crawford that K15 was being used. | Materials | Fire Safety | Rydon
On 4 March 2015, Mark Stapley of Harley sent SIG an email requesting a quotation for K15 for comparison purposes with RS5000. Shows K15 was being considered. | Materials | Fire Safety | Mark Stapley
We accept that Harley decided to substitute K15 for RS5000 because of difficulties obtaining RS5000 on time, but we do not accept that Mr Bailey had a telephone conversation with SIG of the kind he described. Mr Bailey’s response to Ms Walker’s email of 26 May (“Are you joking?!”) conveys an immediate reaction, not one that followed a telephone call during which he had already been told about the delay. Moreover, if Ms Walker had discussed with him the suitability of K15 as an alternative, it is likely that she would have referred to it in her next email. We think it much more likely that the use of K15 as an alternative to RS5000 was suggested by Ben Bailey in his reply to Ms Walker. We do not accept that she told him at any time that K15 was an equivalent product to RS5000. | Materials | Fire Safety | Ben Bailey
Ray Bailey described K15 as a standard insulation product throughout the industry for tall buildings | Materials | Fire Safety | Ray Bailey
Ben Bailey was confident about using K15 because Harley had used it on other projects. He shared his father’s understanding that K15 could be used on high-rise buildings and in combination with any rainscreen. He did not look at the LABC certificate or the relevant BBA certificate; indeed, Harley had on file only the 2008 version of the BBA certificate, which by June 2015 was more than five years old and had been superseded. | Materials | Fire Safety | Ben Bailey
Any research or investigation conducted by Ben Bailey must necessarily have been very limited. He did not consider whether the cladding system proposed for Grenfell Tower was the same as that which had included K15 and had apparently met the criteria in BR 135 following a test in accordance with BS 8414. | Materials | Fire Safety | Ben Bailey
Ray Bailey accepted that Harley had not investigated whether there was any test evidence which showed that K15 was of limited combustibility and agreed that Harley ought to have made further enquiries about the combustibility of K15 before using it on Grenfell Tower. The literature did not show that K15 was safe for use on Grenfell Tower. | Materials | Fire Safety | Ray Bailey
Harley was under pressure from Rydon to keep up progress in accordance with the programme of works. | Materials | Fire Safety | Rydon
Simon Lawrence accepted that obtaining consent from the TMO was his responsibility during his time on the project. | Materials | Fire Safety | Simon Lawrence
We are satisfied that Ben Bailey acted on his own initiative to substitute K15 for RS5000 in order to avoid a delay to the programme. Harley’s previous use of the product had led him to believe that K15 was suitable for use on high-rise buildings in conjunction with any rainscreen system. That assumption was, however, wrong. | Materials | Fire Safety | Ben Bailey
We think that Ben Bailey, who was a young and inexperienced site manager, succumbed to pressure, actual or perceived, from the main contractor to keep up with the construction programme. He thought that K15 was essentially the same as RS5000 and in his mind there was no reason to think that it was unsafe. | Materials | Fire Safety | Ben Bailey
David Hughes thought that Mr Bailey was asking his permission to use K15 in the future and agreed that he could. Shortly afterwards Mr Hughes told Stephen Blake and the clerk of works, Jon White, about the substitution. | Materials | Fire Safety | David Hughes
Having considered all the evidence, we have come to the conclusion that Rydon did not become aware of the use of K15 until December 2015 or January 2016, long after it had first been installed on parts of the facade. However, photographs from September and November 2015 clearly show Kingspan insulation on the building and Rydon could have noticed that, if it had bothered to look. | Materials | Fire Safety | Rydon
Mr Blake assumed that K15 was equivalent in every respect to RS5000 and did not take any steps to establish its suitability for use on the project. In fact, he thought that Mr Hughes was describing the same material manufactured by different companies. He acknowledged that he ought to have checked for himself whether the products were essentially the same. | Materials | Fire Safety | Steve Blake
No one at Rydon consulted Studio E about the substitution; nor did Rydon take any advice from Exova or any other fire engineer to confirm that K15 was safe for the intended use. There was, therefore, a complete failure on Rydon’s part to investigate the suitability of K15 for its intended use. After it had become aware that K15 was being used, Rydon relied on Ben Bailey’s assurance that K15 was an equivalent product to RS5000, which everyone assumed was suitable. | Materials | Fire Safety | Rydon
Neither Mr Hughes nor Mr Blake consulted the TMO or informed building control that a substitution was going to be, or had in fact been, made, Mr Hughes thought that K15 and RS5000 were very similar and that the substitution did not make any difference. Building control was not provided with any document which showed that K15 was being used as insulation and no attempt was made to obtain the TMO’s consent to the substitution at that or any other stage. | Materials | Fire Safety | Steve Blake
Chapter 57 Cavity Barriers
We have concluded that none of the construction professionals gave adequate consideration to the use of cavity barriers at any stage of the design process. | Cavity Barrier | Fire Spread | All
Also an aspect of the design that received scant attention from building control, either in the course of reviewing the drawings or during inspections on site. | Cavity Barrier | Fire Spread | All
Cavity barriers were not installed in the correct positions and were entirely missing around the windows. In addition, many of the cavity barriers which were fitted were poorly installed. | Cavity Barrier | Fire Spread | All
Although the failure to ensure that cavity barriers were properly installed within the cladding probably had little effect on the ultimate development of the fire, it demonstrates a worrying lack of attention to fire safety which we think it is important to record as part of our analysis of the events which led to the tragedy | Cavity Barrier | Fire Spread | All
Possible that the absence of cavity barriers around the windows played a part in enabling the fire to escape from Flat 16 and gain unrestricted access to the combustible insulation and ACM PE cassettes. For those reasons we explain below how it came about that the cavity barriers at Grenfell Tower were so poorly designed and installed. | Cavity Barrier | Windows | All
Two types of cavity barrier, horizontal and vertical. | Cavity Barrier | Fire Spread | All
No consideration of cavity barriers by Studio E or Exova at all. | Cavity Barrier | Fire Spread | Studio E
Mr Crawford accepted that Studio E’s cavity barrier strategy did not require the installation of cavity barriers around the windows. | Cavity Barrier | Fire Spread | Neil Crawford
At no point did Studio E produce detailed drawings of typical elevations or sections for use at tender stage showing precisely where cavity barriers were to be positioned. | Cavity Barrier | Fire Spread | Studio E
On 22 August 2014, Kevin Lamb produced some preliminary drawings to establish the basic principles of the design which he sent to Simon Lawrence of Rydon and copied to Studio E and Daniel Anketell-Jones of Harley. Those drawings did not indicate where cavity barriers would be placed within the facade. | Cavity Barrier | Fire Spread | Kevin Lamb
Mr Crawford provided further comments on Harley’s drawings on 3 Sept 2014 following a design team meeting but did not refer to the absence of cavity barriers. On 12 Sept 2014, he confirmed that he had no further comments to make. | Cavity Barrier | Fire Spread | Neil Crawford
Mr Ashton’s response was that if the insulation in the cavities was combustible it would be necessary to provide cavity barriers in order to prevent fire from spreading from one flat to the flat above. That advice was wrong, however, because cavity barriers were required regardless of the nature of the insulation. | Cavity Barrier | Fire Spread | Terence Ashton
Mr Anketell-Jones did not ask Mr Ashton why cavity barriers were required only if the insulation was combustible and Mr Ashton did not comment on the absence of cavity barriers from Harley’s or Studio E’s drawings. | Cavity Barrier | Fire Spread | Daniel Anketell-Jones
Stephen Blake of Rydon agreed that the use of cavity barriers around the windows of Taplow House had been a critical factor in preventing the spread of fire. He also agreed that he had first-hand knowledge of the importance of cavity barriers around windows, but despite that, he did not think it necessary to check with Studio E or Harley that proper cavity barriers had been included in their designs. | Cavity Barrier | Taplow House | Steve Blake
Harley and Rydon did not bear those lessons in mind from Taplow House when considering the design in the areas surrounding the windows of Grenfell Tower. Ray Bailey accepted that it was a mistake not to have done so. | Cavity Barrier | Taplow House | Ray Bailey
Kevin Lamb took no steps to revise the cavity barrier strategy for Grenfell Tower. | Cavity Barrier | Fire Spread | Kevin Lamb
Ray Bailey sent the exchange to Daniel Anketell-Jones for his comments. Mr Anketell-Jones replied: “Just that it’s ridiculous. There is no point in ‘fire stopping’, as we all know; the ACM will be gone rather quickly in a fire! The whole point is to stop ‘unseen’ fire spreading in the cavity and moving to other parts of the building.” | Cavity Barrier | Fire Spread | Daniel Anketell-Jones
Made no sense for Ben Bailey to disregard Mr Mort’s concerns about the design of the window head simply because the dispute over the rating of the cavity barriers had been resolved shortly afterwards. It was foolhardy to ignore the very clear warning about the design of the window, since it should have been plain to anyone reading Mr Mort’s email and reviewing his sketches that the two issues were distinct from one another. | Cavity Barrier | Fire Spread | Ben Bailey
Although Harley had been alerted in that way to the presence of a potential route for fire to spread at the head of the window, it did not take any steps to make good the defect, either by referring it to the design team for discussion, or by revising its design. | Cavity Barrier | Fire Spread | Harley
Mr Lawrence’s evidence, however, betrayed a failure to understand his responsibility for ensuring that the external wall of the building complied with the requirements of the Building Regulations. | Building Regs | Fire Spread | Simon Lawrence
Harley contacted Siderise on a number of other occasions during the life of the project seeking advice about cavity barriers. Despite that, it did not occur to Ben Bailey to inform himself about the guidance which was available in Approved Document B. The correspondence demonstrates a concerning lack of knowledge and expertise within Harley in relation to the use and siting of cavity barriers, which led to undue reliance on the advice of the manufacturer. Ben Bailey was unable to explain that lack of expertise and could not recall whether he had sought advice from Mr Anketell-Jones, Mr Lamb or Studio E. | Cavity Barrier | Fire Spread | Ben Bailey
The installation of the external facade, including cavity barriers, was carried out by Osborne Berry Ltd as a subcontractor. Mr Osborne had no formal training in the installation of rainscreen cladding facades. The company had no experience of installing cavity barriers with intumescent strips and, as far as Mr Berry was aware, it had not previously installed cavity barriers manufactured by Siderise. Harley did not maintain a permanent presence on site and there was no clerk of works in the traditional sense, so there were times when Osborne Berry and their workmen were unsupervised when installing the facade. | Cavity Barrier | Fire Spread | Osborne Berry
Mr O’Connor did not attempt to check the positions of the horizontal cavity barriers against the drawings, because that was not his personal responsibility, and he therefore did not notice that they had not been positioned in accordance with the drawings. However, he accepted that placing them incorrectly constituted defective workmanship, for which Rydon (amongst others) would be responsible. He would have expected that kind of poor workmanship to be picked up under Rydon’s quality assurance and inspection regime and could not explain why that had not happened. | Cavity Barrier | Fire Spread | Rydon
After the fire the remaining cavity barriers were inspected and found to have various defects. In particular, a. The horizontal cavity barriers were found to have been installed with air gaps in excess of 25mm and in some places the material had been poorly cut and fitted to the surrounding structure with gaps between adjacent barriers at joints. b. Gaps had been left between the vertical cavity barriers and the cladding panels. c. Incorrect fixing brackets had been used. d. In some cases the fixing brackets had been spaced too widely. e. Some cavity barriers in the area of the columns were missing or had gaps. f. Horizontal cavity barriers had been used in the vertical position, with the intumescent edge installed directly against the concrete. | Cavity Barrier | Fire Spread | Rydon
Mr Hoban of RBKC building control also visited the site and carried out inspections. He had not received any training on the installation of cavity barriers in cladding systems, or indeed cladding systems more generally, but a building control officer could be expected to be shown on site what to look for and to be aware of the need to check the manufacturer’s instructions about how the barriers should be installed. Mr Hoban did not check whether cavity barriers had been installed around the windows because most of the windows had by that time been installed and therefore it was not possible to see where the cavity barriers should have been. He did not ask to look behind the windows because he had seen cavity barriers being installed in other locations and so did not think it necessary to do so. | Cavity Barrier | Fire Spread | John Hoban
Studio E never produced any elevation drawings showing how the horizontal cavity barriers at the top of the building would meet the vertical cavity barriers. Mr Sounes confirmed that the risk that the crown might contribute to the spread of a fire in the external wall had not been considered because no one had been aware of the risks posed by ACM panels. | Cavity Barrier | Fire Spread | Bruce Sounes
Chapter 58 Window Infill Panels
Window infill panels may have played an important part in the early development of the fire in and immediately outside Flat 16. | Window Infill | Fire Spread | All
If a customer did not specify a core material, Panel Systems offered Styrofoam as standard because of its thermal efficiency. In those circumstances it would not generally inform the customer of Styrofoam’s fire performance, nor would it tell the customer that it should check whether the use of that material in the particular circumstances they had in mind would comply with the Building Regulations. Panel Systems marketed its insulating panels by reference to the fire rating of the core material, which was the primary factor in their performance. It therefore marketed panels with Styrofoam cores as European Class E. | Window Infill | Fire Spread | All
At all events, there is no reason to think that anyone at Harley gave serious consideration to the fire performance of the panels. | Window Infill | Fire Spread | Harley
The responsibility for ensuring that the fire performance of the core was appropriate rested with Harley, not with Panel Systems. | Window Infill | Fire Spread | Harley
We think it clear that Studio E had an obligation under its contract with Rydon to take reasonable steps to ensure that all designs, whether produced by itself or any sub-contractors, complied with the relevant statutory requirements, including the Building Regulations. Mr Crawford’s understanding that it was not his role to check the materials specified by Harley to ensure that the external wall was compliant with the Building Regulations was therefore wrong. He ought to have applied his mind to the fire performance of the window infill panels, both as a matter of contractual obligation and in the exercise of reasonable skill and care, but he failed to do so. | Window Infill | Fire Spread | Neil Crawford
As we noted in Chapter 62, John Hoban, the building control officer at RBKC responsible for the Grenfell Tower refurbishment, also received Harley’s specification notes on 6 March 2015. He did not notice that Styrofoam and Kingspan TP10 were being proposed as the insulating material in the window infill panels and did not look at the BBA certificates relating to either material; nor did he question the use of those materials. He candidly accepted that he should have done so. | Window Infill | Fire Spread | John Hoban
Given the lack of interest shown by Harley, Rydon and Studio E in the fire performance of the insulating cores of the window infill panels, we think it unlikely that any of them would have objected to the use of Styrofoam in the P2 panels. | Window Infill | Fire Spread | All
Chapter 59 Window Reveals
In his Phase 1 report the chairman concluded that the window reveals had provided a route for fire to spread from the interior of Flat 16 into the cladding. He found that the fire had probably entered the cladding as a result of hot smoke impinging on the uPVC window surrounds causing them to deform and fall away, together with the insulation which was attached to them. That created a gap which allowed the fire to gain access to the cavity behind the ACM panels and ignite combustible materials. | Window Reveal | Fire Spread | All
Since it is likely that the failure of the window reveals played an important part in allowing the fire to escape into the cladding, we think we should summarise the factors that in our view contributed to their inadequate performance. First, Studio E should have produced detailed 1:5 scale drawings clearly identifying the insulation referred to in the NBS Specification and showing where it was to be placed. Next, Rydon should not have accepted Harley’s suggestion that uPVC boards, with poorer fire resistance, should be used for the window reveals in place of plywood just to cut cost, because there was a significant difference in fire performance. Next, Rydon should have sent the NBS Specification to SD Plastering or should at least have given it instructions about the fire performance of the materials to be used in the window reveals. It should not have allowed combustible Celotex or Kingspan insulation to be used instead of the mineral wool insulation specified by Studio E to be fitted around the windows. Finally, neither Rydon nor SD Plastering gave any consideration to the fire performance of the insulation or the construction of the window reveals as a whole, which was unsuitable for its purpose | Window Reveal | Fire Spread | All
Chapter 60 The Smoke Ventilation System
The purpose of a smoke ventilation system is to protect the escape route. In a high-rise building that may involve preventing smoke from entering the stairs and it may also involve at the same time removing it from the corridors and lobbies, which will thereby also obtain a measure of protection. | Smoke Ventilation | Smoke Spread | All
The type of system originally installed in Grenfell Tower was a system based on natural ventilation, but with the addition of fans that firefighters could operate to assist the movement of air into and out of the building. If the fans were not operated, the system functioned as a natural inlet and outlet system. | Smoke Ventilation | Fans | All
Original system operated by ventilating the lobby area with the intention of protecting the escape route through the lobby. | Smoke Ventilation | Lobby | All
Original system fell into disrepair and had failed to work in a previous fire in April 2010. March 2014 LFB issued deficiency notice due to dampers not working. | Fire Safety | Fire Safety Notice | Fire Brigade
Oct 2014 TMO was aware system was beyond repair. | Smoke Ventilation | Repair | KCTMO
TMOs Assets and Regeneration H&S Group decided to tender for replacement with a view to beginning in Dec 2011. | Smoke Ventilation | Replacement | KCTMO
Jul 2012, TMO instructed Max Fordham to expand the scope of the tower's refurbishment to include smoke ventilation system as AECOM had recommended. | Smoke Ventilation | Repair | Max Fordham
Even if the existing smoke ventilation system had been working, necessary to extend it to the new lobbies that were being created on the lower floors. | Smoke Ventilation | Lobby | All
Exova said provision of ventilation was critical for tower's "stay in place" evacuation principle. | Stay Put | Evacuation | Exova
In Issue 3 of the Outline Fire Safety Strategy dated 7 Nov 2013 reference to the smoke ventilation system was limited to noting that it would be overhauled as part of the refurbishment of the building and would be covered in a separate report by Max Fordham. There was no further consideration of the system as part of the fire safety strategy. | Smoke Ventilation | Repair | Max Fordham
On 9 Nov 2012 PSB responded to Mr McQuatt saying that it did not see anything wrong with the proposed design. Following the consultation with PSB the design intent for the improved system was revised to bring it as close to the current regulations as possible within the limitations imposed by the existing shafts. In addition to providing a working smoke ventilation system, it was intended to use the system to provide ventilation to the lobbies to prevent overheating. | Smoke Ventilation | Repair | PSB
Max Fordham’s proposals for the new system did not undergo any changes during that period, but it proved difficult to demonstrate to building control that the new system would be an improvement on the existing system or at least would not make it any worse. The fact that the existing system was not in working order and the paucity of documentation surrounding its installation made it difficult for the designers to compare its performance with the expected performance of any proposed replacement. | Smoke Ventilation | Repair | Building Control
On 25 Oct 2013, Max Fordham repeated its proposals for the new system, stating that, as it was not possible to adapt the existing system to meet current standards, its intention was to bring the existing system up to as high a standard as possible. At that stage, therefore, the proposal was still to improve the existing system rather than replace it with an entirely new one. Max Fordham acknowledged that there were no directly applicable standards that could be used as a basis for the design of the improved system but considered that it was reasonable to aim at providing 15 air changes an hour. That may have been based on conversations with Exova. | Smoke Ventilation | Repair | Max Fordham
On 25 Oct 2013 Bruce Sounes of Studio E submitted Max Fordham’s proposals to RBKC building control, together with the draft Outline Fire Safety Strategy for the building prepared by Exova. In his covering email Mr Sounes said that the design team thought that agreement on the smoke ventilation system was the single biggest risk to the proposals, but that they did not think it was reasonable to leave the existing system in place. | Smoke Ventilation | Repair | Bruce Sounes
On 11 Nov 2013 John Allen, the building control manager at RBKC, told Mr Sounes that the information submitted by Studio E was not adequate to enable an effective consultation to be held with the LFB. However, he said that if it could be shown that the new system was no worse than the existing system, the design would be acceptable. | Smoke Ventilation | Repair | John Allen
On 6 Dec 2013, in a memorandum to Mr Allen, Paul Hanson, then responsible for the Means of Escape Group within RBKC building control, provided further observations on the proposals. He noted that it was not proposed to redesign the system to bring it up to modern standards, as that was likely to require larger shafts, but that building control had indicated that, provided the performance of the system was not made worse, the Building Regulations did not require it to be replaced. | Smoke Ventilation | Repair | Building Control
Simon Lay, one of the experts from whom we heard evidence, was of the opinion that, since the new system was being designed specifically for Grenfell Tower, Exova, Max Fordham and PSB ought to have ensured that a CFD analysis was carried out. He considered that in failing to do so they had fallen below the standards reasonably to be expected of them. Dr Lane also considered that Exova and Max Fordham should have made sure that a CFD analysis was carried out. | Smoke Ventilation | CFD Analysis | Max Fordham
Pressure of time was not a reasonable justification for failing to carry out such an analysis. The existing system had not been in working order for a long time and a further delay of weeks or even months was not a sufficient reason not to analyse properly the performance of the proposed replacement. | Smoke Ventilation | CFD Analysis | Max Fordham
On 24 Nov 2014 at a meeting between building control, Studio E, the TMO and Max Fordham to discuss the system, PSB and JS Wright (Rydon’s electrical and mechanical sub-contractor) put forward an alternative system, the outline of which was contained in a technical submission from PSB dated 12 Nov 2014 produced by Mr Mahoney. | Smoke Ventilation | Repair | Rydon
Dampers are mechanical devices used to prevent air or gases from passing through ducts or from the openings of ducts into the space beyond. | Smoke Ventilation | Dampers | All
The ability of a damper to minimise the leakage of smoke was directly relevant to its suitability for use in the smoke ventilation system of the tower, because the vertical shafts used to extract smoke passed through the lobbies, which were part of the escape route for the occupants of the flats on those floors. A damper that prevented the passage of fire alone would not have been suitable. | Smoke Ventilation | Dampers | All
Statement in Gilberts brochure was therefore inaccurate and misleading, because the test method to which it referred requires testing from the open position. There was no suggestion by Gilberts in the brochure or otherwise that the damper was a smoke control damper in the recognised sense. | Smoke Ventilation | Dampers | Gilberts
Another note recommended that the purchaser discuss the specific technical requirements of the damper with the relevant authority to ensure that it was acceptable but there is no evidence that any of the contractors involved in designing or installing the smoke control system discussed the matter with RBKC building control. | Smoke Ventilation | Dampers | Building Control
In spite of the incorrect and misleading statements about certification and testing in Gilberts’ 2011 brochure and its first quotation, any recipient of Exova’s report who carried out even a cursory review of those results would have understood that the Series 54 damper held no certification whatsoever and had failed the smoke leakage test immediately. The recipients of that report included Mr Mahoney and, in due course, RBKC building control. | Smoke Ventilation | Dampers | Exova
In the absence of test data evidencing their durability there could be no confidence that the dampers would perform properly in a fire after many months of use in a combined environmental and smoke ventilation system. | Smoke Ventilation | Dampers | Exova
Although it received a copy of the Exova report, PSB does not appear to have reviewed the specification of the dampers or to have discussed it with building control. It should have done so, but we have seen nothing to suggest that the implications of Exova’s report were identified or acted upon. PSB should have realised that the Gilberts Series 54 damper was unsuitable for this application. | Smoke Ventilation | Dampers | PSB
Surprised that PSB does not appear to have tried to find appropriately certified dampers. At the very least, it should have told J S Wright about the limitations of the Series 54 damper so that the risks of using it could be properly assessed. | Smoke Ventilation | Dampers | PSB
Mr Lay was of the opinion that, although the Series 54 dampers were not certified and did not meet the alternative Smoke Control Association recommendations, their performance characteristics could allow them to perform adequately as part of the system. However, we do not agree. | Smoke Ventilation | Dampers | PSB
The Series 54 dampers did not meet the requirements for smoke leakage, which was important for protecting routes of escape, and had not been shown to meet the durability requirements. In the absence of reliable test results (i.e. results of tests conducted in accordance with recognised standards) from which to draw inferences, we cannot safely make any findings about how a component might have performed. The point of testing standards is to provide an assurance that a product meets the specified performance criteria and no such assurance was provided in relation to the Gilberts Series 54 dampers. | Smoke Ventilation | Dampers | PSB
It is possible that the use of the Gilberts Series 54 dampers contributed to the breach of compartmentation by permitting more smoke to pass from the shafts into some of the lobbies than would have been the case if appropriately certified dampers had been used, but it is impossible now to tell whether that was in fact the case. However, circumstances surrounding the choice of dampers demonstrates insufficient concern for fire safety to which we think it important to draw attention as part of the events which led to the tragedy. | Smoke Ventilation | Dampers | Gilberts
Exova and the TMO, as the client, should have ensured that the Outline Fire Safety Strategy specifically described the final design of the smoke control system and explained how it supported the fire safety strategy for the building. | Smoke Ventilation | Repair | Exova
However, we are not persuaded that any of the parties involved in the design of the new smoke ventilation system actually relied on the LGA Guide to support its design. It was not referred to in any of the design documents, the witness statements or the oral evidence of those who were involved at the time. | Smoke Ventilation | LGA Guide | All
Evidence suggests that the travel distances were overlooked or that it was assumed that they did not need to be considered because the increase in distance was only around 2 metres. That was not an acceptable approach. | Smoke Ventilation | Travel Distance | All
When it was drafting the fire safety strategy Exova should have identified the extended travel distances in the lobbies and should have recorded its view of the need for mitigating measures to be provided. When the design of the system was changed, Exova should have been asked to consider the fire strategy again to ensure that it reflected developments in the design. | Smoke Ventilation | Travel Distance | Exova
PSB not considered leakage which respresented defect with design process. | Smoke Ventilation | Leakage | PSB
Was important for the designers of the system to identify the circumstances under which it would no longer be able to perform in accordance with its design. The design criteria should have been taken into account in the overall fire safety strategy for the building. | Smoke Ventilation | Leakage | PSB
We think that unless detailed flow measurements under different conditions of door opening had been made, a cold smoke test should have been performed as part of the commissioning process | Smoke Ventilation | Testing | All
Failure to record the performance of the fans, the commissioning of all dampers, door opening forces, or pressure measurements. | Smoke Ventilation | Testing | All
Errors with commissioning method statement and fireman's override switches. | Smoke Ventilation | Testing | All
Building Control shouldn't have accepted the commissioning report. | Smoke Ventilation | Testing | Building Control
TMO had no formal procedures of its own for the maintenance of the smoke ventilation system, having entered into a contract with Allied Protection Ltd for the inspection and servicing of fire safety equipment, including the smoke ventilation system | Smoke Ventilation | Maintenance | KCTMO
Although Allied Protection was required to service the system at 6-monthly intervals in accordance with manufacturer’s instructions, the TMO did not provide those instructions until 14th June 2017. | Smoke Ventilation | Testing | Allied Protection
Overall, the maintenance documentation provided for the smoke ventilation system was poor and did not satisfy the guidance in BS 9999: 2008. Neither the limited weekly test carried out by Mr Steadman (a TMO estate services assistant) or Allied Protection’s checks provided clear evidence of rigorous maintenance and inspection consistent with what was recommended by the guidance. | Smoke Ventilation | Testing | Allied Protection
Allied Protection carried out inspection and maintenance visits without sight of the manufacturer’s instructions and sent an engineer to carry out the inspection on 15 May 2017 who lacked the skill to do the job properly | Smoke Ventilation | Testing | Allied Protection
Little evidence, therefore, that the smoke extraction fan at Level 2 was inspected and maintained in a way that would give one confidence that it would operate effectively if there were a fire. | Smoke Ventilation | Testing | Allied Protection
Chapter 61 The Health and Safety File
CDM regulations require the production of a health and safety file once construction works have been completed. Under the 2007 Regulations the duty to produce a health and safety file lay on Artelia as CDM co-ordinator. Under the 2015 Regulations, the duty lay on the TMO as principal designer. | CDM Regulations | Principle Designer | KCTMO
The health and safety file is an important document. It contains detailed information about work carried out on a building (whether by way of a new construction or refurbishment), including fire safety information. | CDM Regulations | Principle Designer | KCTMO
No health and safety file had been produced. | CDM Regulations | Principle Designer | KCTMO
TMO decided to take on the task itself on the basis of advice it had received, probably from Simon Cash of Artelia, that the design was “fundamentally complete”. It took that decision on the basis that it would ask Rydon to complete the health and safety file. For the purposes of the CDM Regulations 2015, however, it was the obligation of the TMO as principal designer to prepare the health and safety file. | CDM Regulations | Principle Designer | KCTMO
Neil Reed warned Claire Williams that if the TMO took on the role of principal designer, it would need someone to check the health and safety file and confirm that it was compliant. He offered to make someone available as a CDM adviser for that purpose but the offer was refused. | CDM Regulations | Principle Designer | Claire Williams
Dr Lane's particular criticisms of the health and safety file, which we accept, were that it did not enable the persons responsible for any work on Grenfell Tower to understand the condition of the building and the hazards and risks arising from the refurbishment. Nobody sought to challenge Dr Lane’s evidence, which was to a large extent limited to the contents of the documents. | CDM Regulations | Health and Safety File | Barbara Lane
We are satisfied that the health and safety file did not contain the information referred to in the relevant guidance and was not presented in a form that made it readily usable. The TMO failed to ensure that the file was properly organised and contained accurate and up to date information about the refurbishment. Overall, it was incomplete, confusing and thoroughly unhelpful. | CDM Regulations | Health and Safety File | KCTMO
Health and Safety file should have been available on the night of the fire. | CDM Regulations | Health and Safety File | KCTMO
Chapter 62 Building Control
Two surveyors were largely responsible for the project, John Allen, the special projects manager, from 2012 to late 2013, and John Hoban, a senior surveyor, from late 2013 to July 2016. Paul Hanson, a fire engineer in the department, also gave advice on matters concerning functional requirements B1 and B5 of the Building Regulations. | Surveyors | Building Regulations | Building Control
In Sept 2013 the department was restructured and John Allen became Building Control Manager. | Surveyors | Building Regulations | John Allen
Evidence suggests that the role of the Means of Escape group within the department was not well understood, particularly by other professionals working on the Grenfell refurbishment, and Mr Hoban agreed that its relationship with the surveyors could have been clearer. Ms Menzies thought that the department could have made better use of the Means of Escape group generally, in particular because Mr Hanson was a qualified fire engineer. | Means of Escape Group | Structure | John Hoban
RBKC was unable to find the hard-copy file for the Grenfell refurbishment or Mr Hoban’s personal notebooks covering the relevant period, but because of the weeding policy it is not clear which documents would have been retained. | Surveyors | Notebooks | John Hoban
We have seen no indication that the use of a tracker in connection with the refurbishment was proposed by building control or that it was requested by Studio E or Rydon. | Tracker | Project | Building Control
Mr Allen told us that he had not known that the refurbishment involved overcladding the building until around the time of the full plans application. | Materials | Cladding | John Allen
On 7 Nov 2012 Studio E and Exova had a meeting with building control to discuss the fire safety strategy. However, that meeting and subsequent communications between the design team and building control focused primarily on the lower four floors of the tower and the smoke ventilation system. The proposals for overcladding the tower were not discussed with building control either at that meeting or at any time before the full plans application was submitted in Aug 2014, but by the time he took over responsibility for the project in late 2013, John Hoban had become aware that it involved overcladding, because he had seen it on the drawings. | Materials | Cladding | John Hoban
He told us that he would have expected a contractor or architect to seek advice from building control on cladding proposals before it submitted a full plans application, but neither Rydon nor Studio E had done so in this case. Having seen that the project included overcladding, we consider that Mr Hoban should at that stage have taken the initiative and asked for more information about the project as a whole. | Materials | Cladding | John Hoban
On 25 Oct 2013, Studio E sent building control its proposed fire safety strategy for the tower, including Issue 2 of Exova’s Outline Fire Safety Strategy. On 11 Nov 2013, John Allen told Bruce Sounes that he did not think that the information on the smoke control system that had so far been submitted was adequate to enable an effective consultation to be held with the fire authority on functional requirements B1 and B5 as required by the Fire Safety Order. In Jan 2014, Studio E sent an email to building control asking them to consult the fire authority notwithstanding their concerns about the extent of the information available to them, but they did not do so at that time. There was no further contact between the design team and building control between Jan 2014 and Jul 2014. | Fire Safety Strategy | Smoke Control | Building Control
On 4 Aug 2014 Studio E submitted a signed but undated full plans application to building control. By that time some demolition and site clearance work had already begun and Mr Hoban considered that the application had been made rather late in the day. | Full Plans Application | Fire Safety | Studio E
Fundamental misunderstanding among many of those who work in the construction industry, contractors, building control bodies and others, that the function of building control is to provide a service to applicants rather than to enforce the regulations robustly for the benefit of the community at large. In this case Mr Hoban accepted, in hindsight, that he ought to have rejected the full plans application for lacking the necessary supporting documentation. | Full Plans Application | Fire Safety | John Hoban
Building control did not make a decision within the prescribed time and there is no evidence that any extension of time was agreed with either Rydon or Studio E. Mr Allen said that the statutory time limits did not work in the context of design and build projects and that there was little point in rejecting an incomplete application because building work could still go on. We found that part of his evidence rather disturbing, because it amounted to saying that in his eyes the legislation had to give way to commercial considerations and the practices of the construction industry. We do not think that is a proper approach to take to a statutory function and we are fortified in that conclusion by the evidence of Ms Menzies, who could see no reason why the statutory time limits could not be adhered to in the case of design and build projects. | Full Plans Application | Fire Safety | John Allen
Unfortunately, Mr Hoban’s response to the full plans application lacked rigour and fell short of the standard to be expected of a reasonably competent building control officer. He accepted that if he had exercised reasonable care and skill he would have asked Studio E for the information that was needed, but there is no record of his having done so, save for the “meaningful response” note, which does not record what further details he asked for. | Full Plans Application | Fire Safety | John Hoban
We are not persuaded that Mr Hoban made a real effort to obtain the missing information from Studio E. He told us on more than one occasion that he had asked Rydon to provide him with information and that he had obtained some information for himself by looking at things on site, but very little of that is documented in his notes and those requests, if they were made at all, were not followed up by letters or emails. Mr Hoban ought to have asked for further information about the cladding at the full plans stage. His failure to do so represents a serious failing on the part of building control. | Full Plans Application | Fire Safety | John Hoban
We think it likely that Mr Crawford’s recollection that Mr Hoban took drawings away with him is mistaken. | Full Plans Application | Fire Safety | Neil Crawford
Studio E did not submit any drawings to building control until 24 Sept 2014 when Mr Crawford sent a zip file attached to an email. The contents of the zip file did not reflect the drawings listed in the covering email but Mr Hoban did not question that at the time. | Full Plans Application | Fire Safety | Neil Crawford
Although no further details of the cladding were formally submitted, drawings sent to building control for other purposes in Nov 2014 and Mar 2015 showed ACM rainscreen panels on the facade. Mr Hoban could not remember whether those drawings had alerted him to the change from zinc to ACM. | Full Plans Application | Fire Safety | John Hoban
On 25 Sept 2014 RBKC planning officers approved the use of Reynobond smoke silver cassette-fixed ACM panels but Studio E did not inform building control of that at the time and, as we have noted, the drawings submitted to building control continued to refer to zinc panels. | Full Plans Application | Fire Safety | Planning Officers
Mr Hoban did not ask Exova (or anybody else for that matter) whether a further report had been or would be provided to complete the advice on functional requirement B4 and he conceded that he might not have gone back to the file and done everything necessary. His failure to do so was another serious omission. | Full Plans Application | Fire Safety | John Hoban
Mr Hanson responded to Mr Hoban on 10 Nov 2014 saying that building control was not in a position to approve the proposals due to a lack of information about the extraction rate of the smoke ventilation system. Notwithstanding the absence of that information, on 11 Nov 2014, Mr Hoban submitted a formal request to the LFB for their comments on matters affecting functional requirements B1 and B5. He did not ask for its comments on functional requirement B4. The LFB would not normally comment on requirement B4 unless it had been specifically asked to do so. | Full Plans Application | Fire Safety | John Hoban
On 18 Nov 2014 Mr Hoban told Neil Crawford that a formal decision notice on the full plans application would be forwarded shortly. At that point a response from the fire authority was still outstanding. Mr Hoban said that he had completed the standard form decision notice with a schedule of conditions but no copy was available and there is no record of the conditions. Mr Hoban said that he had put it out for the business support group to process, but there is no evidence that a notice was actually sent out and Mr Hoban did not check whether it had been. | Full Plans Application | Fire Safety | John Hoban
There is no written record of the review of the full plans application that led Mr Hoban to issue the decision notice. He said that he had prepared a memorandum in relation to functional requirements B2, B3 and B4 but no copy of any such document was made available to us. When asked how he had concluded that the proposals were likely to comply with the Building Regulations, Mr Hoban said that there would have been conditions and when asked how he was able to issue a decision notice when Mr Hanson had said in his comments on functional requirement B1 that building control could not approve the proposals, he again said that it would be subject to conditions. Mr Hoban apparently felt able to approve the full plans application, even though it did not contain any details of the proposed insulation or rainscreen panels, because he had included a condition that the facade as a whole should comply with section 12 of Approved Document B. However, he did not have a specific recollection of the conditions he had attached to the decision notice and did not know whether he had recorded them elsewhere. We have not seen any documents or correspondence referring to specific conditions of any kind. Mr Allen said that he would expect any conditions applied to a full plans approval to be recorded in writing and kept on the file. In our view the failure to keep a formal record of a matter of that kind was a very serious omission. | Full Plans Application | Fire Safety | John Hoban
On 12 Dec 2014, the LFB sent building control an email attaching a response to the consultation, but neither building control nor the LFB has been able to find the response itself. On 5 Feb 2016, following revisions to the smoke control proposals, building control consulted the LFB again and on 4 Mar 2016 the LFB expressed itself satisfied with the proposals. | Full Plans Application | Fire Safety | Building Control
Mr Hoban approved the full plans application despite Mr Hanson’s advice that there was insufficient information in relation to functional requirement B1 to enable that to be done. He also consulted the fire authority without sufficient information and did not wait for a response before making his decision. | Full Plans Application | Fire Safety | John Hoban
In addition, he failed to carry out a methodical review of the documents submitted to him and failed to notice obvious errors and inconsistencies in the drawings. He either did not read version 3 of Exova’s Outline Fire Safety Strategy or failed to appreciate that on its own terms it was incomplete in an important respect. The only evidence we have seen of a structured review of the full plans application is the memorandum prepared by Mr Hanson on Requirement B1. | Full Plans Application | Fire Safety | John Hoban
We do not know what, if any, conditions Mr Hoban attached to his approval of the full plans, but if, as he suggested, they included a condition that the cladding comply with section 12 of Approved Document B, that would not have been sufficient to enable him to issue a completion certificate in due course. It ought to have required Studio E to provide sufficient evidence that functional requirements B2, B3 and B4 had been met. | Full Plans Application | Fire Safety | John Hoban
Other formal aspects of the application were also handled poorly. RBKC failed to issue a formal decision notice, which it accepted was a failing on its part. Mr Hoban accepted that he ought to have ensured that the decision notice he had prepared had been sent out, but he failed to do so. All in all, RBKC’s approach to the full plans application shows a consistent lack of care and disregard for the procedural requirements of the Building Regulations. RBKC accepted that it bore some responsibility for the failure of the applicant to provide sufficient information in a structured and easily accessible format, but its failings at full plans stage were far more extensive than that. | Full Plans Application | Fire Safety | John Hoban
Mr Hoban failed to ask for basic information about the cladding, did not carry out a proper review of the information he was provided with and gave a conditional approval in circumstances where he ought to have rejected the application altogether. Mr Hoban’s willingness to accommodate Studio E led him to disregard the primary function of building control, with the result that a critical opportunity to scrutinise the design of the cladding was missed. | Full Plans Application | Fire Safety | John Hoban
No correspondence or documentation of any kind passing between building control and any of those engaged on the refurbishment which touches on the question whether the proposed composition of the external wall complied with the Building Regulations. Moreover, no comprehensive package of up-to-date drawings and information was ever provided to building control. | Full Plans Application | Fire Safety | Building Control
However, Mr Hoban knew that ACM was being used because the contractor had told him so at some stage and he had seen the materials once they had arrived on site. He could not say with certainty that he had noticed that ACM had been indicated on the drawings sent to him in Nov 2014 or Mar 2015, but he thought that he had become aware that ACM panels were being used in around 2015 when he met Ben Bailey on site. He was not surprised when he saw ACM being installed instead of zinc as, in his words, “things change”. | Materials | Cladding | John Hoban
Unlikely checking of BBA certificate by Mr Hoban. | BBA Certificate | Fire Safety | John Hoban
Building control officers can be expected to examine certificates of that kind to ascertain whether materials are suitable for the use for which they are intended | BBA Certificate | Fire Safety | John Hoban
Mr Hoban not referred to safety of the crown. | Crown | Fire Safety | John Hoban
Mr Hoban could not say whether he had had any discussions about the insulation with Rydon, Studio E or Harley before looking it up on line and he could not remember whether he had asked any of them for evidence that the insulation was appropriate for use in the cladding system. | Insulation | Fire Safety | John Hoban
Mr Hoban agreed that he had accepted at face value the statement that Celotex RS5000 had passed a BS 8414 test and that he had not been entitled to assume that the design and construction team had checked the suitability of the cladding materials for themselves. | Insulation | Fire Safety | John Hoban
Mr Hoban’s evidence taken in the round has left us in some doubt about exactly what he did to identify the insulation or to satisfy himself that it complied with the Building Regulations. First, and most importantly, he failed to identify the fact that it was not of limited combustibility. It is not clear what information about Celotex he looked at online, but whatever it was, he did not examine it carefully. Instead, he simply accepted the assertion that RS5000 was suitable for use on tall buildings.2709 Critically, he failed to investigate whether the design of the cladding system proposed for Grenfell Tower was the same as that which had been tested in the BS 8414 test to which the product literature referred and did not ask Studio E to obtain test reports to justify its use. He accepted that that had been a serious failing on his part.2 | Insulation | Fire Safety | John Hoban
Mr Hoban did not become aware that Kingspan insulation was being used and no one from Rydon, Harley or Studio E told him that it had been substituted for Celotex RS5000 on occasions.2711 Mr Hoban said that if he had known that he would have looked at the BBA certificate relating to it.2 | Insulation | Fire Safety | John Hoban
Mr Hoban agreed should have chceked what materials were used for infill panels. | Infill Panels | Fire Safety | John Hoban
At all events, Mr Hoban did not check the windows on site to see whether cavity barriers had been installed around them because the work that he had seen had, in his view, been of an adequate standard. He accepted, however, that he should have done so. | Cavity Barriers | Fire Safety | John Hoban
Mr Hoban lack of site visits and not checked cladding. | Site Visits | Fire Safety | John Hoban
Regulation 38 of the Building Regulations requires the person carrying out the works to pass fire safety information to the Responsible Person for the purposes of the Fire Safety Order. Under regulation 17 of the Building Regulations, if the Fire Safety Order applies to a building on completion of the work (as in the case of Grenfell Tower), the local authority has a duty to issue a completion certificate confirming that the requirements of regulation 38 have been satisfied if, after taking all reasonable steps to do so, it has been able to ascertain that that is the case. | Regulation 38 | Fire Safety | John Hoban
Mr Allen said that they did not take independent steps to satisfy themselves that that had been done and that his personal practice was just to check with the client if someone happened to be on site towards the end of a project. Not surprisingly, Mr Hoban adopted the same practice. He believed that he had asked David Hughes whether Rydon had sent the information to the TMO, but he did not record either the question or the answer in writing. | Regulation 38 | Fire Safety | John Allen
The practice adopted by RBKC did not in our view amount to taking all reasonable steps to ascertain whether regulation 38 had been satisfied and did not follow the procedural guidance in force at the time. | Regulation 38 | Fire Safety | John Allen
Mr Hoban caused a completion certificate for the Grenfell refurbishment to be issued in the name of Mr Allen on 7 July 2016. He agreed that, given that the external wall did not comply with functional requirement B4 of the Building Regulations, he should not have done so. We accept that when he caused the certificate to be issued Mr Hoban thought that the functional requirements of the Building Regulations had been satisfied, but his failure to scrutinise the design and execution of the work with sufficient rigour meant that his confidence was entirely misplaced. In its statements to the Inquiry RBKC has rightly accepted that a completion certificate should not have been issued. | Certificate | Fire Safety | John Hoban
The two most serious errors made by Mr Hoban were, first, the failure to recognise that the presence of unmodified polyethylene cores rendered the ACM panels highly combustible, and second, the failure to recognise that the insulation, which was visible on the tower during his site visits, was not of limited combustibility. | Materials | Fire Safety | John Hoban
Mr Hoban 25 years experience but not right training and learning. | Training | Fire Safety | John Hoban
The Grenfell Tower refurbishment was Mr Hoban’s first residential high-rise overcladding project and, apart from the KALC project, for which he also assumed responsibility, his first design and build project. Surprisingly, Mr Allen was not aware of either fact, although we think he should have been. | Training | Fire Safety | John Hoban
We agree with them that a building control officer should be capable of examining manufacturers’ information and test data critically and we do not understand why Mr Hoban thought otherwise. If he did not know how to read manufacturers’ information or how to evaluate test data, he ought to have asked someone within the department for assistance. | Training | Fire Safety | John Hoban
He trusted Studio E and Exova because he had worked with them on the KALC project and was reassured by the fact that Mr Ashton was involved in the refurbishment. | Training | Fire Safety | John Hoban
Although Mr Hoban must bear primary responsibility for the failure of RBKC’s building control department to deal properly with the refurbishment project, his ability to carry out his task effectively was hampered by an excessive workload and poor management of the department as a whole. He told us that he had been very busy at the time of the refurbishment and candidly accepted that that had affected his work. That had led him to give priority to other work, particularly in 2015 and 2016. | Workload | Fire Safety | John Hoban
John Allen said that with a small team there would be rare occasions on which a lot of work would come in at the same time and he would have to manage that and plug gaps, but he did not accept that there had been a substantial increase in the amount of Mr Hoban’s work after the restructuring. | Workload | Fire Safety | John Allen
Mr Hoban told us, however, that at that time he had been coming in to work at weekends and although Mr Allen did not think that the department as a whole was overstretched, we think that Mr Hoban clearly was. At times during the period between 2014 and 2016 he was unable to manage his workload and the quality of his work suffered as a result. He did not feel able to ask for support from his manager and there was no one else to whom he could take his concerns. | Workload | Fire Safety | John Hoban
There was also a failure by RBKC’s building control department to ensure that officers within the department received the training they needed to do their work properly. A building control body should provide continuing professional development for its officers, as is reflected in the Building Control Performance Standards. As a member of the Royal Institute of Chartered Surveyors, Mr Allen was required to undertake regular training, and in the years 2013 to 2017 he had exceeded the minimum hours required of him. He took responsibility for providing technical training to his officers on matters to do with the Building Regulations, but did not organise training on Approved Document B generally or on the fire safety risks posed by cladding systems on high-rise buildings | Training | Fire Safety | Building Control
Similarly, there does not appear to have been any system for ensuring that officers had the knowledge and understanding to examine manufacturers’ information critically, nor were they told that it was important to read certificates, such as BBA certificates, critically and in their entirety. Mr Allen expected his officers to possess those skills already. We do not think that building control officers would normally expect to receive formal training on examining product literature, but that they would normally acquire that skill through their work and from discussions with others. | Training | Fire Safety | John Allen
Mr Allen was aware of confusion in the industry about the meaning of Class 0. Mr Hoban could not recall whether he had been aware of it but he had been aware of manufacturers’ propensity to use misleading terms more generally. | Training | Fire Safety | John Allen
In Oct 2015, Jose Anon (John Allen’s deputy at the time) attended the London District Surveyors’ general meeting where those present discussed a building in Southwark over 18 metres in height on which PIR insulation had been installed. They were told that Kingspan had confirmed that its PIR insulation was combustible. The notes of the meeting also referred to the need for cladding to be of limited combustibility. Mr Allen did not know whether Mr Anon had shared that information with the RBKC building control team but in our view Mr Anon should have ensured that information of that kind was disseminated through the department. | Training | Fire Safety | John Allen
Mr Allen told us that he had regular meetings with the officers and would assess their general competence but we saw no concrete evidence to suggest that he actively checked the officers’ skills to ensure that they had a basic knowledge and understanding of the problems that could arise. The failure to monitor the knowledge and skills of individual officers and to ensure that they received the training needed for them to carry out their function effectively was in our view a serious weakness in the way RBKC’s building control department was run. It was compounded by a failure to recognise that Mr Hoban was struggling to keep up with the work allocated to him and to take steps to ensure that he had the time and knowledge needed properly to oversee a project as substantial as the Grenfell refurbishment. The absence of a quality management system meant that the defects in Mr Hoban’s work were not identified. | Training | Fire Safety | John Allen
Record-keeping within the department was poor. | Record Keeping | Fire Safety | John Allen
Mr Allen was aware that Mr Hoban was behind in writing up site visit notes. | Record Keeping | Fire Safety | John Allen
We have no doubt that the shortcomings in the management of the department to which we have referred played a significant part in Mr Hoban’s failure to carry out his role properly. | Training | Fire Safety | John Allen
Although we have found that other parties, in particular those responsible for the design of the cladding, bear considerable responsibility for the fact that following the refurbishment the external wall of Grenfell Tower did not comply with the Building Regulations and was dangerous, building control was the last line of defence and had a statutory obligation to check for compliance with the Building Regulations. It had a responsibility to protect the public and it wholly failed to perform that function. It therefore bears considerable responsibility for the dangerous condition of Grenfell Tower immediately on completion of the refurbishment. | Responsibility | Fire Safety | Building Control
Chapter 63 The Contribution of Studio E
Studio E questioned the expertise of expert witness Mr Hyett. | Expert Witness | Evidence | Studio E
Andrew Kuszell accepted Studio E would not have won tender due to lack of significant experience for overcladding high rise residential building. | Procurement | Tender | Andrew Kuszell
Should have been apparent to Mr Kuszell that none of the existing partners or employees had relevant knowledge, experience of skills. | Experience | Tender | Studio E
Studio E should have engaged someone who could bring specific experience of overcladding high rise. | Experience | Tender | Studio E
Studio E was lead consultant and lead designer. | Lead Designer | Consultant | Studio E
Studio E sough to place responsibility on others, maintained that it was for others to ensure that materials chosen for use in the construction of the cladding were suitable and would ensure compliance with the Building Regulations, clearly wrong to do so. | Materials | Selection | Studio E
Studio E had an overriding obligation, initially to the TMO and subsequently to Rydon, to ensure that the work was carried out properly and the choices of materials were suitable. | Materials | Selection | Studio E
Bruce Sounes not familiar with Part B of Schedule 1 to the Building Regulations and Approved Document B. Not take steps in getting acquainted with these. | Building Regulations | Approved Document B | Bruce Sounes
He occasionally referred to Approved Document B2828 but did not read the guidance relating to requirement B4 and did not appear to have any clear understanding of what it entailed. | Building Regulations | Approved Document B | Bruce Sounes
Did not investigate legislative requirements. Ignorance of paragraphs 12.5 to 12.9 of Approved Document B meant that he was unaware of the guidance it contained on the risks arising from the use of certain materials and the ways in which compliance with functional requirement B4(1) could be achieved. | Legislation | Fire Safety | Bruce Sounes
In failing to review Approved Document B and to onsider carefully its significance for the project Mr Sounes fell seriously below the standard to be expected of a reasonably competent architect. | Building Regulations | Approved Document B | Bruce Sounes
Serious errors by Mr Sounes in not recognising materials being combustible. External wall did not comply with functional requirement B4(1). | Materials | Approved Document B | Bruce Sounes
Reasonable competent architect should know 12.5 and 12.7 of Approved Document B contained warning against use of combustible materials in external walls. | Materials | Approved Document B | Bruce Sounes
Leadbitter had warned Studio E against the use of combustible insulation behind rainscreen in Jan 2013. | Materials | Leadbitter | Bruce Sounes
Celotex FR5000 specified by Studio E was a polyisocyanurate material and as such was combustible. | Materials | Fire Safety | Bruce Sounes
Specified Celotex FR5000 for use in the external wall without giving any consideration to whether the resulting structure would comply with functional requirement B4(1). That was a significant failure. | Materials | Approved Document B | Bruce Sounes
U-value disregarded focus on insulation combustibility. | Materials | Fire Safety | Bruce Sounes
Inappropriate for him to treat that as advice from Max Fordham to use FR5000. It was even more inappropriate to accept it uncritically without taking steps to understand the nature of the product and satisfying himself of its suitability. That was a serious error on the part of Mr Sounes. | Materials | Fire Safety | Bruce Sounes
Mr Sounes not take steps that rainscreen panels were consistent with guidance in Approved Document B. | Materials | Cladding | Bruce Sounes
Mr Sounes content in using ACM PE panels. | Materials | Cladding | Bruce Sounes
Mr Sounes not aware that ACM panels could be produced with different cores. | Materials | Cladding | Bruce Sounes
Mr Sounes should have supervised work of Tomas Rek and Adrian Jess. Should have satisfied himself of suitability of materials. | Materials | Supervision | Bruce Sounes
Studio E produced three versions of the NBS Specification, one on 21 Nov 2013, one on 29 Nov 2013 and one on 30 January 2014. Mr Sounes confirmed that no one at Studio E had satisfied themselves before they were drawn up that the materials referred to in any of those versions would ensure compliance with the Building Regulations. That was a fundamental failing on the part of Studio E which had significant consequences. Mr Sounes sought to explain that omission by telling us that Studio E would not usually expect to verify compliance of all materials and products before submitting a full plans application to building control, and that to do so would be wasted work if the contractor subsequently made a change. He also suggested that building control might take a different view of the proposals and that it was not common practice to carry out a full assessment of compliance with the functional requirements of Part B of Schedule 1 at RIBA stages D or E. | Materials | NBS Specification | Bruce Sounes
Under its contract with the TMO, it was Studio E’s responsibility to ensure that the materials included in the NBS Specification complied with the Building Regulations. | Materials | NBS Specification | Bruce Sounes
In failing to satisfy itself that the materials specified would enable the refurbished building to comply with the Building Regulations, Studio E, and particular Mr Sounes, Mr Crawford and Mr Rek, fell seriously below the standard to be expected of persons in their positions. | Materials | NBS Specification | Studio E
We saw no evidence that Mr Sounes had asked any specialist for advice or that he had received any advice that would satisfy a reasonably competent architect that the products specified in the proposed application were suitable for the purpose and would not result in the refurbished building contravening the Building Regulations. | Materials | Building Regulations | Bruce Sounes
Mr Sounes himself did not consider whether the proposed use of Celotex FR5000 above 18 metres met the guidance in Approved Document B or would result in the external wall’s complying with functional requirement B4(1). He did not ask Max Fordham that question nor did he seek any advice from Exova about it. | Materials | Insulation | Bruce Sounes
Mr Sounes not checked suitability of cladding even when industry guidance was available. | Materials | Cladding | Bruce Sounes
Relying on what others have done in the past is not good enough when the practice in question affects people’s safety, is inconsistent with industry guidance and, most importantly, does not withstand rational scrutiny. | Materials | Cladding | Bruce Sounes
Mr Sounes was the lead designer responsible for the project at the time the NBS Specification was compiled. It was therefore his responsibility to ensure that the materials specified in it were consistent with the requirements of the Building Regulations. He failed to do so. He also failed to make it clear to the TMO, Rydon and Harley that Studio E had not taken steps to satisfy itself by reference to testing or other data that the materials included in the specification would result in an external wall that complied with the regulations. He was at fault in not doing so. | Materials | Building Regulations | Bruce Sounes
Studio E failed to devise a proper cavity barrier strategy for the overcladding system, which led to ever-increasing confusion as the project developed. | Cavity Barrier | Building Regulations | Studio E
On the basis of Mr Hyett’s evidence we are satisfied that at tender stage Studio E should have produced drawings showing all vertical and horizontal cavity barriers for all bay and column conditions for all four facade elevations at 1:20 scale and at 1:5 scale for details around the windows where they abutted the columns. We accept his criticism that Studio E should have identified the clash between the brackets and supporting angles and sought to resolve it. | Cavity Barrier | Building Regulations | Studio E
We do not accept that the design of a cavity barrier strategy could be left entirely to Harley as the cladding sub-contractor. It was Studio E’s responsibility to explore and resolve the strategy at tender stage in order that the details subsequently produced by Harley were properly based. | Cavity Barrier | Building Regulations | Studio E
Studio E failed to take a close interest in Exova’s work on the Outline Fire Safety Strategy, which, as we have noted elsewhere, remained materially incomplete in the absence of advice on the fire safety of the proposed overcladding and its effect on functional requirement B4. | Fire Safety | Exova | Studio E
Sounes thought it was the responsibility of the design and build contractor to ensure that the advice was completed, but he failed to warn the TMO or Rydon that Exova’s work had not been finished | Materials | Cladding | Bruce Sounes
Studio E was reassured generally by the fact that Exova had been instructed on the project, even though it did not provide Exova with the full range of information that would have enabled it to provide proper advice and did not question the limited advice that it did receive. | Fire Safety | Exova | Studio E
Casual approach to formulation of contract between Studio E and Rydon, Neil Crawford said it was just the norm. | Contract | Fire Safety | Neil Crawford
Deed covered reasonable care and skill of Studio E. | Contract | Fire Safety | Studio E
Bruce Sounes received a copy of the BBA certificate for the Reynobond ACM panels in April 2014, but failed to read it in full carefully. Neil Crawford unlikely to have read this. | BBA Certificate | Fire Safety | Studio E
We accept Mr Hyett’s opinion that once Studio E had become aware in or around March 2014 of the plan to substitute the Reynobond 55 PE for the zinc rainscreen panel originally specified, it ought to have conducted an urgent investigation into its characteristics in order to satisfy itself that the external wall as a whole would comply with the requirements of the Building Regulations. Studio E as lead designer was responsible for satisfying itself that the product was suitable for use and for obtaining advice from Exova if it was in any doubt. | Cladding | Fire Safety | Studio E
We consider that in failing to do so Studio E fell seriously below the standard of a reasonably competent architect. Mr Sounes appears to have thought that, in relation to a project being carried out under a design and build contract, the architect, having become a consultant engaged by the contractor, had no responsibility for overseeing what others were doing. That was wrong, however, because after its services had been transferred from the TMO to Rydon Studio E remained responsible for ensuring the suitability of the proposed cladding panels. | Materials | Building Regulations | Bruce Sounes
Mr Sounes and Mr Crawford should have read the BBA certificate in full carefully. It was a short document and plainly an important one. Even though by that time Studio E’s services had been transferred to Rydon, it remained under an obligation to exercise reasonable skill, care and diligence in the discharge of its services, which included seeking to ensure that all designs complied with the relevant statutory requirements. We were troubled by Mr Sounes’ practice of not reading the whole of the BBA certificate for any product he was planning to recommend for a project. His failure to do so fell very far below the standard of a reasonably competent architect | BBA Certificate | Fire Safety | Bruce Sounes
Studio E should have checked that Harley’s drawings were consistent with any legislative requirements. | Fire Safety | Harley | Studio E
We think that if Studio E’s work in relation to Harley’s designs was intended to be as narrow in scope as has been suggested, that would have been formally recorded in some way. | Fire Safety | Harley | Studio E
Substituted Celotex RS5000 for the Celotex FR5000 wasn’t checked by Studio E Neil Crawford. | Materials | Insulation | Neil Crawford
Mr Crawford should have realised that RS5000 was not generally suitable for use on buildings over 18 metres in height and should not have been proposed for use in the refurbishment. The failure to investigate the characteristics of RS5000 was another serious failing on Mr Crawford’s part. | Materials | Insulation | Neil Crawford
Mr Crawford also failed to notice that Harley’s specification did not identify the insulation to be used in the construction of the external wall. Despite that omission, Mr Crawford stamped the specification as conforming to design intent when it did not | Fire Safety | Harley | Neil Crawford
Studio E failed to identify from Harley's drawings lack of cavity barriers. | Cavity Barrier | Harley | Studio E
Harley’s construction drawings that were endorsed by Studio E were deeply flawed. | Fire Safety | Harley | Studio E
Studio E’s lack of technical knowledge and experience in respect of cavity barriers is evident from Neil Crawford’s approach to Harley’s request for information in Sept 2014. | Cavity Barrier | Harley | Neil Crawford
Studio E also failed to notice that materials specified by Harley, including Styrofoam in the P1 window infill panel and Kingspan TP10 in the P2 panel, were not suitable for use in their intended applications. Despite that, Mr Crawford accepted the specification without commenting on the choice of those materials. | Window Infill | Harley | Studio E
Studio E's full plans submission to RBKC building control contained drawings that were out of date or inaccurate and was insufficient to demonstrate compliance with the Building Regulations. | Full Plans Application | Building Regulations | Studio E
Studio E’s failure to provide comprehensive and accurate information to building control made it difficult for RBKC to discharge its own functions under the Building Regulations | Full Plans Application | Building Regulations | Studio E
Mr Sounes lack of quality control and training. | Fire Safety | Building Regulations | Bruce Sounes
The technical review was carried out far too late and no senior technically experienced member of staff not otherwise involved in the project had any involvement in checking the designs, in particular for compliance with the Building Regulations. | Fire Safety | Technical Review | Studio E
"As Built" drawings did not accurately record structure of the building, assumed zinc and ACM cladding had been used which wasn’t the case. | Full Plans Application | Building Regulations | Studio E
Chapter 64 The Contribution of Rydon
Rydon was responsible for all aspects of the design and construction of the refurbishment and was obliged to ensure, among other things, that when completed the building complied with the Building Regulations. That obligation existed whether the work was carried out by Rydon itself or by its sub-contractors, consultants or other specialists. | Fire Safety | Building Regulations | Rydon
Under its contract with the TMO Rydon was responsible for all aspects of the design and construction of the refurbishment and was obliged to ensure, among other things, that when completed the building complied with the Building Regulations. That obligation existed whether the work was carried out by Rydon itself or by its sub-contractors, consultants or other specialists. | Fire Safety | Building Regulations | Rydon
Rydon was also the principal contractor under the CDM Regulations 2007 and 2015 | CDM Regulations | Principle Contractor | Rydon
Duty as principal contractor was properly to plan, manage and co-ordinate work during the construction phase in order to ensure that health and safety risks were properly controlled. | CDM Regulations | Principle Contractor | Rydon
Simon Lawrence (contracts manager), Simon O’Connor (project manager) and Zak Maynard (commercial manager) were all acting in those capacities for the first time, inexperienced. | Fire Safety | Experience | All
Although Stephen Blake said that Simon O’Connor’s promotion to project manager had been nominal, in the sense that his role on the project had been effectively that of a site manager, no attempt was made to explain that to him or to ensure that the position of site manager was filled by someone else with suitable experience. | Fire Safety | Experience | All
Stephen Blake accepted that the way in which Mr O’Connor’s qualifications and experience had been described was thoroughly misleading. | Qualifications | Fraud | Simon O’Connor
None of Rydon’s employees had any substantive knowledge of the Building Regulations or of the approved documents that applied to the project. | Fire Safety | Experience | Rydon
Rydon had no, or no effective, system for ensuring that its employees received regular training during their employment. Simon Lawrence had never discussed training with his peers or supervisors and Stephen Blake conceded that he had not undertaken any continuing professional development in the period between leaving university in 1985 and the fire in 2017. Rydon thus failed to take any steps to maintain or improve the competence of its employees or its awareness as a business of matters affecting fire safety. | Fire Safety | Training | Rydon
Rydon should have been aware of all those aspects of the design that required the attention of appropriately qualified professionals so that it could satisfy itself that people with the necessary skill and training had applied their minds to them. | Fire Safety | Qualifications | Rydon
Rydon conceded that in substance it had provided the TMO with nothing more than a management service. In reality, it had organised the work being carried out by a web of sub-contractors and consultants, acting as a channel of communication between the TMO and the various persons contributing to the project in their different capacities. However, it is clear that Rydon failed in number of important respects to perform even its management role properly. It was not appropriate or safe for a contractor undertaking a project on the scale of the Grenfell Tower refurbishment to conduct its business in that manner. | Fire Safety | Experience | Rydon
Although Rydon relied entirely on its sub-contractors and consultants to perform its own contractual obligations to the TMO, it made no serious effort to find out whether the bodies it proposed to engage for that purpose were competent. | Fire Safety | Competence | Rydon
Did not assess work Studio E had already done. | Fire Safety | Studio E | Rydon
Rydon did not ask Harley to examine Studio E's work. | Fire Safety | Harley | Rydon
If Rydon had been aware of Studio E’s lack of experience in overcladding high-rise buildings, it is possible that Rydon would have taken more seriously the need to instruct a fire engineer to assess the safety of the external wall. | Fire Safety | Studio E | Rydon
Included Harley as a sub-contractor on other projects, including the Chalcots Estate and Ferrier Point projects, didn’t check Harley. | Fire Safety | Harley | Rydon
As principal contractor it was Rydon’s responsibility to ensure that sufficient expertise and resources were made available to the project and that the work carried out by external consultants, such as Exova, was satisfactory. In the event, Rydon’s approach to Exova, and to fire engineering generally, was alarmingly complacent. | Fire Safety | Exova | Rydon
Rydon appears to have had no interest in the use of a fire engineer on the Grenfell Tower project. | Fire Safety | Fire Safety Engineer | Rydon
Mr Lawrence had no discussions with the TMO, Studio E or Artelia about the role that Exova might play in the future of the project. He repeated his assurance that he would contact Exova at several subsequent site meetings, but failed to take any action in respect of it. | Fire Safety | Exova | Rydon
We do not think that Rydon gave any genuine consideration to seeking the advice of a fire engineer in respect of the lower four floors, or indeed at all. | Fire Safety | Fire Safety Engineer | Rydon
Rydon should have appreciated that it was ill-equipped to make an informed judgement about the need for fire engineering advice and should therefore have consulted the TMO (its client) and Studio E (its principal designer) before making any decision. | Fire Safety | Principle Contractor | Rydon
To the extent that Rydon investigated the quality of Exova’s work at all, its actions were cursory and superficial. Rydon received Issue 3 of Exova’s Outline Fire Safety Strategy as part of the tender documents and accepted that it contained the fire safety strategy underpinning the design work that had been carried out before its appointment. Nonetheless, it did not ask Studio E whether Exova’s work had been sufficient for its purposes and did not attempt to familiarise itself with the terms on which Exova had been appointed. It does not appear to have occurred to Rydon that the title of the Outline Fire Safety Strategy itself suggested that it might not be in final form. Each of those was a serious failure on the part of Rydon. | Fire Safety | Exova | Rydon
Mr Lawrence assumed that Exova had been involved in the design of the refurbishment from the outset, but did not ask anyone whether that had actually been the case. | Fire Safety | Exova | Simon Lawrence
Simon Lawrence appears to have understood that part of the report to mean that the cladding would have no adverse effect on the fire safety of the tower provided Rydon ensured that it complied with functional requirement B4. | Fire Safety | Cladding | Simon Lawrence
Rydon appears to have thought that any defects in the design or choice of materials would ultimately be identified by building control, but that reflected a fundamental misunderstanding of the role of building control. | Fire Safety | Building Control | Simon Lawrence
Abdicated that responsibility by failing to take an interest in Exova’s work. | Fire Safety | Exova | Rydon
Approach to the involvement of Exova represents a serious failing. It is telling that Simon Lawrence conceded, in hindsight, that the advice of a fire engineer is essential on any construction project with any significant degree of complexity. That Rydon did not realise that at the time indicates the extent of its general lack of concern for fire safety in relation to the project. | Fire Safety | Exova | Simon Lawrence
Rydon’s internal system for evaluating and co-ordinating the design work was inadequate. | Fire Safety | Quality Control | Rydon
No matrix of responsibilities produced. | Fire Safety | Matrix | Rydon
Failed to monitor subcontractors. | Fire Safety | Quality Control | Rydon
No electronic drawing control system. | Fire Safety | Drawings | Rydon
Rydon never turned its mind to the question whether Studio E was actually considering statutory compliance when it reviewed design drawings. By failing to ask those questions Rydon failed to ensure that the design of the cladding was safe, at least as far as fire was concerned. | Fire Safety | Studio E | Rydon
Undue reliance on previous projects e.g. Chalcots. Didn’t learn from previous project fires such as barriers. | Fire Safety | Experience | Rydon
Never appropriate for a principal contractor (or any other party) to rely on building control to ensure that its designs comply with the Building Regulations. | Fire Safety | Building Control | Simon Lawrence
Inappropriate and unsafe for Rydon to rely on building control to the extent that it did because its haphazard communications with building control meant that it could never be confident that it had given building control the information it needed properly to evaluate the design. For example, Rydon approved the substitution of Celotex RS5000 by Kingspan K15 (a product with a different chemical composition) and took no steps to conduct any investigation of its own into the suitability of the product or to ensure that building control and the TMO had been alerted to the change. | Fire Safety | Building Control | Rydon
On 12 November 2014 Claire Williams wrote to Simon Lawrence seeking clarification on the fire retardance of the new cladding and saying that she had just had a “Lakanal moment”. There is no evidence that he or anyone else at Rydon responded in any way to the email. | Cladding | Claire Williams | Simon Lawrence
On 10 April 2015, Ms Williams wrote to Simon O’Connor and asked him for the fire rating of the cladding and fixings and to confirm their acceptance by building control. Although Ms Williams chased for a response, Rydon appears to have taken no action in response to her request. | Cladding | Claire Williams | Simon O’Connor
Rydon failed to ensure that the non-combustible insulation material which had been specified by Studio E in the NBS Specification was used around the windows and instead allowed the use of combustible Celotex and Kingspan insulation products. Rydon also changed the internal window surrounds from plywood to uPVC without seeking the approval of the TMO or considering the fire safety consequences of doing so. The consequences were very serious because the deformation of the uPVC window surrounds in the kitchen of Flat 16 is most likely to have been the means by which fire first entered the cladding on 14 June 2017. | Window | Fire Spread | Rydon
Failures in site supervision. | Fire Safety | Site Supervision | Rydon
Daniel Osgood was brought onto the project between 27 Apr 2015 and 24 Jul 2015 to oversee the installation of the cladding. Although he had previously worked on similar projects as a fitter, he had never worked with ACM panels. He had never received any training in how to inspect cladding installations or in the requirements of the Building Regulations and he did not know that there was statutory guidance on the construction of the external walls of buildings over 18 metres in height. Mr Osgood assumed that all materials installed on the outside of buildings were entirely “fireproof”. He did not know of the need for cavity barriers to be installed around windows and was not aware of the difference between Rockwool (a non-combustible mineral wool insulation product) and Celotex RS5000 (a combustible PIR insulation product). | Materials | Fire Spread | Daniel Osgood
David Hughes had not previously worked on a project that involved fitting cladding to a high-rise building. He did not understand, even in broad terms, the functional requirements of the Building Regulations, was not aware that the external walls of buildings should adequately resist the spread of fire over the surface, was not aware that guidance had been published on the construction of the external walls of buildings over 18 metres in height, was not aware of the expression “limited combustibility” and was not aware that cavity barriers should be fitted around windows. | Fire Safety | Experience | David Hughes
Rydon also exercised little, if any, meaningful control over the materials that were used on site by its sub-contractors, trusting them instead to use only those which were appropriate. | Materials | Fire Spread | Rydon
Both Simon Lawrence’s and Neil Reed’s statements reflect a contemporaneous perception, supported by other evidence before us, that the general quality of Rydon’s work fell significantly below that which could be expected of a reasonably competent design and build contractor. | Materials | Fire Spread | Rydon
Rydon ought to have checked All Group Holding’s work. It is doubtful whether the information provided to the TMO satisfied either regulation 38 or the requirements of the CDM Regulations. | CDM Regulations | Regulation 38 | Rydon
Mr Hoban said that he had asked David Hughes whether Rydon had given the TMO the information required by regulation 38 and that Mr Hughes had told him that the necessary information was being sent to the TMO. We do not understand how Mr Hughes was able to give that assurance. | Fire Safety | Regulation 38 | Rydon
Chapter 65 The Contribution of Harley
Harley appointed for overcladding in July 2014 by Rydon. Did not execute a formal agreement. | Contract | Rydon | Harley
Harley bore bore responsibility for ensuring that the design of the facade complied with all statutory requirements, including the requirements of the Building Regulations. | Fire Safety | Façade | Harley
Harley accepted responsibility to Rydon for the contents of the NBS Specification insofar as they related to the design of the facade. | Fire Safety | NBS Specification | Harley
Harley claimed not understand contract with Rydon but should have done so. | Contract | Rydon | Harley
Harley was aware that it had a responsibility to check that the materials described in the NBS Specification were suitable and to ensure that on the completion of the work the external walls of the tower complied with the Building Regulations, including functional requirement B4(1). | Fire Safety | Materials | Harley
Harley challenged the expert witness Jonathan Sakula. | Fire Safety | Materials | Harley
Standard of Harley’s work fell well below that to be expected of a reasonably competent cladding contractor and it must therefore bear a significant degree of responsibility for the fire. | Fire Safety | Materials | Harley
Many of those failures had the same root cause, namely, the inadequate technical expertise of its employees and representatives. | Fire Safety | Experience | Harley
Ray Bailey considered only to have working knowledge of Approved Document B. | Fire Safety | Experience | Ray Bailey
Daniel Anketell-Jones knowledge of the Building Regulations did not extend beyond matters relating to structural stability, not familiar with Approved Document B. | Fire Safety | Experience | Daniel Anketell-Jones
Ben Bailey not received training with Approved Document B. | Fire Safety | Experience | Ben Bailey
Mark Harris and Mike Albiston admitted not been competent to advise on any question of compliance with Building Regulations or Approved Document B. | Fire Safety | Experience | Harley
Kevin Lamb never undertaken formal training on Building Regulations or the guidance in the approved documents. He didn’t think he needed to be detailed with Approved Document B. | Fire Safety | Building Regulations | Kevin Lamb
Unacceptable that Harley only had passing familiarity with the relevant Building Regulations or approved documents. | Fire Safety | Experience | Harley
Difficult to understand how Harley could reasonably have believed it could discharge its obligations to Rydon without having essential technical knowledge. | Fire Safety | Rydon | Harley
Reasonably competent cladding contractor would have had a system in place for checking the suitability of any products proposed for use on a refurbishment project of that kind. | Fire Safety | Materials | Harley
Harley had no such system, not to have employed anyone capable of managing this. | Fire Safety | Materials | Harley
Ben Bailey lacked the competence and experience to act as Harley's project manager on a project of size and complexity of Grenfell. | Fire Safety | Experience | Ben Bailey
Ben Bailey was 25 year old graduate with a foundation degree in motor sport engineering. Not qualified and no experience. | Fire Safety | Experience | Ben Bailey
Noone at Harley had grasp of fire testing regime. | Fire Safety | Experience | Harley
Ray Bailey Class 0 classification misundertanding. | Fire Safety | Experience | Ray Bailey
Daniel Anketell-Jones ignorance on non combustible, combustible and Class 0. | Fire Safety | Building Regulations | Daniel Anketell-Jones
Mr Lamb claimed to have understood what Class 0 meant, but he said that he had no need to understand the tests that underpinned that classification. | Fire Safety | Experience | Kevin Lamb
If a designer seeks to follow the guidance provided by what has been called the “linear route” in relation to a building over 18 metres in height, paragraph 12.7 requires insulation products to be materials of limited combustibility. Mr Lamb did not understand that distinction. We consider that to be inexcusable in one who was employed to carry out design work. | Fire Safety | Materials | Kevin Lamb
Mr Anketell-Jones was seeking to play down his technical knowledge when giving evidence before us and that he knew more than he was prepared to admit. | Fire Safety | Materials | Daniel Anketell-Jones
Harley had no arrangements for disseminating technical information. | Fire Safety | Experience | Harley
Lack of steps to ensure employees were adequately trained. | Fire Safety | Training | Harley
No evidence that Graham Hackley was involved in being required to train other employees. Ray Bailey was responsible for this. | Fire Safety | Training | Ray Bailey
Ray Bailey not read CWCT Standard for Systemised Building Envelopes. | Fire Safety | Training | Ray Bailey
Ray Bailey nor Mr Anketell-Jones could recall ever having seen Curtins specification. | Fire Safety | Training | Ray Bailey
If gaps of Mr Anketell-Jones existed as he described then he should not have been working on the refurbishment in a design capacity. If they were not, his failure to take action all the more serious. Appears he did know rather more about fire performance than prepared to admit. Difficult to believe he was as ignorant of fire safety matters. | Fire Safety | Materials | Daniel Anketell-Jones
We think Mr Anketell-Jones knew more than he was prepared to admit about the combustibility of ACM PE and technical requirements. | Fire Safety | Materials | Daniel Anketell-Jones
Although Kevin Lamb was certain that he had reviewed the CWCT Standard for Systemised Building Envelopes during his work on the Grenfell Tower project, that had not gone beyond a brief look and he candidly admitted that he had not considered whether his designs complied with it. It was not until March 2015, when a conversation took place between Harley, Exova, Rydon and building control in respect of the fire performance of the cavity barriers, that he had consulted any external guidance. | Fire Safety | Materials | Kevin Lamb
Harley nor Mr Lamb paid attention to relevant documents as would be required by a reasonable competent contractor. | Fire Safety | Materials | Kevin Lamb
Reasonable competent contractor would have been aware of international cladding fires that had taken place. | Fire Safety | Materials | Harley
Harley should have been aware of 12.7 of Approved Document B and of the distinction between Class 0 and limited combustibility. | Fire Safety | Approved Document B | Harley
Significant degree of responsibility for the decision to use Reynobond ACM PE panels on the tower. | Fire Safety | Cladding | Harley
Harley encouraged the use of Reynobond PE 55 in its own interests, among which were maintaining its commercial relationship with Deborah French (Arconic’s UK sales representative). | Fire Safety | Arconic | Harley
Question whether ACM was suitable for use on the tower was never raised by Harley with Studio E (or indeed vice-versa). Both assumed that the product was safe because it had been used on many other buildings, but neither of them took any steps to investigate its fire performance. | Fire Safety | Cladding | Harley
No reasonably competent cladding contractor would have relied simply on the fact that ACM PE had been used on buildings for many years | Fire Safety | Cladding | Harley
Harley’s relationship with Arconic and its consequent ability to offer a significant reduction in the price of Reynobond panels was a factor which helped Rydon secure the contract, and in due course Harley was appointed by Rydon as cladding sub-contractor | Fire Safety | Arconic | Harley
Harley’s involvement thus made a significant contribution to the eventual use of ACM PE on Grenfell Tower. | Fire Safety | Cladding | Harley
Harley knew more than it was willing to admit about the availability of panels with fire-resistant cores and about the dangers posed by panels with unmodified polyethylene cores. Attended presentation and asked Deborah French of Arconic for information about Reynobond ACM panels. | Fire Safety | Arconic | Harley
No excuse for Harley not to have read the NBS specification. | Fire Safety | NBS Specification | Harley
No check on the suitability of the ACM PE panels was subsequently carried out by anyone at Harley. ACM panels were included in the “Specification Notes” produced by Kevin Lamb in early 2015 describing the products that would be used in the construction of the external facade of the tower. | Fire Safety | Cladding | Kevin Lamb
Competent contractor would have examined certificates e.g. BBA (British Board of Agreement). | Fire Safety | BBA Certificate | Harley
Harley should have satisfied itself with use of Celotex RS5000 when to be in place of FR5000. | Fire Safety | Insulation | Harley
Serious failure in ensuring satisfying B4(1) as per Approved Document B. | Fire Safety | Approved Document B | Harley
As a result of the conversations between Jonathan Roome and Ben Bailey in June 2014, Harley was well aware that Celotex did not at that time offer a product that was suitable for use on buildings above 18 metres in height. There was therefore no reasonable basis on which Daniel Anketell-Jones could have thought that the fire performance of RS5000 had been investigated by Studio E during the preparation of the NBS Specification or that it had been “checked through with desktop studies”, not least since RS5000 was not in the NBS Specification. Indeed, it could not have been because it did not exist as a separate brand in November 2013. | Fire Safety | Insulation | Harley
Did not examine sales and technical literature for Celotex RS5000 insulation. | Fire Safety | Insulation | Harley
If read past pink banner then would've seen RS5000 had been classed as suitable for use above 18 metres applied only if the product was incorporated into a cladding system identical to the one that had been tested | Fire Safety | Insulation | Harley
Harley’s Specification Notes of 15 July 2015 did not specify the type of insulation that was to be used. Further, although its drawings included references to insulation, they did not include a description of what product was to be used either. That deprived others who might review the drawings of the ability to identify the products and conduct their own checks. | Fire Safety | Materials | Harley
Kingspan K15 was used as a last-minute substitute for Celotex RS5000 when there was a delay in obtaining supplies of that product. It was used without any proper investigation being made into its suitability for that purpose or into whether its use would result in an external wall that complied with the Building Regulations or was consistent with statutory or industry guidance. | Fire Safety | Insulation | Harley
Ben Bailey did not look into relevant LABC or BBA certificates for Kingspan K15. Placed orders for K15 without telling Rydon or anyone else it was being used. | Fire Safety | Insulation | Harley
Rydon failed to enquire into the suitability of the product or to inform the TMO or building control that it was being used when Harley advised of substituting. | Fire Safety | Materials | Harley
Kevin Lamb sought Kingspan TP10 for window infill panels when not reviewed Approved Document B. Should've checked combustibility. | Fire Safety | Materials | Kevin Lamb
Cavity barriers fabrication drawings of the details around the windows of Grenfell Tower which contained a series of fundamental errors that were identified by Mr Hyett. The structures they described did not comply with the Building Regulations and did not reflect the guidance given in Approved Document B. | Fire Safety | Cavity Barrier | Harley
Kevin Lamb drawings with no comment from Rydon or Studio E about absence of cavity barriers. | Fire Safety | Cavity Barrier | Kevin Lamb
Should have been aware of Taplow House and Chalcots Estate where had cavity barriers. | Fire Safety | Experience | Harley
Ray Bailey was aware of the importance of effective cavity barriers around windows but did not draw attention to the absence of cavity barriers around the windows in Harley’s drawings. There appear to have been no discussions within Harley about what Approved Document B recommended in that respect. | Fire Safety | Cavity Barrier | Ray Bailey
Kevin Lamb noticed that Studio E had failed to include cavity barriers around the windows and told us that he had understood that Approved Document B required them in that location as an important means of ensuring the safety of residents, he nonetheless failed to ask why they were missing or whether the designs complied with regulatory requirements. We do not accept his evidence that it was not his place to raise the matter. He had no reason to think that others at Harley considered that cavity barriers were unnecessary or that anyone at Harley had consulted Studio E. | Fire Safety | Cavity Barrier | Kevin Lamb
No consideration for fire performance of the crown. | Fire Safety | Crown | Harley
Not good with design process such as with supervision and management. | Fire Safety | Management | Harley
Mr Anketell-Jones was not always candid or reliable. He was Design Manager. | Fire Safety | Evidence | Daniel Anketell-Jones
Failed to supervise Mr Lamb's work. Should have supervised its subcontractors. | Fire Safety | Management | Kevin Lamb
Failed with its relationship with Studio E. | Fire Safety | Studio E | Harley
Harley should have taken steps to satisfy itself independently that the form of construction and the materials described in drawings by Studio E would result in a building that complied with the Building Regulations, but it failed to do so. | Fire Safety | Studio E | Harley
Harley should have taken steps to ensure that its own designs complied with any relevant legislation and guidance, regardless of Studio E’s approach to its work. | Fire Safety | Materials | Harley
Kevin Lamb took no steps to familiarise himself with products. | Fire Safety | Materials | Kevin Lamb
Kevin Lamb said that it had never crossed his mind to consider whether there was a British Board of Agrément certificate for Reynobond PE 55 ACM, let alone to look at it. | Fire Safety | BBA Certificate | Kevin Lamb
Management of staff failing extended to that of installer Osborne Berry (engaged to install façade). Ben Bailey lack of inspections of cavity barriers. | Fire Safety | Osborne Berry | Ben Bailey
Not considered combustibility of RS5000, Mr Anketell Jones not probing further and Mr Mort of Siderise Ltd which made cavity barriers alerting to Ben Bailey. | Fire Safety | Insulation | Daniel Anketell-Jones
Chapter 66 The Contribution of the Tenant Management Organisation
As the client for the refurbishment, the TMO failed to take sufficient care in its choice of architect and paid insufficient attention to fire safety matters, including the work of the fire engineer. | Procurement | Studio E | KCTMO
TMO assumed that Studio E had the skills, knowledge, experience and resources to carry out a high-rise residential overcladding project, which was fundamentally different from designing a school or leisure centre. That assumption turned out to be incorrect and led to a series of decisions which had disastrous consequences. No procurement. | Procurement | Studio E | KCTMO
As the client under the CDM Regulations 2007, the TMO had a duty to take reasonable steps to ensure that any designer, principal contractor or contractor it appointed was competent to take on the role in question and had allocated sufficient time and resources to the project. There is no evidence that the TMO was aware of that obligation. | CDM Regulations | Competence | KCTMO
At a meeting of the Lancaster West Estate Management Board on 15 May 2012, at which representatives of the TMO and Studio E were present, Edward Daffarn asked whether Studio E had experience of working on tower blocks and, if not, why it was proposed that it should be appointed as architect for the refurbishment. Although he was told by Cllr Coleridge at some stage that Studio E had been chosen in the interests of financial and practical efficiency, it does not appear that Mr Daffarn ever received an answer to his question from the TMO. It certainly never prompted the TMO to ask that question of itself or anyone else. | CDM Regulations | Studio E | KCTMO
Artelia, as employer’s agent, ought to have made it clear to the TMO that it was in breach of procurement rules by capping the fees of its consultants. Instead, it appears that it simply acquiesced in the TMO’s plan. The unfortunate practical result was that the TMO deprived itself of the opportunity to select an architect from a wider range of applicants, some of whom might have had more relevant experience. | Procurement | Artelia | KCTMO
It does not seem that anyone at the TMO read any of the versions of Exova’s Outline Fire Safety Strategies, in detail or at all, even though they were produced for it as Exova’s client. Both the draft Existing Fire Safety Strategy and the draft Outline Fire Safety Strategy should have been documents of particular interest to the TMO, both as a client which was managing works in a mixed-use occupied residential block and as the responsible person under the Fire Safety Order. | Fire Safety | Exova | KCTMO
David Gibson, Peter Maddison and Claire Williams should all have read Exova’s fire safety strategies carefully. In our view, the draft Outline Fire Safety Strategy was not difficult to understand and they should certainly have noticed that, in relation at least to the external wall, the advice it contained was provisional only. It appears, however, that none of them read it or, if they did, that they did not take proper note of its contents. If they had paid attention to what it said, they would have realised that the strategy was incomplete in relation to functional requirement B4(1) and that it required further work. | Fire Safety | Exova | KCTMO
There were at least two occasions during the life of the project when it was made clear to the TMO that Exova’s work was incomplete. Terence Ashton told Claire Williams on 4 November 2013 (three days before Issue 3 of the Outline Fire Safety Strategy was produced) that after invoicing everything as of that date, there would be a balance remaining from the initial quotation. That should have alerted her to the fact that Exova had not by then done all that it had expected to do under its contract. By Nov 2013, many key design decisions had not been made, including the choice of rainscreen cladding. If anyone at the TMO had turned their minds at that stage to the point, they would have realised that the fire safety strategy had not been completed and that further work had to be done on it. Not to have done so was a serious failing on its part. | Fire Safety | Exova | Claire Williams
The TMO failed to ask why a fire engineer had not been engaged by Rydon after it had been appointed as principal contractor. | Fire Safety | Rydon | KCTMO
The TMO ought to have obtained a clear decision from Rydon and, if Rydon was unwilling to appoint a fire engineer, an explanation for it. Although Artelia, as employer’s agent, should have asked the same questions, the TMO as the employer had a responsibility of its own to monitor the work and ensure that it was being carried out effectively. In that case it failed to do so. | Fire Safety | Rydon | KCTMO
Having raised the fire performance of the cladding with Rydon in her email of 12 November 2014, Claire Williams ought to have insisted on receiving a written response to her question. The matter was too important to be allowed to pass without comment. The fact that it had to be asked at all, in particular at what was a relatively late stage in the project (a year after the NBS Specification had been produced), is a matter of criticism in itself. The fact that an answer was not obtained is difficult to explain, even as an oversight | Fire Safety | Rydon | Claire Williams
Failed to involve residents. | Fire Safety | Residents | KCTMO