## Discharge in Cumecs
IS STANDARD CENTRIFUGAL PUMP DISCHARGE CALCULATION SHEET |  |  | DJ
( Reference: IS 9137 / IS 5120 )
Sl.No | INPUT DATA
1 | Motor Power (HP): | 7.5 |  | INPUT DATA HERE
2 | Motor Power (kW) : (1HP = 0.746 KW) | 5.595 |  | Motor Power IN HP : (i.e 2/5/7.5/10/15/20/40/100 etc) | 7.5 | HP
3 | Overall Efficiency: (Efficiency considered @ 70% typical for centrifugal pumps) | 0.6 |  | Overall Efficiency: (i.e: 60/65/70/75/80/90/100) | 60 | %
4 | Static Head (m): (Suction Level to Delivery Level) | 3.048 |  | Static Head in meters: | 3.048 | Meters
5 | Friction Loss (m): Not Considered | 0 |  | Friction Loss in meters: | 0 | Meters
6 | Total Dynamic Head TDH (m): Sl.No (4+5) | 3.048
7 | Water Density (kg/m3) | 1000
8 | Acceleration due to Gravity (m/s2) | 9.81
CALCULATIONS
9 | Hydraulic Power (kW) Sl.No 2 x 3 | 3.357
10 | Hydraulic Power (W): 1 KW = 1000 Watts | 3357
11 | Discharge Q (m3/s): [Q=Ph/(ρgH)] Q=(P x efficency) /(density x gravity x head) Sl.No 10 / (7 x 8 x 6) | 0.11227
12 | Discharge Q (Cusec): Sl.No 11 x 35.315 | 3.9648
13 | Discharge (L/s): 1 Cum = 1000 Litres | 112.2709
14 | Discharge (L/min): Sl.No 12 x 60 | 6736.2566
15 | Discharge (m3/h): Sl.No 11 x 60 x 60 | 404.1754

## Discharge in Cusecs
HORIZONTAL CENTRIFUGAL PUMPS
H.P. CALUCULATIONS
HP= | (62.45 * Q * H)/(550 * n)
Where Q= | Discharge of each pump in cusecs
H= | Total pumping head in feet
n= | Overall efficiencyof the pump as per table
Efficiency of pump
|  | HP |  |  |  | % ge
|  | 2 | to | 20 |  | 60%
|  | 21 | to | 35 |  | 70%
|  | 36 | to | 75 |  | 75%
|  | 76 | to | 200 |  | 78%
|  | 200 | above |  |  | 80%
Cushioning
|  |  | up to | 2 | HP | 50%
|  | 2 | to | 5 | HP | 30%
|  | 5 | to | 10 | HP | 20%
|  | 10 | to | 20 | HP | 15%
|  | 20 | above |  | HP | 10%
Q= | (HP * 550 * n)/(62.45 * H)
|  | DISCHARGES | [7 empty] | 1cft | 0.028317 | cum | 28.3168 | litres
| HP | 2 | 5 | 7.5 | 10 | 15 | 20 | 40 | 100
Head | 10 | 1.0568 | 2.6421 | 3.9632 | 5.2842 | 7.9263 | 10.5685 | 26.4211 | 70.4564
| 15 | 0.70456 | 1.7614 | 2.6421 | 3.5228 | 5.2842 | 7.0456 | 17.6141 | 46.9709 | 1cusec/day= | 0.0864 | mcft | 2.4466 | Mlitres
| 20 | 0.52842 | 1.3211 | 1.9816 | 2.6421 | 3.9632 | 5.2842 | 13.2106 | 35.2282 |  | 2446552.4565 | litres
Q= | ((HP * 550 * n)/(62.45 * H)/(100%+CUSHION %GE)) |  |  |  |  | WITH CUSHION |  |  |  | 1000 Mlitrre | 35.315 | mcft
|  | DISCHARGES | [8 empty] | 408.7384 | 29.1956 | days
| HP | 2 | 5 | 7.5 | 10 | 15 | 20 | 40 | 100 | daily 40 Mlitre | 1.4126 | mcft
Head | 10 | 0.70456 | 2.0324 | 3.3026 | 4.4035 | 6.8925 | 9.19 | 24.0192 | 64.0512 |  | 16.3495 | 16.3495 | cusecs
| 15 | 0.46971 | 1.3549 | 2.2018 | 2.9357 | 4.595 | 6.1266 | 16.0128 | 42.7008
| 20 | 0.35228 | 1.0162 | 1.6513 | 2.2018 | 3.4462 | 4.595 | 12.0096 | 32.0256