## Introduction
Version 1.1
2025-03-08
This worksheet is intended as an installation aid for ERCES/ERRCS installers. There are no guarantees that this worksheet will solve all BDA issues and is intended as a commissioning aid for basic gain and noise power adjustments.
The Link Budget worksheet calculates free space loss for UL and DL bands and also allows the installer to enter actual rooftop measurements to see the impact of clutter losses in the donor path. The actual rooftop measurement should be made with a calibrated instrument using a spike unity gain antenna.
The BDA Gain Calculator provides a starting point to calculate the minimum amount of gain needed to meet RF signal levels that will provide a reliable DAQ on both UL and DL paths. Further testing may be required to verify DAQ performance.
The BDA Gain Calculator is optimized for 700/800MHz band systems. Other frequency bands may operate differently due to lower indoor RF path losses and therefore BDA design.
The Noise Power Link Budget worksheet provides formulas that will aid installers to assure that BDA installations meet FCC rules of no more than ⎼43dBm of noise power radiated and installations will not raise the noise floor at the donor site.
The RF Calculations worksheet is borrowed from Jack Daniel Co verbatim. This worksheet consists of a plethora of RF formulas, for example, path loss in miles and feet, isolation between antennas, distance between Lat-Lon points, numerical conversions and much more.
The Frequency Bands worksheet provides band plans for the frequency bands most used by prublic safety and industrial radio users. This is useful to know when setting up test equipment to discover desired, and undesired, RF signals.

## Link Budgets
Link Budget Calculator
Downlink Link Budget
Note, this worksheet operates independent from the following worksheets |  |  |  | VHF | 160
Donor Site ERP | 50 | Watts | Enter Effective Radiated Power (ERP) of Donor Site | UHF | 460 | 470
Donor ERP Converted to dBm | 46.9897 | dBm | Converted to dBm
Distance to donor site | 4 | Miles | Enter distance to donor site in miles | 700 Band | 765 | 801
Frequency Band | 700 Band | MHz | Select frequency band | 800 Band | 856 | 811
Calculated Free Space Path Loss | 106.3144 | dB | Based on unobstructed RF path | 106.3144 | 765 | 801
Calculated Power at Donor Antenna | -59.3247 | dBm | Just for reference to compare against actual
Actual Downlink Power Measured | -64 | dBm | Enter actual donor measurement from roof using 0dB spike antenna
Actual Downlink Path Loss | 110.9897 | dB
Actual Path Obstructions | 4.6753 | dBm | This is the additional obstructions to the RF path
Uplink Link Budget
Calculated Free Space Path Loss | 106.7139 | dB | Based on unobstructed UL RF path | 106.7139
Path Obstructions | 4.6753 | dB | Path Obstruction from DL measurement
Calculated UL Path Loss | 111.3891 | dB | Actual UL path loss

## BDA Gain Calculator
BDA Gain Calculator
Donor Path Measurement
This section is to measure total path loss between the donor site and the input of the BDA
Donor Site ERP | 75 | Watts | Enter Effective Radiated Power (EPR) of Donor Site
Donor ERP Converted to dBm | 48.7506 | dBm | Converted to dBm
Channel Power Measured at BDA Donor Port | -68 | dBm | Measure channel power at the end of donor coax where BDA will connect
Total Path Loss Donor Site to BDA Donor Input | 116.7506 | dB | Total Path loss including donor antenna system
Total Number of Channels | 20 |  | Enter total number of channels in radio network
Composite Power Adjustment | 13.0103 | dB | Just for reference to compare against actual
Composite Maximum Input Power | -54.9897 | dBm | If greater than -40dBm consider adding hard attenuation to donor coax
In-Building Path Loss Measurements
This section is to measure indoor path losses between service antenna system and the near and far users
Signal Generator Power Level | 0 | dBm | Enter power level of test signal generator
Near Antenna Power Measurement | -61 | dBm | Enter power measured from 8 ft from strongest antenna
Path Loss to Near User | 61 | dB | If less than 60dB consider adding attenuator to service antenna system*
Far Antenna Power Measurement | -89 | dBm | Enter power measured from location with lowest signal level in building
Path Loss to Far User | 89 | dB
Near-Far Delta | 28 | dB | This is the difference between the near user and the far user **
* Note, indoor antenna systems with less than 20dB of loss between each antenna and the BDA may cause the BDA to engage the macro UL AGC circuit causing a near-far performance issue.
** Note, if greater than 35dB consider upgrading to class A channelized BDA or have designer add more antennas to cover weak areas.
Suggested BDA Gain Adjustments
This section provides starting point for BDA Gain Settings (Based on using the minimum gain required to achieve target signal levels)
Downlink Power Target at Portable Receiver | -100 | dBm | Enter minimum in-building signal level target
Uplink Power Target at Donor Site Receiver | -100 | dBm | Enter minimum uplink power required to donor site receiver
Donor Site Antenna System Gain | 10 | dB | Enter gain of receive antenna system at donor tower site * (See Note Below)
Transmit Power of AHJ Portables | 3 | Watts | Enter typical transmit power of AHJ's portable radios
Portable TX power converted to dBm | 34.7712 | dBm
Near user input power into to BDA mobile port | -26.2288 | dBm
Far user input power into BDA mobile port | -54.2288 | dBm
Recommended BDA Downlink Gain | 57 | dB | Enter this value into BDA as starting DL gain and validate with testing
Recommended BDA Uplink Gain | 60.9794 | dB | Enter this value into BDA as starting UL gain and validate with testing
* Most code officials will not know this, FCC licensee may be able to provide. If not available use 10dB for 700/800 systems, 6dB for UHF and 4dB for VHF. Or use 0dB to calculate power to the face of the donor site antenna.
Class B Near-Far performance
This section shows the amount of gain control applied by the near user in a class B BDA
Calculated near User's BDA output power | 34.7506 | dBm | Not an actual output if exceeding BDA composite Maximum
Maximum composite UL power of BDA | 27 | dBm | Enter the maximum UL composite power rating of the BDA
Amount of BDA AGC attenuation by near user | 7.7506 | dB | Should be less than 10dB to preserve near-far performance
Near User Power Adjustment for Class B BDAs or Class A Without Per Filter Power Sharing
This section applies if AHJ identifies maximum UL power received at donor site
Maximum UL power allowed | -85 | dBm | Enter maximum power allowed at donor site receiver
Maximum BDA UL Power | 27 | dBm | From C52 in above section
BDA UL Composite Power Setting | 21.7506 | dBm | If greater than Max BDA UL Power, no adjustment is necessary
Reduce BDA UL Composite power control to 22dBm

## Noise Power Link Budget
Noise Power Link Budget
Note , Fill in Downlink received power measurement on BDA Gain Calculator worksheet first
Noise Power Compliance Validation
Thermal Noise at 10kHz Bandwidth | -134 | dBm
Actual path loss from BDA Gain Calculator | 116.7506 | dBm | From BDA Gain Calculator Worksheet
Measure BDA Noise Power @ 10kHz bandwidth | -53 | dBm | Noise power as measured using the test setup below using 10kHz RBW
Calculated Noise Power at Donor Site | -169.7506 | dBm | Must be 10 to 15dB below -134dBm to not cause noise rise at donor site
If warning notification is displayed UL gain MUST be reduced until in compliance
Gain of Donor Antenna System (Ant gain - coax loss) | 8 | dB | Enter gain of the donor antenna system, donor antenna gain minus coax loss
Radiated Noise Power | -45 | dBm | MUST be below -43dBm to comply with FCC Rules.
BDA Noise Power Test Setup | Diagram of UL Noise Power (KTB = Thermal background noise floor @ 10kHz BW)

## Frequency Bands
Frequency Bands
Band Name | Downlink MHz | Uplink MHz | Notes
VHF | 150-175 | 150-174 | No define UL DL bands, frequency pairs may be interleaved
UHF | 450-455 | 455-460 | Mixed public safety and industrial
UHF | 460-465 | 465-470 | Mixed public safety and industrial
UHF | 470-473 | 473-476 | Public Safety - Chicago, Cleveland, Los Angeles, Miami, NY, N.E. NJ, Pittsburg, Boston
UHF | 476-479 | 479-482 | Public Safety - Chicago, Cleveland, Detroit, NY, N.E. NJ
UHF | 482-485 | 485-488 | Public Safety - Cleveland, Dallas/Fort Worth, Detroit, San Francisco/Oakland, Boston, Los Angeles, New York
UHF | 488-491 | 491-494 | Public Safety - Houston, San Francisco/Oakland, Washington DC/MD/VA
UHF | 494-497 | 497-500 | Public Safety - Pittsburg, Washington DC/MD/VA
UHF | 500-503 | 503-506 | Public Safety - Philadelphia
UHF | 506-509 | 509-512 | Public Safety - Los Angeles, Philadelphia
Band 14 | 758-768 | 788-798 | Firstnet Band, operated by AT&T
700 | 769-775 | 799-805 | 700 MHz Narrowband, Public Safety/local government only
800 NPSCP | 851-854 | 806-809 | Dedicated for public safety use
800 | 854-861 | 809-816 | Mixed public safety and industrial
Guard Bands for Testing
Lower | Upper | Within BDA Passband* | Notes
757 | 758 | No | Between Band 14 Firstnet and Verizon 700 LTE. Not typically in BDA passband
768 | 769 | Yes | Between Band 14 and narrowband public safety.
775 | 776 | No | Between Band 14 Firstnet and Verizon 700 LTE.
805 | 806 | Yes | Between 700 public safety and 800 public safety uplink bands.
816 | 817 | No | Between 800 public safety and industrial band and Sprint 850 LTE band.
861 | 862 | No | Between 800 public safety and industrial band and Sprint 850 LTE band.
* BDA passbands will vary. Check with BDA manufacturer on passbands.

## RF Calculations
RF Calculator spreadsheet program |  |  |  |  | V 8.7 | 2002-03-10
Complements of Jack Daniel Co
© 2002 Jack Daniel. All Rights Reserved. Do Not Remove this notice.
Notice: No Charge, No Warranty, No Guarantee, No Exceptions!
General Use Section (See Signal Booster section below)
1. Find Free Space (clear line of sight) Path Loss
Enter | 460 | MHz
Enter | 0.25 | miles, Path length
Answer | 77.814 | dB, Path Loss
2. Convert watts to dBm and dBW
Enter | 25 | watt
Answer | 43.9794 | dBm
Answer | 13.9794 | dBW
3. Convert dBm to watts and milliwatts
Enter | -95 | dBm
Answer | 3.1623e-13 | watts
Answer | 3.1623e-10 | milliwatts
4. Convert uV to dBm (50 ohm impedance)
Enter | 10 | uV
Answer | -86.9897 | dBm
5. Convert dBm to uV (50 ohm impedance)
Enter | -60 | dBm
Answer | 223.6068 | uV
6. Convert dBW to uV (50 ohm impedance)
Enter | -120 | dBW
Answer | 7.0711 | uV
7. Convert dBu and Freq. to dBm and uV
Enter | 65.59 | dBu
Enter | 850 | MHz
Answer | -67.9984 | dBm
Answer | 89.0361 | uV
8. Convert dBm and Freq. to Field Strength in dBu and mV/meter (relative to a dipole)
Enter | 850 | MHz
Enter | -70 | dBm
Answer | 63.5884 | dBu (dB above 1 uV/meter)
Answer | 1.5115 | mV/meter
9. Calculate Return Loss and VSWR from Power out and Power reflected
Use the same base (w or mW) in both power level entries
Enter Power Forward |  | 2 | w or mw
Enter Power Reflected |  | 0.5 | w or mw
Return Loss = |  | 6.0206 | dBRL
VSWR = |  | 3 | :1 ratio
10. Calculate Vertical Ant to Ant Isolation (Based on Dipoles)
Enter | 0 | dB: Top antenna gain toward bottom antenna
Enter | 0 | dB: Bottom antenna gain toward top antenna
Enter | 30 | feet (Vertical separation)
Enter | 850 | MHz
Answer | 84.5418 | dB Isolation
11. Calculate Horizontal Ant to Ant Isolation (Based on Dipoles)
Enter | 0 | dB: Left antenna gain toward Right antenna
Enter | 0 | dB: Right antenna gain toward Left antenna
Enter | 100 | feet (Horizontal separation)
Enter | 850 | MHz
Answer | 60.7285 | dB Isolation
12. Calculate distance to horizon (smooth earth)
Enter | 100 | feet, antenna height
Answer | 14.1421 | miles
13. Calculate Radio Horizon, Center of Vertical Beam horizon and
3 dB point beam horizons. Allows Beam Downtilt. FLAT EARTH!
Enter | 100 | feet, Antenna Ht. HAAT
Enter | 10 | degrees; Vertical -3 dB beamwidth
Enter | 4 | degrees; Downtilt below horizon
Answer | 14.1421 | mi.: Radio Horizon
Answer | 0.1195 | mi.: Lower 3 dB beamwidth horizon |  |  |  | 0.1195
Answer | 0.27042 | mi.: Center of beamwidth horizon |  |  |  | 0.27042
Answer | > Horizon | mi.: Upper 3 dB beamwidth horizon |  |  |  | -1.0924
-1.0924
14. Calculate unobstructed signal levels using data from calculations above
Enter | 500 | MHz, center frequency
Enter | 45 | dBm: ERP at antenna |  |  |  |  | 113.5897
Level at | 0.1195 | miles = | -30.1266 | dBm |  |  | 72.1266
Level at | 0.27042 | miles = | -34.2201 | dBm |  |  | 79.2201
Level at | 14.1421 | miles = | -71.5897 | dBm, worse case |  |  | 113.5897
15. Convert Degree-Minute.decimal coordinate format to other formats
(Note: If you enter an incorrect value you will get an incorrect answer)
| Degrees | Minutes | Seconds
Enter | 30 | 30.25 | (dna) |  | D/M
Answer | 30 | 30 | 15 |  | D/M/S
Answer | 30.5042 | (dna) | (dna) |  | D
16. Convert Degree-Minute-Second coordinate format to other formats
| Degrees | Minutes | Seconds
Enter | 30 | 30 | 15 |  | D/M/S
Answer | 30 | 30.25 | (dna) |  | D/M
Answer | 30.5042 | (dna) | (dna) |  | D
17. Convert Degree.decimal coordinate format to other formats
| Degrees | Minutes | Seconds
Enter | 30.5504 | (dna) | (dna) | D |  | 0.55042
Answer | 30 | 33 | 1.5001 | D/M/S |  | 0.025002
Answer | 30 | 33.025 | (dna) | D/M
18. Distance between coordinates: FCC distance method: Valid up to ~250 miles
(DD = Degrees, MM = Minutes, SS = Seconds)
Enter |  | Latitude |  | 34.5 |  | Longitude
Coord.s: | DD | MM | SS | 116.5 | DDD | MM | SS
Site A | 34 | 30 | 0 | 33.75 | 116 | 30 | 0
Site B | 33 | 45 | 0 | 116.7583 | 116 | 45 | 30
Answer | 53.7717 | miles between Site A and Site B.
Answer | 195.9853 | degrees; Site A to Site B | [5 empty] | 0.59559
Answer | 15.9853 | degrees; Site B to Site A | [5 empty] | 68.9233
57.3222
Signal Booster Calculation Section | [7 empty] | 51.6924
14.8082
A. Calculate Free Space Loss for distances in feet. | [7 empty] | 195.9853
NOT ACCURATE LESS THAN 20 FEET or 10 Wavelengths!
Enter | 160 | MHz | [5 empty] | 15.9853
Enter | 10 | Feet
Answer | 26.2297 | dB
B. Calculate Composite Power of multiple carriers.
(Enter -200 dBm for unused carrier entry)
(For more than 4, Calculate 4 then use the answer as #1 input then enter others)
Enter Carrier 1 level |  | -67 | dBm | 1.9953e-10
Enter Carrier 2 level |  | -67 | dBm | 1.9953e-10
Enter Carrier 3 level |  | -67 | dBm | 1.9953e-10
Enter Carrier 4 level |  | -57 | dBm | 1.9953e-09
Enter Carrier 5 level |  | -200 | dBm | 1e-23
Enter Carrier 6 level |  | -200 | dBm | 1e-23
Enter Carrier 7 level |  | -200 | dBm | 1e-23
Enter Carrier 8 level |  | -200 | dBm | 1e-23
Enter Carrier 9 level |  | -200 | dBm | 1e-23
Composite Power Level |  | -55.8606 | dBm | 2.5938e-09
C. Calculate Amplifier Input/Output Noise levels using N.F. , BW and 3rd OIP
Enter Noise Figure |  |  | 6 | dB
Enter BW in MHz |  |  | 0.03 | MHz
Enter Amplifier gain |  |  | 80 | dB
Enter 3rd OIP |  |  | 2 | dBm
Input Noise "floor" = |  |  | -123.2288 | dBm
Output Noise for Entered BW = |  |  | -43.2288 | dBm
Output Noise: 25 KHz window = |  |  | -44.0206 | dBm
Output Noise:12.5 KHz window = |  |  | -47.0309 | dBm
D. Calculate 3rd order IM product in Class A RF Amps:
Enter Amplifier Gain |  |  | 15 | dB
Enter 3rd Order Output IP |  |  | 26 | dBm
Enter carrier input level |  |  | -40 | dBm
Approx. 1 dB compression level |  |  | 16 | dBm (at output)
Carrier output level |  |  | -25 | dBm
3rd IM output level |  |  | -127 | dBm
3rd IM to carrier difference |  |  | -102 | dB
E. Calculate 2nd & 3rd Order IM using 3rd OIP and Output level
Enter 3rd OIP (Output Intercept Point) |  |  | 44 | dBm
Enter Output Level |  |  | 10 | dBm
2nd Order IM below Output |  |  | -24 | dBm
2nd Order IM Output Level |  |  | -14 | dB
3rd Order IM below Output |  |  | -58 | dBm
3rd Order IM Output level |  |  | -48 | dB
F. Calculate maximum Output power per carrier for multiple carriers.
Note: Uses EIA PN2009 method: Based on equal input levels for all carriers AND
IM's attenuated by at least 43 + 10 log(output power per carrier )
Enter 3rd Order Output IP |  |  | 45 | dBm
Enter Number of input carriers |  |  | 2 | carriers (minimum = 2)
Output power per carrier |  |  | 25.3925 | dBm
Output power per carrier |  |  | 346.1374 | milliwatts
Metric Conversions (For FCC forms, etc.)
Convert Inches to Centimeters and meters
Enter | 6 | inches
Answer | 15.24 | cm
Answer | 0.1524 | meters
Convert Feet to Meters/Kilometers
Enter | 6 | feet
Answer | 1.8288 | meters
Answer | 0.0018288 | kilometers
Convert Miles to Meters and Kilometers
Enter | 6 | miles
Answer | 9655.8 | meters
Answer | 9.6558 | kilometers
Convert Meters to inches, feet, yards and miles
Enter | 6 | meters
Answer | 236.232 | inches
Answer | 19.686 | feet
Answer | 6.562 | yards (feet/3)
Answer | 0.0037284 | miles
Note on F112: Mike Brownson: Formaulas hidden here
Note on J115: Mike Brownson: Formula hidden here