2021 Consumer Confidence Report

Pillsbury Lake/Franklin Pierce

PWS ID# 2462040

Introduction

Like any responsible public water system, our mission is to help our NH communities maintain public health through drinking water supply. We do this by tailoring and carrying out preventative maintenance checks and services to the individual water system to ensure a strong and reliable water supply system. We adhere to the EPA and NH DES regulations and master sampling schedule to continuously monitor water quality and ensure the water being delivered to your home is safe for consumption.

Aging infrastructure presents challenges to drinking water safety, and continuous improvement is needed to maintain the quality of life we desire for today and for the future.

In the past year, we have begun/completed, valve isolation, repaired the valve connection from Franklin Pierce to the Peninsula system so it may be used to transfer water, leak detections and repairs, rebedding of the arsenic treatment tank, modification and disconnection to the Rumford Dr section and completed a pressure test to the lines running under the lake.

In the coming year we intend to maintain all systems on a regular basic to help keep the quality of the water to the residents safe.

These investments along with on-going operation and maintenance costs are vital to the systems integrity and ability to delivery clean, safe and reliable water to your homes.

When considering the high value we place on water, it is truly a bargain to have water service that protects public health, fights fires, supports businesses and the economy, and provides us with the high-quality of life we enjoy.

What is a Consumer Confidence Report?

The Consumer Confidence Report (CCR) details the quality of your drinking water, where it comes from, and where you can get more information. This annual report documents all detected primary and secondary drinking water parameters, and compares them to their respective standards known as Maximum Contaminant Levels (MCLs).

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

Inorganic contaminants, such as salts and metals, which can be naturally occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining or farming.

Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

Organic chemical contaminants, including per- and polyfluoroalkyl substances, synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban storm water runoff, and septic systems.

Radioactive contaminants, which can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, EPA prescribe regulations which limit the amount of certain contaminants in water provided by public water systems. The US Food and Drug Administration (FDA) regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

What is the source of my drinking water?

Franklin Pierce system draws its water from 3 bedrock wells (BRW).

BRW 4

BRW 7

BRW 8

Atmospheric Storage Tank

In addition, due to source having trouble keeping up with the demand, finding and repairing leaks we had to purchase bulk water on the below dates

07/01/2020

07/07/2020

07/26/2020

11/06/2020

Why are contaminants in my water? Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline at 1-800-426-4791.

Do I need to take special precautions? Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline at 1-800-426-4791.

Source Water Assessment Summary

NHDES prepared drinking water source assessment reports for all public water systems between 2000 and 2003 in an effort to assess the vulnerability of each of the state’s public water supply sources. Included in the report is a map of each source water protection area, a list of potential and known contamination sources, and a summary of available protection options.  The results of the assessment, prepared on 09/28/2001 are found at: http://www.des.nh.gov/site/g/files/ehbemt341/files/documents/webster.pdf

Note:  This information is over 19 years old and includes information that was current at the time the report was completed.  Therefore, some of the ratings might be different if updated to reflect current information.  At the present time, DES has no plans to update this data.

How can I get involved?

For more information about your drinking water, please call Brandon Doherty at pillsburylakevillagedistrict@gmail.com , Ali Vasquez at plvd.vasquez@gmail.com or info@aquamenwatersolutions.com .Although we do not have specific dates for public participation events or meetings, feel free to contact us with any questions you may have.

Definitions:

Ambient Groundwater Quality Standard or AGQS: The maximum concentration levels for contaminants in groundwater that are established under RSA 485-C, the Groundwater Protection Act.

Action Level or AL: The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

Level I Assessment: A study of the water system to identify potential problems and determine, if possible, why total coliform bacteria have been found in our water system.

Level II Assessment: A very detailed study of the water system to identify potential problems and determine, if possible, why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.

Maximum Contaminant Level or MCL: The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal or MCLG: The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

Maximum Residual Disinfectant Level or MRDL: The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

Maximum Residual Disinfectant Level Goal or MRDLG: The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

Treatment Technique or TT: A required process intended to reduce the level of a contaminant in drinking water.

Abbreviations

BDL: Below Detection Limit

mg/L: milligrams per Liter

NA: Not Applicable

ND: Not Detectable at testing limits

NTU: Nephelometric Turbidity Unit

pCi/L: picoCurie per Liter

ppb: parts per billion

ppm: parts per million

RAA: Running Annual Average

TTHM: Total Trihalomethanes

UCMR: Unregulated Contaminant Monitoring Rule

ug/L: micrograms per Liter

The following statement must be included.

Drinking Water Contaminants:

Lead: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.  This water system is responsible for high quality drinking water, but can not control the variety of materials used in your plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing cold water from your tap for at least 30 seconds before using water for drinking or cooking.  Do not use hot water for drinking and cooking.  If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at http://water.epa.gov/drink/info/lead/index.cfm

System Name: ____Pillsbury Lake/Franklin Pierce_______  PWS ID: _2462040___

2021 Report (2020 data)

| Bulk Water Deliveries |  |  |  |
| --- | --- | --- | --- |
| Bulk Water Source | Dates of Water Delivery | Gallons Delivered | Reason for Delivery |
| 1471010, 1121010 | 07/01/2020 | 12,000 gallons | Source having trouble keeping up with demand |
| 1181020 | 07/07/2020 | 6,000 gallons | Found and repaired a leak in distribution |
| 1181020 | 07/26/2020 | 12,000 gallons | Source having trouble keeping up with demand |
| 1471010 | 11/06/2020 | 6,000 gallons | Source having trouble keeping up with demand, leak detection was completed |

*The value must be reported as whole number, see Env-Dw 811, Appendix B for conversions:

LEAD AND COPPER

| - Contaminant (Units) | Action Level | 90th percentile sample value * | Date | # of sites above AL | Violation Yes/No | Likely Source of Contamination | Health Effects of Contaminant |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - Copper (ppm) | 1.3 | 0.159 | 09/10/20 |  | no | - Corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives | Copper is an essential nutrient, but some people who drink water containing copper in excess of the action level over a relatively short amount of time could experience gastrointestinal distress. Some people who drink water containing copper in excess of the action level over many years could suffer liver or kidney damage. People with Wilson’s Disease should consult their personal doctor. |
| - Lead - (ppb) | 15 | - 2ppb | - 09/10/20 |  | - no | - Corrosion of household plumbing systems, erosion of natural deposits | (15 ppb in more than 5%) Infants and young children are typically more vulnerable to lead in drinking water than the general population. It is possible that lead levels at your home may be higher than at other homes in the community as a result of materials used in your home’s plumbing. If you are concerned about elevated lead levels in your home’s water, you may wish to have your water tested and flush your tap for 30 seconds to 2 minutes before using tap water. Additional information is available from the Safe Drinking Water Hotline (800-426-4791). (above 15 ppb) Infants and children who drink water containing lead in excess of the action level could experience delays in their physical or mental development. Children could show slight deficits in attention span and learning abilities. Adults who drink this water over many years could develop kidney problems or high blood pressure. |

| - Radioactive Contaminants |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Compliance Gross Alpha (pCi/L) | 0.8 02/11/20 0.1 04/02/20 0 08/20/20 2.4 08/20/20 0 10/15/20 | 15 | 0 | no | Erosion of natural deposits | Certain minerals are radioactive and may emit a form of radiation know as alpha radiation. Some people who drink water containing alpha emitters in excess of the MCL over many years may have an increased risk of getting cancer. |
| Uranium (ug/L) | 5.5 02/11/20 2.6 04/02/20 2 08/20/20 0 08/20/20 2.5 10/15/20 | 30 | 0 | no | Erosion of natural deposits | Some people who drink water containing uranium in excess of the MCL over many years may have an increased risk of getting cancer and kidney toxicity. |
| Combined Radium 226 + 228 (pCi/L) | 1.1 02/11/2020 2 04/02/2020 0 08/20/2020 0 08/20/2020 2.6 10/15/2020 | 5 | 0 | no | Erosion of natural deposits | Some people who drink water containing radium 226 or 228 in excess of the MCL over many years may have an increased risk of getting cancer. |
| - Inorganic Contaminants |  |  |  |  |  |  |
| Arsenic (ppb) | 7.2 02/10/20 3.3 04/02/20 11 06/08/20 4 08/17/20 4 08/17/20 5 10/15/20 3 10/15/20 | 10 | 0 | no | Erosion of natural deposits; runoff from orchards; runoff from glass and electronics production wastes | (5 ppb through 10 ppb) While your drinking water meets EPA’s standard for arsenic, it does contain low levels of arsenic. EPA’s standard balances the current understanding of arsenic’s possible health effects against the costs of removing arsenic from drinking water. EPA continues to research the health effects of low levels of arsenic, which is a mineral known to cause cancer in humans at high concentrations and is linked to other health effects such as skin damage and circulatory problems. (above 10 ppb) Some people who drink water containing arsenic in excess of the MCL over many years could experience skin damage or problems with their circulatory system, and may have an increased risk of getting cancer. |
| Fluoride (ppm) | .18 04/02/20 .18 04/02/20 0.3 06/08/20 0.3 06/08/20 | 4 | 4 | no | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories | Some people who drink water containing fluoride in excess of the MCL over many years could get bone disease, including pain and tenderness of the bones. Fluoride in drinking water at half the MCL or more may cause mottling of children’s teeth, usually in children less than nine years old. Mottling also known as dental fluorosis, may include brown staining and/or pitting of the teeth, and occurs only in developing teeth before they erupt from the gums. |
| - Synthetic Organic Contaminants including Pesticides and Herbicides |  |  |  |  |  |  |

*If applicable report average and range and date sampled if prior to the reporting year. Level detected must be reported as whole number, see Env-Dw 811, Appendix B for conversions:

| SECONDARY CONTAMINANTS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Secondary MCLs (SMCL) | Level Detected | Date | Treatment technique (if any) | AL (Action Level), SMCL or AGQS (Ambient groundwater quality standard) | Specific contaminant criteria and reason for monitoring |
| Chloride (ppm) | 3.1 | 4/2/20 | N/A | 250 | Wastewater, road salt, water softeners, corrosion |
| Fluoride (ppm) |  |  | N/A | 2 | Add Health effects language from Env-Dw 806.11 or attach public notice to CCR |
| Iron (ppm) | 0.088 0.12 | 4/2/20 6/8/20 | N/A | 0.3 | Geological |
| Manganese (ppm) |  |  | N/A | 0.05 | Geological |
| Nickel | 0.008 | 6/8/20 | N/A | N/A | Geological; electroplating, battery production,ceramics |
| PH (ppm) | 7.61 7.76 | 4/2/20 6/8/20 | N/A | 6.5-8.5 | Precipitation and geology |
| Sodium (ppm) | 4.2 4.9 | 4/2/20 6/8/20 | N/A | 100-250 | We are required to regularly sample for sodium |
| Sulfate (ppm) | 6.5 7.8 | 4/2/20 6/8/20 | N/A | 250 | Naturally occurring |
| Zinc (ppm) | 0.64 0.602 | 4/2/20 6/8/20 | N/A | 5 | Galvanized pipes |