## Sheet1
DATE REVISED: TyA - OCT 2024 - MPNSW
R-32 SMALL PACK ROOFTOP UNITS (RTU) - SINGLE PHASE
STANDARD EFFICIENCY - SINGLE STAGE COOLING
TAG | DAIKIN MODEL | TONS | CFM | ESP | COOLING | [5 empty] | EFFICIENCY |  | HEATING (BTU) | [5 empty] | DIMENSIONS (IN) |  |  | WEIGHT | ELECTRICAL |  |  |  | NOTES
|  |  | (AT ELEV.) | (IN WG) | EAT | EAT | LAT | LAT | TOTAL COOLING | SENSIBLE COOLING |  |  | LOW HEAT OPTION |  | MEDIUM HEAT OPTION |  | HIGH HEAT OPTION |  |  |  |  | (LBS) | 208-230/1/60
[5 empty] | (DB) | (WB) | (DB) | (WB) | (BTUH) | (BTUH) | SEER2 | EER2 | INPUT | OUTPUT | INPUT | OUTPUT | INPUT | OUTPUT | H | W | L |  | MCA |  | MOP
RTU-3 | DSG0361D | 3 | 1217 | 0.5 | 80 | 62 | 54.8 | 50.6 | 33480 | 28952 | 14 | 12 | 45000 | 36450 | 60000 | 48600 | 90000 | 72900 | 39-⅞ | 48-⅜ | 74 | 635 | 27.2 |  | 40 |  | 1,2,3,4,6,7,8,9,10,12
RTU-4 | DSG0481D | 4 | 1602 | 0.5 | 80 | 62 | 53.8 | 50.4 | 43820 | 39575 | 13.7 | 11.8 | 90000 | 72900 | N/A | N/A | 115000 | 93150 | 39-⅞ | 48-⅜ | 74 | 669 | 33.1 |  | 50 |  | 1,2,3,4,6,7,8,9,10,12
RTU-5 | DSG0601D | 5 | 2031 | 0.5 | 80 | 62 | 54.7 | 50.4 | 55210 | 48600 | 13.7 | 11.8 | 90000 | 72900 | N/A | N/A | 140000 | 113400 | 39-⅞ | 48-⅜ | 74 | 668 | 38.7 |  | 60 |  | 1,2,3,4,5,6,7,8,9,10,12
HIGH EFFICIENCY - TWO STAGE COOLING
TAG | DAIKIN MODEL | TONS | CFM | ESP | COOLING | [5 empty] | EFFICIENCY |  | HEATING (BTU) | [5 empty] | DIMENSIONS (IN) |  |  | WEIGHT | ELECTRICAL |  |  |  | NOTES
|  |  | (AT ELEV.) | (IN WG) | EAT | EAT | LAT | LAT | TOTAL COOLING | SENSIBLE COOLING |  |  | LOW HEAT OPTION |  | MEDIUM HEAT OPTION |  | HIGH HEAT OPTION |  |  |  |  | (LBS) | 208-230/1/60
[5 empty] | (DB) | (WB) | (DB) | (WB) | (BTUH) | (BTUH) | SEER2 | EER2 | INPUT | OUTPUT | INPUT | OUTPUT | INPUT | OUTPUT | H | W | L |  | MCA |  | MOP
RTU-3 | DHG0361D | 3 | 1221 | 0.5 | 80 | 62 | 51.4 | 50.2 | 33020 | 33020 | 16.6 | 12.5 | 45000 | 36450 | 70000 | 56700 | 115000 | 93150 | 39-⅞ | 48-⅜ | 74 | 688 | 24.8 |  | 35 |  | 1,2,3,4,6,7,8,9,10,11
RTU-4 | DHG0481D | 4 | 1628 | 0.5 | 80 | 62 | 51.6 | 50.4 | 43590 | 43590 | 16.4 | 12.2 | 70000 | 56700 | 115000 | 93150 | 140000 | 113400 | 43-½ | 48-⅜ | 74 | 763 | 36.9 |  | 60 |  | 1,2,3,4,6,7,8,9,10,11
RTU-5 | DHG0601D | 5 | 1956 | 0.5 | 80 | 62 | 55.2 | 50.1 | 55780 | 45700 | 16.2 | 12.2 | 70000 | 56700 | 115000 | 93150 | 140000 | 113400 | 43-½ | 48-⅜ | 74 | 771 | 43.3 |  | 70 |  | 1,2,3,4,5,6,7,8,9,10,11
R-32 PACKAGED ROOFTOP UNITS (RTU) - THREE PHASE
STANDARD EFFICIENCY
TAG | DAIKIN MODEL | TONS | CFM | ESP | COOLING | [5 empty] | EFFICIENCY |  | HEATING (BTU) | [5 empty] | DIMENSIONS (IN) |  |  | WEIGHT | ELECTRICAL |  |  |  | NOTES
|  |  | (AT ELEV.) | (IN WG) | EAT | EAT | LAT | LAT | TOTAL COOLING | SENSIBLE COOLING |  |  | LOW HEAT OPTION |  | MEDIUM HEAT OPTION |  | HIGH HEAT OPTION |  |  |  |  | (LBS) | 208-230/3/60 |  | 460/3/60
[5 empty] | (DB) | (WB) | (DB) | (WB) | (BTUH) | (BTUH) | IEER | EER | INPUT | OUTPUT | INPUT | OUTPUT | INPUT | OUTPUT | H | W | L |  | MCA | MOP | MCA | MOP
RTU-3 | DSG0363W | 3 | 1315 | 0.75 | 80 | 62 | 55.7 | 51.5 | 33734 | 30146 | 14* | 12* | 45000 | 36450 | 70000 | 56700 | 90000 | 72900 | 39-⅞ | 74 | 48-⅜ | 633 | 21.4 | 30 | 10 | 15 | 1,2,3,4,6,7,8,9,10,12
RTU-4 | DSG0483W | 4 | 1722 | 0.75 | 80 | 62 | 54.3 | 51.5 | 44115 | 41904 | 13.7* | 11.8* | 70000 | 56700 | 90000 | 72900 | 115000 | 93150 | 39-⅞ | 74 | 48-⅜ | 664 | 24.4 | 35 | 11.5 | 15 | 1,2,3,4,6,7,8,9,10,12
RTU-5 | DSG0603W | 5 | 2014 | 0.75 | 80 | 62 | 54.6 | 50.7 | 55163 | 48387 | 13.7* | 11.8* | 90000 | 72900 | 115000 | 93150 | 140000 | 113400 | 39-⅞ | 74 | 48-⅜ | 664 | 31.1 | 45 | 15.9 | 20 | 1,2,3,4,5,6,7,8,9,10,12
RTU-6 | DSG0723W | 6 | 2538 | 0.75 | 80 | 62 | 54.7 | 51.1 | 67094 | 60720 | 16.7 | 11.8 | 90000 | 72900 | 115000 | 93150 | 140000 | 113400 | 43-½ | 74 | 48-⅜ | 757 | 32.1 | 45 | 15.1 | 20 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-7.5 | DSG0903L | 7.5 | 3078 | 1 | 80 | 62 | 50.5 | 50.5 | 85843 | 85843 | 16 | 12 | 130000 | 105300 | 180000 | 145800 | 225000 | 182250 | 54-⅝ | 93-¾ | 60-⅜ | 1269 | 42.7 | 50 | 21.3 | 25 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-8.5 | DSG1023L | 8.5 | 3455 | 1 | 80 | 62 | 51.6 | 50.9 | 92975 | 92974 | 15.5 | 11.4 | 130000 | 105300 | 180000 | 145800 | 225000 | 182250 | 54-⅝ | 93-¾ | 60-⅜ | 1281 | 49.9 | 60 | 24.5 | 30 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-10 | DSG1203L | 10 | 4041 | 1 | 80 | 62 | 50.6 | 50.5 | 112558 | 112558 | 15.2 | 11.4 | 130000 | 105300 | 180000 | 145800 | 240000 | 194400 | 54-⅝ | 93-¾ | 60-⅜ | 13242 | 60.7 | 70 | 30.8 | 40 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-12.5 | DSG1503L | 12.5 | 5060 | 1 | 80 | 62 | 51.6 | 50.9 | 135999 | 135999 | 15.2 | 11.4 | 130000 | 105300 | 180000 | 145800 | 240000 | 194400 | 54-⅝ | 93-¾ | 60-⅜ | 1407 | 66 | 80 | 34.8 | 45 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-15 | DSG1803W | 15 | 6010 | 1.5 | 80 | 62 | 53.8 | 50.5 | 166987 | 149063 | 14 | 10.8 | 260000 | 210600 | 360000 | 291600 | 400000 | 324000 | 51 | 133-⅞ | 88-½ | 2242 | 91.3 | 110 | 48.2 | 50 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-20 | DSG2403W | 20 | 8428 | 1.5 | 80 | 62 | 53 | 50.9 | 226651 | 215361 | 14 | 10.8 | 260000 | 210600 | 360000 | 291600 | 400000 | 324000 | 51 | 133-⅞ | 88-½ | 2506 | 106 | 125 | 57.6 | 70 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-25 | DSG3003W | 25 | 10267 | 1.5 | 80 | 62 | 54 | 50.5 | 284589 | 251965 | 13 | 9.8 | 260000 | 210600 | 360000 | 291600 | 400000 | 324000 | 51 | 133-⅞ | 88-½ | 2647 | 151 | 175 | 74.3 | 90 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
HIGH EFFICIENCY - TWO STAGE COOLING
TAG | DAIKIN MODEL | TONS | CFM | ESP | COOLING | [5 empty] | EFFICIENCY |  | HEATING (BTU) | [5 empty] | DIMENSIONS (IN) |  |  | WEIGHT | ELECTRICAL |  |  |  | NOTES
|  |  | (AT ELEV.) | (IN WG) | EAT | EAT | LAT | LAT | TOTAL COOLING | SENSIBLE COOLING |  |  | LOW HEAT OPTION |  | MEDIUM HEAT OPTION |  | HIGH HEAT OPTION |  |  |  |  | (LBS) | 208-230/3/60 |  | 460/3/60
[5 empty] | (DB) | (WB) | (DB) | (WB) | (BTUH) | (BTUH) | IEER | EER | INPUT | OUTPUT | INPUT | OUTPUT | INPUT | OUTPUT | H | W | L |  | MCA | MOP | MCA | MOP
RTU-3 | DHG0363 | 3 | 1353 | 0.75 | 80 | 62 | 54.2 | 52 | 33024 | 33023 | 16.6* | 12.5* | 45000 | 36450 | 70000 | 56700 | 115000 | 93150 | 39-⅞ | 74 | 48-⅜ | 688 | 17.4 | 25 | 8.2 | 15 | 1,2,3,4,6,7,8,9,10,11
RTU-4 | DHG0483 | 4 | 1739 | 0.75 | 80 | 62 | 53.5 | 51.8 | 43590 | 43590 | 16.4* | 12.2* | 70000 | 56700 | 115000 | 93150 | 140000 | 113400 | 43-½ | 74 | 48-⅜ | 763 | 20.9 | 30 | 10.7 | 15 | 1,2,3,4,6,7,8,9,10,11
RTU-5 | DHG0603 | 5 | 1956 | 0.75 | 80 | 62 | 55.2 | 50.1 | 55783 | 45702 | 16.2* | 12.2* | 70000 | 56700 | 115000 | 93150 | 140000 | 113400 | 43-½ | 74 | 48-⅜ | 771 | 28.5 | 40 | 13.3 | 20 | 1,2,3,4,5,6,7,8,9,10,11
RTU-6 | DHG0723 | 6 | 2523 | 0.75 | 80 | 62 | 52.1 | 51.1 | 66593 | 66592 | 18.6 | 12.5 | 70000 | 56700 | 125000 | 101250 | 150000 | 121500 | 53-¾ | 74 | 48-⅜ | 832 | 29.3 | 45 | 15.1 | 20 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-7.5 | DHG0903 | 7.5 | 3201 | 1 | 80 | 62 | 51.5 | 50.9 | 86186 | 86186 | 17.5 | 12.5 | 130000 | 105300 | 180000 | 145800 | 225000 | 182250 | 54-⅝ | 93-¾ | 60-⅜ | 1415 | 42.7 | 50 | 21.3 | 25 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-8.5 | DHG1023 | 8.5 | 3608 | 1 | 80 | 62 | 51 | 50.7 | 98946 | 98946 | 17.5 | 12.5 | 130000 | 105300 | 180000 | 145800 | 225000 | 182250 | 54-⅝ | 93-¾ | 60-⅜ | 1431 | 49.9 | 60 | 24.5 | 30 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-10 | DHG1203 | 10 | 4098 | 1 | 80 | 62 | 55.3 | 50.7 | 112231 | 95579 | 17 | 12.5 | 130000 | 105300 | 180000 | 145800 | 240000 | 194400 | 54-⅝ | 93-¾ | 60-⅜ | 1448 | 52.8 | 60 | 27.4 | 35 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
RTU-12.5 | DHG1503 | 12.5 | 4064 | 1 | 80 | 62 | 45.6 | 48.3 | 132146 | 132146 | 16 | 12 | 130000 | 105300 | 180000 | 145800 | 240000 | 194400 | 58-⅞ | 93-¾ | 60-⅜ | 1473 | 64.4 | 80 | 31.8 | 40 | 1,2,3,4,5,6,7,8,9,10,11,13,14,15
*3, 4 and 5-ton units are rated in SEER2/EER2. 6-ton and above are rated in IEER/EER.
Notes: | [10 empty] | Factory Installed Options | [6 empty] | Field Installed Options
1 | PROVIDE FACTORY INSTALLED ELECTRO-MECHANICAL CONTROLS
2 | PROVIDE FACTORY INSTALLED HINGED PANELS | [9 empty] | Economizer/Damper | [6 empty] | Economizer/Damper
3 | PROVIDE FIELD INSTALLED ULTRA LOW-LEAK DOWNFLOW ECONOMIZER W/ ENTHALPY SENSOR | [9 empty] | Low-Leak Downflow Economizer W/ Dry Bulb Sensor | [6 empty] | Low-Leak Downflow Economizer W/ Dry Bulb Sensor
4 | PROVIDE FACTORY INSTALLED R32 SENSOR | [9 empty] | Low-Leak Downflow Economizer W/ Enthalpy Sensor | [6 empty] | Low-Leak Downflow Economizer W/ Enthalpy Sensor
5 | PROVIDE FACTORY INSTALLED RETURN AIR SMOKE DETECTOR | [9 empty] | Ultra Low-Leak Downflow Economizer W/ Dry Bulb Sensor | [6 empty] | Ultra Low-Leak Downflow Economizer W/ Dry Bulb Sensor
6 | PROVIDE FIELD INSTALLED HIGH ALTITUDE KIT | [9 empty] | Ultra Low-Leak Downflow Economizer W/ Enthalpy Sensor | [6 empty] | Ultra Low-Leak Downflow Economizer W/ Enthalpy Sensor
7 | PROVIDE FIELD INSTALLED 14" ROOF CURB | [16 empty] | Manual Fresh Air Damper
8 | PROVIDE FACTORY INSTALLED STANDARD ALUMINIZED EXCHANGER | [9 empty] | Factory Installed Options | [6 empty] | Motorized Fresh Air Damper
9 | PROVIDE FIELD INSTALLED FILTRATION-MERV8 | [9 empty] | Unit Pwrd GFCI Conv. Outlet |  | Phase Monitor |  | Low Ambient Kit
10 | PROVIDE FIELD INSTALLED 4H/2C COMMERCIAL 7DAY PROGRAMMABLE WI-FI CAPABLE HUM/DEHUM THERMOSTAT | [9 empty] | Non Pwrd GFCI Conv. Outlet |  | Thru-the-Base connections |  | Return Air Smoke Detectors |  |  | Other Options available for Field Install: (all units)
11 | PROVIDE FACTORY INSTALLED TWO STAGE COOLING MODES | [9 empty] | Hinged Panels |  | Power Exhaust Power Conn. |  | Supply Air Smoke Detectors |  |  | Condenser Hail Guard |  |  | Overflow Switch |  |  | Differential Enthalpy Sensor
12 | PROVIDE FACTORY INSTALLED SINGLE STAGE COOLING MODES | [9 empty] | Non-Fused Disconnect |  | Condenser Hail Guard |  | Stainless Steel Heat Exchanger |  |  | Low Ambient Control |  |  | LP Conversion Kit |  |  | Smoke Detector- Watertight
13 | PROVIDE FACTORY INSTALLED SINGLE POINT POWER CONNECTION FOR POWER EXHAUST | [16 empty] | Phase Monitor |  |  | High Altitude Kit |  |  | Smoke Detector- Duct Mounted
14 | PROVIDE FIELD INSTALLED PROP FOR DOWNFLOW ECONOMIZER | [9 empty] | DDC Communicating Controller Availability: | [6 empty] | Thru-the-Base connections |  |  | Flue Extension |  |  | Metal sampling tube, 2-4' duct
15 | PROVIDE FIELD INSTALLED ECONOMIZER HOOD | [9 empty] | High Efficiency Models: All Units | [6 empty] | Power Exhaust Prop |  |  | Concentric Duct Kits |  |  | Metal sampling tube, 4-8' duct
[11 empty] | Standard Efficiency Models: 15-Ton, 20-Ton, 25-Ton Units | [6 empty] | Burglar Bars |  |  | Concentric Diffuser |  |  | MERV8 Filtration
[18 empty] | MERV8 or MERV 13 Filtration |  |  | CO2 Sensor |  |  | MERV13 Filtration
[11 empty] | LINK TO ACCESSORIES BROCHURE | [6 empty] | Economizer Hood |  |  | Hold Down Bracket Kit |  |  | 14" Roof Curb
[18 empty] | 14" Tall Wind/Hurricane Curb |  |  | 14" Tall Seismic Curb |  |  | 24" Roof Curb
[11 empty] | LINK TO NOMENCLATURE GUIDE | [6 empty] | Multiple Thermostat options are available, including BACnet compatible options