## R32 ODU
DATE REVISED: AT/WN-APR 2025
R32 |  |  |  | NOTES: 1. To Include iTM Centralized Controller with BACnet Gateway 2. To Include Snow/Hail Gaurds 3. To Include 24" Stand 4. A2L Refrigerant System
R-32 HEAT RECOVERY - VRV OUTDOOR UNITS
AIR or WATER | FAMILY | HEAT RECOVERY | TAG | MODEL | NOMINAL TONNAGE | MODULES (Tonnage Combo's) | ELECTRICAL | [12 empty] | DIMENSIONS |  | EFFICIENCY (NonDucted/Ducted or Specific Combo) | [6 empty] | NOTES
[7 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
[8 empty] | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | (WxHxD) (inch) | WEIGHT (lbs) | EER | IEER | COP47 | COP17 | SCHE | SEER | HSPF
AIR COOLED | EMERION | HEAT RECOVERY | 208-A-E-HR-6 | REYA72AATJA | 6 | 1 | 208V - 230V 3ph | 34 | - | - | 34 | 35 | - | - | 35 |  | - | - |  | 36.7 x 65.4 x 30.1 | 525 | 15.7 / 12.8 | 28.0 / 23.0 | 4.4 / 3.6 | 2.5 / 2.4 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  | 208-A-E-HR-8 | REYA96AATJA | 8 | 1 | 208V - 230V 3ph | 36.3 | - | - | 36.3 | 40 | - | - | 40 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 14.6 / 12.8 | 30.0 / 25.3 | 4.3 / 3.6 | 2.5 / 2.3 | 26.1 / 21.1 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-10 | REYA120AATJA | 10 | 1 | 208V - 230V 3ph | 41.7 | - | - | 41.7 | 45 | - | - | 45 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 13.2 / 12.4 | 27.5 / 23.5 | 4.0 / 3.5 | 2.4 / 2.3 | 26.1 / 22.2 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-12 | REYA144AATJA | 12 | 1 | 208V - 230V 3ph | 52 | - | - | 52 | 60 | - | - | 60 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 12.5 / 12.0 | 26.5 / 22.5 | 3.8 / 3.4 | 2.2 / 2.1 | 25.6 / 22.1 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-14 | REYA168AATJA | 14 | 1 | 208V - 230V 3ph | 62.6 | - | - | 62.6 | 70 | - | - | 70 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-16 | REYA192AATJA | 16 | 1 | 208V - 230V 3ph | 62.4 | - | - | 62.4 | 70 | - | - | 70 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 12.3 / 11.5 | 24.0 / 21.0 | 3.9 / 3.5 | 2.1 / 2.1 | 26.6 / 22.80 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-18 | REYA216AATJA | 18 | 1 | 208V - 230V 3ph | 72.8 | - | - | 72.8 | 80 | - | - | 80 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-20 | REYA240AATJA | 20 | 1 | 208V - 230V 3ph | 84.2 | - | - | 84.2 | 90 | - | - | 90 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.0 / 10.8 | 21.6 / 19.7 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-22 | REYA264AATJA | 22 | 2 (12+10) | 208V - 230V 3ph | 41.7 | 52 | - | 93.7 | 45 | 60 | - | 105 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1525 | 12.0 / 10.6 | 23.9 / 19.2 | 3.7 / 3.2 | 2.4 / 2.1 | 26.2 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-24 | REYA288AATJA | 24 | 2 (12+12) | 208V - 230V 3ph | 52 | 52 | - | 104 | 60 | 60 | - | 120 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 12.0 / 11.0 | 23.2 / 19.3 | 3.6 / 3.3 | 2.4 / 2.1 | 23.4 / 20.0 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-26 | REYA312AATJA | 26 | 2 (14+12) | 208V - 230V 3ph | 52 | 62.6 | - | 114.6 | 60 | 70 | - | 130 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 11.3 / 10.8 | 22.8 / 19.2 | 3.6 / 3.3 | 2.4 / 2.1 | 24.4 / 20.8 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-28 | REYA336AATJA | 28 | 2 (14+14) | 208V - 230V 3ph | 62.6 | 62.6 | - | 125.2 | 70 | 70 | - | 140 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 10.5 / 10.6 | 22.1 / 18.6 | 3.6 / 3.2 | 2.2 / 2.1 | 23.4 / 19.8 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-30 | REYA360AATJA | 30 | 2 (16+14) | 208V - 230V 3ph | 62.6 | 62.4 | - | 125 | 70 | 70 | - | 140 |  |  | - |  | 68.9 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1772 | 11.5 / 10.7 | 21.0 / 18.2 | 3.6 / 3.2 | 2.1 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-32 | REYA384AATJA | 32 | 2 (16+16) | 208V - 230V 3ph | 62.4 | 62.4 | - | 124.8 | 70 | 70 | - | 140 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 22.0 / 18.8 | 3.4 / 3.3 | 2.1 / 2.1 | 22.0 / 17.0 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-34 | REYA408AATJA | 34 | 2 (18+16) | 208V - 230V 3ph | 62.4 | 72.8 | - | 135.2 | 70 | 80 | - | 150 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 21.5 / 18.4 | 3.4 / 3.3 | 2.1 / 2.1 | 21.9 / 18.4 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-36 | REYA432AATJA | 36 | 2 (18+18) | 208V - 230V 3ph | 72.8 | 72.8 | - | 145.6 | 80 | 80 | - | 160 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.1 | 21.1 / 18.1 | 3.4 / 3.3 | 2.1 / 2.1 | 20.3 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-38 | REYA456AATJA | 38 | 2 (20+18) | 208V - 230V 3ph | 72.8 | 84.2 | - | 157 | 80 | 90 | - | 170 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.9 / 9.8 | 20.2 / 17.5 | 3.4 / 3.3 | 2.1 / 2.1 | 18.9 / 18.0 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HR-40 | REYA480AATJA | 40 | 2 (20+20) | 208V - 230V 3ph | 84.2 | 84.2 |  | 168.4 | 90 | 90 | - | 180 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.7 / 9.6 | 19.4 / 17.2 | 3.4 / 3.3 | 2.1 / 2.1 | 16.9 / 16.5 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-6 | REYA72AATDA | 6 | 1 | 460V 3ph | 12.4 | - | - | 12.4 | 15 | - | - | 15 |  | - | - |  | 36.7 x 65.4 x 30.1 | 525 | 15.7 / 12.8 | 28.0 / 23.0 | 4.4 / 3.6 | 2.5 / 2.4 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  | 460-A-E-HR-8 | REYA96AATDA | 8 | 1 | 460V 3ph | 16.4 | - | - | 16.4 | 20 | - | - | 20 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 14.6 / 12.8 | 30.0 / 25.3 | 4.3 / 3.6 | 2.5 / 2.3 | 26.1 / 21.1 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-10 | REYA120AATDA | 10 | 1 | 460V 3ph | 16.6 | - | - | 16.6 | 20 | - | - | 20 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 13.2 / 12.4 | 27.5 / 23.5 | 4.0 / 3.5 | 2.4 / 2.3 | 26.1 / 22.2 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-12 | REYA144AATDA | 12 | 1 | 460V 3ph | 21.3 | - | - | 21.3 | 25 | - | - | 25 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 12.5 / 12.0 | 26.5 / 22.5 | 3.8 / 3.4 | 2.2 / 2.1 | 25.6 / 22.1 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-14 | REYA168AATDA | 14 | 1 | 460V 3ph | 24.9 | - | - | 24.9 | 30 | - | - | 30 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-16 | REYA192AATDA | 16 | 1 | 460V 3ph | 28.3 | - | - | 28.3 | 35 | - | - | 35 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 12.3 / 11.5 | 24.0 / 21.0 | 3.9 / 3.5 | 2.1 / 2.1 | 26.6 / 22.80 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-18 | REYA216AATDA | 18 | 1 | 460V 3ph | 29.9 | - | - | 29.9 | 35 | - | - | 35 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-20 | REYA240AATDA | 20 | 1 | 460V 3ph | 33.4 | - | - | 33.4 | 40 | - | - | 40 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.0 / 10.8 | 21.6 / 19.7 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-22 | REYA264AATDA | 22 | 2 (12+10) | 460V 3ph | 18.9 | 24.2 | - | 43.1 | 20 | 25 | - | 45 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1525 | 12.0 / 10.6 | 23.9 / 19.2 | 3.7 / 3.2 | 2.4 / 2.1 | 26.2 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-24 | REYA288AATDA | 24 | 2 (12+12) | 460V 3ph | 24.2 | 24.2 | - | 48.4 | 25 | 25 | - | 50 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 12.0 / 11.0 | 23.2 / 19.3 | 3.6 / 3.3 | 2.4 / 2.1 | 23.4 / 20.0 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-26 | REYA312AATDA | 26 | 2 (14+12) | 460V 3ph | 24.2 | 28.3 | - | 52.5 | 25 | 30 | - | 55 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 11.3 / 10.8 | 22.8 / 19.2 | 3.6 / 3.3 | 2.4 / 2.1 | 24.4 / 20.8 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-28 | REYA336AATDA | 28 | 2 (14+14) | 460V 3ph | 28.3 | 28.3 | - | 56.6 | 30 | 30 | - | 60 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 10.5 / 10.6 | 22.1 / 18.6 | 3.6 / 3.2 | 2.2 / 2.1 | 23.4 / 19.8 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-30 | REYA360AATDA | 30 | 2 (16+14) | 460V 3ph | 28.3 | 32.2 | - | 60.5 | 30 | 35 | - | 65 |  |  | - |  | 68.9 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1772 | 11.5 / 10.7 | 21.0 / 18.2 | 3.6 / 3.2 | 2.1 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-32 | REYA384AATDA | 32 | 2 (16+16) | 460V 3ph | 32.2 | 32.2 | - | 64.4 | 35 | 35 | - | 70 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 22.0 / 18.8 | 3.4 / 3.3 | 2.1 / 2.1 | 22.0 / 17.0 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-34 | REYA408AATDA | 34 | 2 (18+16) | 460V 3ph | 32.2 | 34.1 | - | 66.3 | 35 | 35 | - | 70 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 21.5 / 18.4 | 3.4 / 3.3 | 2.1 / 2.1 | 21.9 / 18.4 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-36 | REYA432AATDA | 36 | 2 (18+18) | 460V 3ph | 34.1 | 34.1 | - | 68.2 | 35 | 35 | - | 70 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.1 | 21.1 / 18.1 | 3.4 / 3.3 | 2.1 / 2.1 | 20.3 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-38 | REYA456AATDA | 38 | 2 (20+18) | 460V 3ph | 34.1 | 38.1 | - | 72.2 | 35 | 40 | - | 75 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.9 / 9.8 | 20.2 / 17.5 | 3.4 / 3.3 | 2.1 / 2.1 | 18.9 / 18.0 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HR-40 | REYA480AATDA | 40 | 2 (20+20) | 460V 3ph | 38.1 | 38.1 | - | 76.2 | 40 | 40 | - | 80 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.7 / 9.6 | 19.4 / 17.2 | 3.4 / 3.3 | 2.1 / 2.1 | 16.9 / 16.5 | n/a / n/a | n/a / n/a
R-32 HEAT PUMP - VRV OUTDOOR UNITS
AIR or WATER | FAMILY | HEAT PUMP | TAG | MODEL | NOMINAL TONNAGE | MODULES (Tonnage Combo's) | ELECTRICAL | [12 empty] | DIMENSIONS |  | EFFICIENCY (NonDucted/Ducted or Specific Combo) | [6 empty] | NOTES
[7 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
[8 empty] | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | (WxHxD) (inch) | WEIGHT (lbs) | EER | IEER | COP47 | COP17 | SCHE | SEER | HSPF
AIR COOLED | EMERION | HEAT PUMP | 208-A-E-HP-6 | RXYA72AATJA | 6 | 1 | 208V - 230V 3ph | 34 | - | - | 34 | 35 | - | - | 35 |  | - | - |  | 36.7 x 65.4 x 30.1 | 525 | 15.7 / 12.8 | 28.0 / 23.0 | 4.4 / 3.6 | 2.5 / 2.4 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  | 208-A-E-HP-8 | RXYA96AATJA | 8 | 1 | 208V - 230V 3ph | 36.3 | - | - | 36.3 | 40 | - | - | 40 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 14.6 / 12.8 | 30.0 / 25.3 | 4.3 / 3.6 | 2.5 / 2.3 | 26.1 / 21.1 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-10 | RXYA120AATJA | 10 | 1 | 208V - 230V 3ph | 41.7 | - | - | 41.7 | 45 | - | - | 45 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 13.2 / 12.4 | 27.5 / 23.5 | 4.0 / 3.5 | 2.4 / 2.3 | 26.1 / 22.2 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-12 | RXYA144AATJA | 12 | 1 | 208V - 230V 3ph | 52 | - | - | 52 | 60 | - | - | 60 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 12.5 / 12.0 | 26.5 / 22.5 | 3.8 / 3.4 | 2.2 / 2.1 | 25.6 / 22.1 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-14 | RXYA168AATJA | 14 | 1 | 208V - 230V 3ph | 62.6 | - | - | 62.6 | 70 | - | - | 70 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-16 | RXYA192AATJA | 16 | 1 | 208V - 230V 3ph | 62.4 | - | - | 62.4 | 70 | - | - | 70 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 12.3 / 11.5 | 24.0 / 21.0 | 3.9 / 3.5 | 2.1 / 2.1 | 26.6 / 22.80 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-18 | RXYA216AATJA | 18 | 1 | 208V - 230V 3ph | 72.8 | - | - | 72.8 | 80 | - | - | 80 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-20 | RXYA240AATJA | 20 | 1 | 208V - 230V 3ph | 84.2 | - | - | 84.2 | 90 | - | - | 90 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.0 / 10.8 | 21.6 / 19.7 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-22 | RXYA264AATJA | 22 | 2 (12+10) | 208V - 230V 3ph | 41.7 | 52 | - | 93.7 | 45 | 60 | - | 105 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1525 | 12.0 / 10.6 | 23.9 / 19.2 | 3.7 / 3.2 | 2.4 / 2.1 | 26.2 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-24 | RXYA288AATJA | 24 | 2 (12+12) | 208V - 230V 3ph | 52 | 52 | - | 104 | 60 | 60 | - | 120 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 12.0 / 11.0 | 23.2 / 19.3 | 3.6 / 3.3 | 2.4 / 2.1 | 23.4 / 20.0 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-26 | RXYA312AATJA | 26 | 2 (14+12) | 208V - 230V 3ph | 52 | 62.6 | - | 114.6 | 60 | 70 | - | 130 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 11.3 / 10.8 | 22.8 / 19.2 | 3.6 / 3.3 | 2.4 / 2.1 | 24.4 / 20.8 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-28 | RXYA336AATJA | 28 | 2 (14+14) | 208V - 230V 3ph | 62.6 | 62.6 | - | 125.2 | 70 | 70 | - | 140 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 10.5 / 10.6 | 22.1 / 18.6 | 3.6 / 3.2 | 2.2 / 2.1 | 23.4 / 19.8 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-30 | RXYA360AATJA | 30 | 2 (16+14) | 208V - 230V 3ph | 62.6 | 62.4 | - | 125 | 70 | 70 | - | 140 |  |  | - |  | 68.9 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1772 | 11.5 / 10.7 | 21.0 / 18.2 | 3.6 / 3.2 | 2.1 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-32 | RXYA384AATJA | 32 | 2 (16+16) | 208V - 230V 3ph | 62.4 | 62.4 | - | 124.8 | 70 | 70 | - | 140 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 22.0 / 18.8 | 3.4 / 3.3 | 2.1 / 2.1 | 22.0 / 17.0 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-34 | RXYA408AATJA | 34 | 2 (18+16) | 208V - 230V 3ph | 62.4 | 72.8 | - | 135.2 | 70 | 80 | - | 150 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 21.5 / 18.4 | 3.4 / 3.3 | 2.1 / 2.1 | 21.9 / 18.4 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-36 | RXYA432AATJA | 36 | 2 (18+18) | 208V - 230V 3ph | 72.8 | 72.8 | - | 145.6 | 80 | 80 | - | 160 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.1 | 21.1 / 18.1 | 3.4 / 3.3 | 2.1 / 2.1 | 20.3 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-38 | RXYA456AATJA | 38 | 2 (20+18) | 208V - 230V 3ph | 72.8 | 84.2 | - | 157 | 80 | 90 | - | 170 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.9 / 9.8 | 20.2 / 17.5 | 3.4 / 3.3 | 2.1 / 2.1 | 18.9 / 18.0 | n/a / n/a | n/a / n/a
|  |  | 208-A-E-HP-40 | RXYA480AATJA | 40 | 2 (20+20) | 208V - 230V 3ph | 84.2 | 84.2 |  | 168.4 | 90 | 90 | - | 180 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.7 / 9.6 | 19.4 / 17.2 | 3.4 / 3.3 | 2.1 / 2.1 | 16.9 / 16.5 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-6 | RXYA72AAYDA | 6 | 1 | 460V 3ph | 15.5 | - | - | 15.5 | 20 | - | - | 20 |  | - | - |  | 36.7 x 65.4 x 30.1 | 525 | 15.7 / 12.8 | 28.0 / 23.0 | 4.4 / 3.6 | 2.5 / 2.4 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  | 460-A-E-HP-8 | RXYA96AAYDA | 8 | 1 | 460V 3ph | 18.7 | - | - | 18.7 | 20 | - | - | 20 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 14.6 / 12.8 | 30.0 / 25.3 | 4.3 / 3.6 | 2.5 / 2.3 | 26.1 / 21.1 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-10 | RXYA120AAYDA | 10 | 1 | 460V 3ph | 18.9 | - | - | 18.9 | 20 | - | - | 20 |  | - | - |  | 48.8 x 65.4 x 30.1 | 725 | 13.2 / 12.4 | 27.5 / 23.5 | 4.0 / 3.5 | 2.4 / 2.3 | 26.1 / 22.2 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-12 | RXYA144AAYDA | 12 | 1 | 460V 3ph | 24.2 | - | - | 24.2 | 25 | - | - | 25 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 12.5 / 12.0 | 26.5 / 22.5 | 3.8 / 3.4 | 2.2 / 2.1 | 25.6 / 22.1 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-14 | RXYA168AAYDA | 14 | 1 | 460V 3ph | 28.3 | - | - | 28.3 | 30 | - | - | 30 |  | - | - |  | 48.8 x 65.4 x 30.1 | 800 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-16 | RXYA192AAYDA | 16 | 1 | 460V 3ph | 32.2 | - | - | 32.2 | 35 | - | - | 35 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 12.3 / 11.5 | 24.0 / 21.0 | 3.9 / 3.5 | 2.1 / 2.1 | 26.6 / 22.80 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-18 | RXYA216AAYDA | 18 | 1 | 460V 3ph | 34.1 | - | - | 34.1 | 35 | - | - | 35 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-20 | RXYA240AAYDA | 20 | 1 | 460V 3ph | 38.1 | - | - | 38.1 | 40 | - | - | 40 |  | - | - |  | 68.9 x 65.4 x 30.1 | 972 | 11.0 / 10.8 | 21.6 / 19.7 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-22 | RXYA264AAYDA | 22 | 2 (12+10) | 460V 3ph | 18.9 | 24.2 | - | 43.1 | 20 | 25 | - | 45 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1525 | 12.0 / 10.6 | 23.9 / 19.2 | 3.7 / 3.2 | 2.4 / 2.1 | 26.2 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-24 | RXYA288AAYDA | 24 | 2 (12+12) | 460V 3ph | 24.2 | 24.2 | - | 48.4 | 25 | 25 | - | 50 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 12.0 / 11.0 | 23.2 / 19.3 | 3.6 / 3.3 | 2.4 / 2.1 | 23.4 / 20.0 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-26 | RXYA312AAYDA | 26 | 2 (14+12) | 460V 3ph | 24.2 | 28.3 | - | 52.5 | 25 | 30 | - | 55 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 11.3 / 10.8 | 22.8 / 19.2 | 3.6 / 3.3 | 2.4 / 2.1 | 24.4 / 20.8 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-28 | RXYA336AAYDA | 28 | 2 (14+14) | 460V 3ph | 28.3 | 28.3 | - | 56.6 | 30 | 30 | - | 60 |  |  | - |  | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1600 | 10.5 / 10.6 | 22.1 / 18.6 | 3.6 / 3.2 | 2.2 / 2.1 | 23.4 / 19.8 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-30 | RXYA360AAYDA | 30 | 2 (16+14) | 460V 3ph | 28.3 | 32.2 | - | 60.5 | 30 | 35 | - | 65 |  |  | - |  | 68.9 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1772 | 11.5 / 10.7 | 21.0 / 18.2 | 3.6 / 3.2 | 2.1 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-32 | RXYA384AAYDA | 32 | 2 (16+16) | 460V 3ph | 32.2 | 32.2 | - | 64.4 | 35 | 35 | - | 70 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 22.0 / 18.8 | 3.4 / 3.3 | 2.1 / 2.1 | 22.0 / 17.0 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-34 | RXYA408AAYDA | 34 | 2 (18+16) | 460V 3ph | 32.2 | 34.1 | - | 66.3 | 35 | 35 | - | 70 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.5 | 21.5 / 18.4 | 3.4 / 3.3 | 2.1 / 2.1 | 21.9 / 18.4 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-36 | RXYA432AAYDA | 36 | 2 (18+18) | 460V 3ph | 34.1 | 34.1 | - | 68.2 | 35 | 35 | - | 70 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 10.7 / 10.1 | 21.1 / 18.1 | 3.4 / 3.3 | 2.1 / 2.1 | 20.3 / 18.2 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-38 | RXYA456AAYDA | 38 | 2 (20+18) | 460V 3ph | 34.1 | 38.1 | - | 72.2 | 35 | 40 | - | 75 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.9 / 9.8 | 20.2 / 17.5 | 3.4 / 3.3 | 2.1 / 2.1 | 18.9 / 18.0 | n/a / n/a | n/a / n/a
|  |  | 460-A-E-HP-40 | RXYA480AAYDA | 40 | 2 (20+20) | 460V 3ph | 38.1 | 38.1 | - | 76.2 | 40 | 40 | - | 80 |  |  | - |  | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1948 | 9.7 / 9.6 | 19.4 / 17.2 | 3.4 / 3.3 | 2.1 / 2.1 | 16.9 / 16.5 | n/a / n/a | n/a / n/a

## R32 BSB
DATE REVISED: AT/WN-MAR 2025
R32 |  |  |  |  | NOTES: 1. To Include Service Ball Valves on both inlet and outlet ports 2. No condensate pump required
VRV Heat Recovery - BSB's
FAMILY | TAG | # PORTS | MODEL | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) | MAX OVERCURRENT PROTECTION (MOP) | MAX CAPACITY (per Port) | MAX CAPACITY (per Box) | DIMENSIONS (WxHxD inch) | WEIGHT (lbs) | NOTES
Single Port | BS-1 | 1 | BSA36AAVJ | 208-230V 1ph |  |  | 36 | 36 | 8-1/8 x 15-1/4 x 16-3/4
| BS-1 | 1 | BSA60AAVJ | 208-230V 1ph |  |  | 60 | 60 | 8-1/8 x 15-1/4 x 16-3/4
| BS-1 | 1 | BSA96AAVJ | 208-230V 1ph |  |  | 96 | 96 | 8-1/8 x 15-1/4 x 16-3/4
Flex Series | BSF-4 | 4 | BSF4A54AAVJ | 208-230V 1ph |  |  | 54 | 144 | 9-1/2 x 19-5/16 x 27-11/16 |  | Capable of Left, Right, or Pass-through configurations. Can connect in parallel or series. Limited to 12 ports when connected in series. Other limitations in series may apply.
| BSF-6 | 6 | BSF6A54AAVJ | 208-230V 1ph |  |  | 54 | 216 | 9-1/2 x 33-7/16 x 27-11/16
| BSF-8 | 8 | BSF8A54AAVJ | 208-230V 1ph |  |  | 54 | 290 | 9-1/2 x 33-7/16 x 27-11/16
VRV Heat Pump or Heat Recovery - SSOV's
FAMILY | TAG | # PORTS | MODEL | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) | MAX OVERCURRENT PROTECTION (MOP) | MAX CAPACITY (per Port) | MAX CAPACITY (per Box) | DIMENSIONS (WxHxD inch) | WEIGHT (lbs) | NOTES
SSOV | SSOV-60 | 1 | BSA36AAVJ | 208-230V 1ph |  |  | A < 60 | A < 60 | 8-1/8 x 15-1/4 x 16-3/4 |  | Utilized in help Mrel calculations per ASHRAE 15
| SSVOV-96 | 1 | BSA60AAVJ | 208-230V 1ph |  |  | 60 < A < 96 | 60 < A < 96 | 8-1/8 x 15-1/4 x 16-3/4

## R32 IDU
DATE REVISED: AT/WN-MAR 2025
R32 |  |  |  | NOTES: 1. Standard Limited Warranty: 10-year warranty on compressor and all parts 2. 360 degree airflow distribution and three room sensors enables optimized occupant comfort and efficiency (FXFQ) 3. Optional self-cleaning filter panel to further increase efficiency and reduce maintenance costs (FXFQ) 4. Built-in condensate pump (FXDQ_M, FXFQ_P, FXFQ_T, FXMQ_M, FXMQ_P, FXUQ_P, FXZQ_M)
VARIABLE REFRIGERANT VOLUME - INDOOR UNIT SCHEDULE
| IMAGE | BASIS OF DESIGN (DAIKIN) | NOMINAL TONNAGE | TYPE | SUPPLY FAN | COOLING CAPACITY |  |  |  | HEATING CAPACITY |  | ELECTRICAL |  |  | DIMENSIONS | WEIGHT | NOTES | Options and Accessories
[5 empty] | AIR FLOW RATE cfm | TOTAL BTU/h | SENSIBLE BTU/h | ENTERING AIR |  | TOTAL BTU/h | ENTERING AIR °Fdb | Voltage - Phase | MCA | MOP | WxHxD | lbs
[8 empty] | °F DB | °F WB
DUCTED UNITS | #VALUE! | FXSA05AAVJU | 0.5 | MSP Concealed Ducted Unit (Medium Static) | 281 | 5800 | 4060 | 80 | 67 | 6500 | 70 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55 |  | BRC1NRV71 (1)
|  | FXSA07AAVJU | 0.6 |  | 281 | 7200 | 5040 | 80 | 67 | 8500 | 70 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55
|  | FXSA09AAVJU | 0.75 |  | 318 | 9500 | 6650 | 80 | 67 | 10500 | 70 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55
|  | FXSA12AAVJU | 1 |  | 335 | 12000 | 8400 | 80 | 67 | 13500 | 70 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55
|  | FXSA15AAVJU | 1.25 |  | 530 | 15000 | 10500 | 80 | 67 | 17000 | 70 | 208-230V 1ph | 1.4 | 15 | 27-9/16 x 9-11/16 x 31-1/2 | 60
|  | FXSA18AAVJU | 1.5 |  | 600 | 18000 | 12600 | 80 | 67 | 20000 | 70 | 208-230V 1ph | 1.6 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 77
|  | FXSA24AAVJU | 2 |  | 742 | 24000 | 16800 | 80 | 67 | 27000 | 70 | 208-230V 1ph | 1.8 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 77
|  | FXSA30AAVJU | 2.5 |  | 812 | 30000 | 21000 | 80 | 67 | 34000 | 70 | 208-230V 1ph | 1.8 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 82
|  | FXSA36AAVJU | 3 |  | 1130 | 36000 | 25200 | 80 | 67 | 40000 | 70 | 208-230V 1ph | 2.5 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 101
|  | FXSA48AAVJU | 4 |  | 1307 | 48000 | 33600 | 80 | 67 | 54000 | 70 | 208-230V 1ph | 2.8 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 104
|  | FXSA54AAVJU | 4.5 |  | 1377 | 54000 | 37800 | 80 | 67 | 60000 | 70 | 208-230V 1ph | 3.3 | 15 | 61 x 9-11/16 x 31-1/2 | 115
| #VALUE! | FXMA15AAVJU | 1.25 | HSP Concealed Ducted Unit (High Static 0.8") | 560 | 14200 | 9940 | 80 | 67 | 17000 | 70 | 208-230V 1ph | 1.8 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 82 |  | BRC1NRV71 (1)
|  | FXMA18AAVJU | 1.5 |  | 635 | 18000 | 12600 | 80 | 67 | 20000 | 70 | 208-230V 1ph | 1.9 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 82
|  | FXMA24AAVJU | 2 |  | 742 | 24000 | 16800 | 80 | 67 | 27000 | 70 | 208-230V 1ph | 1.9 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 84
|  | FXMA30AAVJU | 2.5 |  | 1094 | 30000 | 21000 | 80 | 67 | 34000 | 70 | 208-230V 1ph | 3 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 101
|  | FXMA36AAVJU | 3 |  | 1130 | 36000 | 25200 | 80 | 67 | 40000 | 70 | 208-230V 1ph | 3.1 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 101
|  | FXMA48AAVJU | 4 |  | 1377 | 48000 | 33600 | 80 | 67 | 54000 | 70 | 208-230V 1ph | 3.6 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 106
|  | FXMA54AAVJU | 4.5 |  | 1518 | 54000 | 37800 | 80 | 67 | 63000 | 70 | 208-230V 1ph | 3.6 | 15 | 61 x 9-11/16 x 31-1/2 | 115
| #VALUE! | FXTA09AAVJUD | 0.75 | Multi Position Air Handler (Factory Disconnect) | 300 | 7200 | 5040 | 80 | 67 | 8500 | 70 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 108 |  | BRC1NRV71 (1)
|  | FXTA12AAVJUD | 1 |  | 400 | 12000 | 8400 | 80 | 67 | 13500 | 70 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 115
|  | FXTA18AAVJUD | 1.5 |  | 600 | 18000 | 12600 | 80 | 67 | 20000 | 70 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 118
|  | FXTA24AAVJUD | 2 |  | 800 | 24000 | 16800 | 80 | 67 | 27000 | 70 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 115
|  | FXTA30AAVJUD | 2.5 |  | 1000 | 30000 | 21000 | 80 | 67 | 34000 | 70 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 116
|  | FXTA36AAVJUD | 3 |  | 1050 | 36000 | 25200 | 80 | 67 | 40000 | 70 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 116
|  | FXTA42AAVJUD | 3.5 |  | 1400 | 42000 | 29400 | 80 | 67 | 46000 | 70 | 208-230V 1ph | 6.5 | 15 | 21 x 53-1/2 x 21 | 147
|  | FXTA48AAVJUD | 4 |  | 1520 | 48000 | 33600 | 80 | 67 | 54000 | 70 | 208-230V 1ph | 6.5 | 15 | 21 x 53-1/2 x 21 | 147
|  | FXTA54AAVJUD | 4.5 |  | 1800 | 54000 | 37800 | 80 | 67 | 60000 | 70 | 208-230V 1ph | 8.6 | 15 | 21 x 58 x 24-1/2 | 168
|  | FXTA60AAVJUD | 5 |  | 1800 | 60000 | 42000 | 80 | 67 | 66000 | 70 | 208-230V 1ph | 8.6 | 15 | 21 x 58 x 24-1/2 | 168
NON DUCTED UNITS | #VALUE! | FXAA05AAVJU | 0.5 | Wall Mounted Unit | [13 empty] | BRC1NRV71 (1)
|  | FXAA07AAVJU | 0.6 |  | 282 | 7500 | 5250 | 80 | 67 | 8500 | 70 | 208-230V 1ph |  |  | 33-13/16 x 11-5/8 x 9-3/4 | 27
|  | FXAA09AAVJU | 0.75 |  | 353 | 9500 | 6650 | 80 | 67 | 10500 | 70 | 208-230V 1ph |  |  | 33-13/16 x 11-5/8 x 9-3/4 | 27
|  | FXAA12AAVJU | 1 |  | 406 | 12000 | 8400 | 80 | 67 | 13500 | 70 | 208-230V 1ph |  |  | 33-13/16 x 11-5/8 x 9-3/4 | 27
|  | FXAA18AAVJU | 1.5 |  | 512 | 18000 | 12600 | 80 | 67 | 20000 | 70 | 208-230V 1ph |  |  | 44-1/8 x 11-5/8 x 9-3/4 | 35
|  | FXAA24AAVJU | 2 |  | 670 | 24000 | 16800 | 80 | 67 | 27000 | 70 | 208-230V 1ph |  |  | 44-1/8 x 11-5/8 x 9-3/4 | 35
| #VALUE! | FXFA07AAVJU | 0.6 | Round Flow Sensing Cassette | 441 | 7200 | 5760 | 80 | 67 | 8500 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42 |  | BRC1NRV71 (1)
|  | FXFA09AAVJU | 0.75 |  | 441 | 9500 | 7600 | 80 | 67 | 10500 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFA12AAVJU | 1 |  | 441 | 12000 | 9600 | 80 | 67 | 13500 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFA15AAVJU | 1.25 |  | 512 | 14400 | 11520 | 80 | 67 | 17000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFA18AAVJU | 1.5 |  | 547 | 18000 | 14400 | 80 | 67 | 20000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFA24AAVJU | 2 |  | 776 | 23000 | 18400 | 80 | 67 | 27000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 51
|  | FXFA30AAVJU | 2.5 |  | 1059 | 30000 | 24000 | 80 | 67 | 34000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 11-11/32 x 33-1/16 | 58
|  | FXFA36AAVJU | 3 |  | 1253 | 36000 | 28800 | 80 | 67 | 40000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 11-11/32 x 33-1/16 | 58
|  | FXFA48AAVJU | 4 |  | 1253 | 48000 | 38400 | 80 | 67 | 54000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 11-11/32 x 33-1/16 | 58
|  | FXFA54AAVJU | 4.5 |  | 1253 | 54000 | 43200 | 80 | 67 | 60000 | 70 | 208-230V 1ph |  | 15 | 33-1/16 x 11-11/32 x 33-1/17 | 58
| #VALUE! | FXZA05AAVJU | 0.5 | 4-Way Discharge Ceiling Cassette Vista (2' x 2') white | 300 | 5800 | 4060 | 80 | 67 | 6500 | 70 | 208-230V 1ph |  |  | 10-1/4 x 22-5/8 x 22-5/8 | 41.5 |  | BRC1NRV71 (1)
|  | FXZA07AAVJU | 0.6 |  | 307 | 7500 | 5250 | 80 | 67 | 8500 | 70 | 208-230V 1ph |  |  | 10-1/4 x 22-5/8 x 22-5/8 | 41.5
|  | FXZA09AAVJU | 0.75 |  | 317 | 9500 | 6650 | 80 | 67 | 10500 | 70 | 208-230V 1ph |  |  | 10-1/4 x 22-5/8 x 22-5/8 | 41.5
|  | FXZA12AAVJU | 1 |  | 353 | 12000 | 8400 | 80 | 67 | 13500 | 70 | 208-230V 1ph |  |  | 10-1/4 x 22-5/8 x 22-5/8 | 42.6
|  | FXZA15AAVJU | 1.25 |  | 405 | 15000 | 10500 | 80 | 67 | 17000 | 70 | 208-230V 1ph |  |  | 10-1/4 x 22-5/8 x 22-5/8 | 42.6
|  | FXZA18AAVJU | 1.5 |  | 511 | 18000 | 12600 | 80 | 67 | 20000 | 70 | 208-230V 1ph |  |  | 10-1/4 x 22-5/8 x 22-5/8 | 48.1