## R410a ODU
DATE REVISED: AT/WN-MAR 2025
R410A |  |  |  |  | NOTES: 1. To Include iTM Centralized Controller with BACnet Gateway 2. To Include Snow/Hail Gaurds 3. To Include 24" Stand
HEAT RECOVERY SYTEM - 208V | VRV OUTDOOR UNITS
| AIR or WATER | FAMILY | HEAT RECOVERY | TAG | MODEL | NOMINAL TONNAGE | MODULES (Tonnage Combo's) | ELECTRICAL | [12 empty] | DIMENSIONS |  | EFFICIENCY (NonDucted/Ducted or Specific Combo) | [6 empty] | NOTES
[8 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
[9 empty] | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | (WxHxD) (inch) | WEIGHT (lbs) | EER | IEER | COP47 | COP17 | SCHE | SEER | HSPF
| AIR COOLED | IV-X | HEAT RECOVERY | 208-A-X-HR-6 | REYQ72XATJB | 6 | 1 | 208V - 230V 3ph | 38.1 | - | - | 38.1 | 45 | - | - | 45 | 20.8 | - | - | 20.8 | 66-11/16 x 48-7/8 x 30-3/16 | 727 | 15.8 / 13.9 | 25.2 / 21.3 | 4.3 / 3.7 | 2.5 / 2.3 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  |  | 208-A-X-HR-8 | REYQ96XATJB | 8 | 1 | 208V - 230V 3ph | 38.1 | - | - | 38.1 | 45 | - | - | 45 | 23.3 | - | - | 23.3 | 66-11/16 x 48-7/8 x 30-3/16 | 727 | 14.6 / 12.5 | 27.8 / 21.9 | 4.2 / 3.6 | 2.6 / 2.3 | 26.4 / 21.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-10 | REYQ120XATJB | 10 | 1 | 208V - 230V 3ph | 43 | - | - | 43 | 50 | - | - | 50 | 28.2 | - | - | 28.2 | 66-11/16 x 48-7/8 x 30-3/16 | 727 | 13.2 / 12.3 | 25.5 / 22.6 | 3.8 / 3.5 | 2.5 / 2.3 | 26.0 / 22.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-12 | REYQ144XATJB | 12 | 1 | 208V - 230V 3ph | 58.3 | - | - | 58.3 | 70 | - | - | 70 | 42.6 | - | - | 42.6 | 66-11/16 x 48-7/8 x 30-3/16 | 793 | 11.9 / 11.6 | 23.5 / 21.6 | 3.8 / 3.4 | 2.2 / 2.1 | 25.5 / 22.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-14 | REYQ168XATJB | 14 | 1 | 208V - 230V 3ph | 61.9 | - | - | 61.9 | 70 | - | - | 70 | 49 | - | - | 49 | 66-11/16 x 48-7/8 x 30-3/16 | 793 | 10.8 / 10.7 | 22.3 / 20.4 | 3.6 / 3.3 | 2.1 / 2.1 | 25.5 / 22.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-16 | REYQ192XATJB | 16 | 2 | 208V - 230V 3ph | 38.1 | 38.1 | - | 76.2 | 45 | 45 | - | 90 | 24.7 | 24.7 | - | 49.4 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1454 | 13.0 / 13.0 | 22.6 / 21.4 | 3.9 / 3.7 | 2.5 / 2.4 | 26.6 / 22.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-18 | REYQ216XATJB | 18 | 2 | 208V - 230V 3ph | 38.1 | 43 | - | 81.1 | 45 | 50 | - | 95 | 28.5 | 28.5 | - | 57 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1454 | 12.4 / 12.3 | 23.1 / 21.7 | 3.8 / 3.5 | 2.3 / 2.2 | 25.5 / 21.9 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-20 | REYQ240XATJB | 20 | 2 | 208V - 230V 3ph | 43 | 43 | - | 86 | 50 | 50 | - | 100 | 29 | 29 | - | 58 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1454 | 11.6 / 11.7 | 22.2 / 20.0 | 3.7 / 3.4 | 2.3 / 2.2 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-22 | REYQ264XATJB | 22 | 2 | 208V - 230V 3ph | 43 | 58.3 | - | 101.3 | 50 | 70 | - | 120 | 32.9 | 42.1 | - | 75 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1520 | 11.2 / 10.4 | 21.6 / 18.0 | 3.6 / 3.2 | 2.2 / 2.1 | 26.1 / 18.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-24 | REYQ288XATJB | 24 | 2 | 208V - 230V 3ph | 58.3 | 58.3 | - | 116.6 | 70 | 70 | - | 140 | 43.5 | 43.5 | - | 87 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1586 | 11.0 / 10.3 | 21.0 / 17.9 | 3.5 / 3.2 | 2.2 / 2.1 | 23.3 / 19.9 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-26 | REYQ312XATJB | 26 | 2 | 208V - 230V 3ph | 58.3 | 61.9 | - | 120.2 | 70 | 70 | - | 140 | 46.5 | 46.5 | - | 93 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1586 | 10.1 / 9.9 | 20.4 / 18.0 | 3.6 / 3.2 | 2.1 / 2.1 | 24.3 / 20.7 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-28 | REYQ336XATJB | 28 | 2 | 208V - 230V 3ph | 61.9 | 61.9 | - | 123.8 | 70 | 70 | - | 140 | 50.1 | 50.1 | - | 100.2 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1586 | 9.9 / 9.5 | 20.0 / 17.3 | 3.5 / 3.2 | 2.1 / 2.1 | 23.3 / 19.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-30 | REYQ360XATJB | 30 | 3 | 208V - 230V 3ph | 43 | 43 | 43 | 129 | 50 | 50 | 50 | 150 | 32.7 | 32.7 | 32.7 | 98.1 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2181 | 10.9 / 10.6 | 20.0 / 18.8 | 3.6 / 3.2 | 2.3 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-32 | REYQ384XATJB | 32 | 3 | 208V - 230V 3ph | 43 | 43 | 58.3 | 144.3 | 50 | 50 | 70 | 170 | 33.8 | 33.8 | 43.7 | 111.3 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2247 | 9.7 / 9.9 | 19.0 / 17.6 | 3.2 / 3.2 | 2.2 / 2.1 | 21.9 / 17.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-34 | REYQ408XATJB | 34 | 3 | 208V - 230V 3ph | 43 | 58.3 | 58.3 | 159.6 | 50 | 70 | 70 | 190 | 35.7 | 45.1 | 45.1 | 125.9 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2313 | 9.8 / 9.7 | 17.2 / 17.7 | 3.2 / 3.2 | 2.1 / 2.1 | 21.8 / 18.3 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-36 | REYQ432XATJB | 36 | 3 | 208V - 230V 3ph | 58.3 | 58.3 | 58.3 | 174.9 | 70 | 70 | 70 | 210 | 45.1 | 45.1 | 45.1 | 135.3 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2379 | 9.8 / 9.7 | 16.2 / 17.3 | 3.2 / 3.2 | 2.1 / 2.1 | 20.2 / 18.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-X-HR-38 | REYQ456XATJB | 38 | 3 | 208V - 230V 3ph | 58.3 | 58.3 | 61.9 | 178.5 | 70 | 70 | 70 | 210 | 47 | 47 | 47 | 141 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2379 | 9.3 / 9.5 | 16.2 / 16.7 | 3.2 / 3.2 | 2.1 / 2.1 | 18.8 / 17.9 | n/a / n/a | n/a / n/a
| AIR COOLED | EMERION | HEAT RECOVERY | 208-A-E-HR-6 | REYQ72AATJA | 6 | 1 | 208V - 230V 3ph | 27.3 | - | - | 27.3 | 30 | - | - | 30 | 11.1 | - | - | 11.1 | 36.7 x 65.4 x 30.1 | 509 | 15.7 / 12.8 | 28.0 / 23.0 | 4.4 / 3.6 | 2.5 / 2.4 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  |  | 208-A-E-HR-8 | REYQ96AATJA | 8 | 1 | 208V - 230V 3ph | 34.1 | - | - | 34.1 | 35 | - | - | 35 | 15.2 | - | - | 15.2 | 48.8 x 65.4 x 30.1 | 710 | 14.6 / 12.8 | 30.0 / 25.3 | 4.3 / 3.6 | 2.5 / 2.3 | 26.1 / 21.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-10 | REYQ120AATJA | 10 | 1 | 208V - 230V 3ph | 36.5 | - | - | 36.5 | 40 | - | - | 40 | 21.1 | - | - | 21.1 | 48.8 x 65.4 x 30.1 | 712 | 13.2 / 12.4 | 27.5 / 23.5 | 4.0 / 3.5 | 2.4 / 2.3 | 26.1 / 22.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-12 | REYQ144AATJA | 12 | 1 | 208V - 230V 3ph | 47.8 | - | - | 47.8 | 50 | - | - | 50 | 25.8 | - | - | 25.8 | 48.8 x 65.4 x 30.1 | 785 | 12.5 / 12.0 | 26.5 / 22.5 | 3.8 / 3.4 | 2.2 / 2.1 | 25.6 / 22.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-14 | REYQ168AATJA | 14 | 1 | 208V - 230V 3ph | 54.9 | - | - | 54.9 | 60 | - | - | 60 | 32.5 | - | - | 32.5 | 48.8 x 65.4 x 30.1 | 787 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-16 | REYQ192AATJA | 16 | 1 | 208V - 230V 3ph | 59.8 | - | - | 59.8 | 60 | - | - | 60 | 33.2 | - | - | 33.2 | 68.9 x 65.4 x 30.1 | 957 | 12.3 / 11.5 | 24.0 / 21.0 | 3.9 / 3.5 | 2.1 / 2.1 | 26.6 / 22.80 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-18 | REYQ216AATJA | 18 | 1 | 208V - 230V 3ph | 67.2 | - | - | 67.2 | 70 | - | - | 70 | 40 | - | - | 40 | 68.9 x 65.4 x 30.1 | 957 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-20 | REYQ240AATJA | 20 | 1 | 208V - 230V 3ph | 73.7 | - | - | 73.7 | 80 | - | - | 80 | 48.8 | - | - | 48.8 | 68.9 x 65.4 x 30.1 | 957 | 11.0 / 10.8 | 21.6 / 19.7 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-22 | REYQ264AATJA | 22 | 2 (12+10) | 208V - 230V 3ph | 47.8 | 36.5 | - | 84.3 | 50 | 40 | - | 90 | 25.8 | 21.1 | - | 46.9 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1497 | 12.0 / 10.6 | 23.9 / 19.2 | 3.7 / 3.2 | 2.4 / 2.1 | 26.2 / 18.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-24 | REYQ288AATJA | 24 | 2 (12+12) | 208V - 230V 3ph | 47.8 | 47.8 | - | 95.6 | 50 | 50 | - | 100 | 25.8 | 25.8 | - | 51.6 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1570 | 12.0 / 11.0 | 23.2 / 19.3 | 3.6 / 3.3 | 2.4 / 2.1 | 23.4 / 20.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-26 | REYQ312AATJA | 26 | 2 (14+12) | 208V - 230V 3ph | 54.9 | 47.8 | - | 102.7 | 60 | 50 | - | 110 | 32.5 | 25.8 | - | 58.3 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1572 | 11.3 / 10.8 | 22.8 / 19.2 | 3.6 / 3.3 | 2.4 / 2.1 | 24.4 / 20.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-28 | REYQ336AATJA | 28 | 2 (14+14) | 208V - 230V 3ph | 54.9 | 54.9 | - | 109.8 | 60 | 60 | - | 120 | 32.5 | 32.5 | - | 65 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1574 | 10.5 / 10.6 | 22.1 / 18.6 | 3.6 / 3.2 | 2.2 / 2.1 | 23.4 / 19.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-30 | REYQ360AATJA | 30 | 2 (16+14) | 208V - 230V 3ph | 59.8 | 54.9 | - | 114.7 | 60 | 60 | - | 120 | 33.2 | 32.5 | - | 65.7 | 68.9 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1744 | 11.5 / 10.7 | 21.0 / 18.2 | 3.6 / 3.2 | 2.1 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-32 | REYQ384AATJA | 32 | 2 (16+16) | 208V - 230V 3ph | 59.8 | 59.8 | - | 119.6 | 60 | 60 | - | 120 | 33.2 | 33.2 | - | 66.4 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 10.7 / 10.5 | 22.0 / 18.8 | 3.4 / 3.3 | 2.1 / 2.1 | 22.0 / 17.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-34 | REYQ408AATJA | 34 | 2 (18+16) | 208V - 230V 3ph | 67.2 | 59.8 | - | 127 | 70 | 60 | - | 130 | 40 | 33.2 | - | 73.2 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 10.7 / 10.5 | 21.5 / 18.4 | 3.4 / 3.3 | 2.1 / 2.1 | 21.9 / 18.4 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-36 | REYQ432AATJA | 36 | 2 (18+18) | 208V - 230V 3ph | 67.2 | 67.2 | - | 134.4 | 70 | 70 | - | 140 | 40 | 40 | - | 80 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 10.7 / 10.1 | 21.1 / 18.1 | 3.4 / 3.3 | 2.1 / 2.1 | 20.3 / 18.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-38 | REYQ456AATJA | 38 | 2 (20+18) | 208V - 230V 3ph | 73.7 | 67.2 | - | 140.9 | 80 | 70 | - | 150 | 48.8 | 40 | - | 88.8 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 9.9 / 9.8 | 20.2 / 17.5 | 3.4 / 3.3 | 2.1 / 2.1 | 18.9 / 18.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-E-HR-40 | REYQ480AATJA | 40 | 2 (20+20) | 208V - 230V 3ph | 73.7 | 73.7 |  | 147.4 | 80 | 80 | - | 160 | 48.8 | 48.8 | - | 97.6 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 9.7 / 9.6 | 19.4 / 17.2 | 3.4 / 3.3 | 2.1 / 2.1 | 16.9 / 16.5 | n/a / n/a | n/a / n/a
| AIR COOLED | AURORA | HEAT RECOVERY | 208-A-A-HR-6 | RELQ72TBTJA | 6 | 1 | 208V - 230V 3ph | 60.8 | - | - | 60.8 | 70 | - | - | 70 | 20.7 | - | - | 20.7 | 66-11/16 X 48-7/8 X 30-3/16 | 727 | 15.8 / 13.7 | 24.0 / 20.8 | 4.30 / 3.68 | 2.3 / 2.4 | 26.1 / 22.6 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -22 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  |  | 208-A-A-HR-8 | RELQ96TBTJA | 8 | 1 | 208V - 230V 3ph | 76.5 | - | - | 76.5 | 80 | - | - | 80 | 36.8 | - | - | 36.8 | 66-11/16 X 48-7/8 X 30-3/16 | 793 | 15.3 / 12.5 | 24.8 / 19.1 | 4.23 / 3.42 | 2.25 / 2.37 | 25.7 / 19.7 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-A-HR-10 | RELQ120TBTJA | 10 | 1 | 208V - 230V 3ph | 83.4 | - | - | 83.4 | 90 | - | - | 90 | 39.3 | - | - | 39.3 | 66-11/16 X 48-7/8 X 30-3/16 | 793 | 13.7 / 12.4 | 23.4 / 19.6 | 3.98 / 3.51 | 2.25 / 2.25 | 26.7 / 21.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-A-HR-12 | RELQ144TATJA | 12 | 2 (6+6) | 208V - 230V 3ph | 60.8 | 60.8 | - | 121.6 | 70 | 70 | - | 140 | 21.6 | 21.6 | - | 43.2 | 66-11/16 X 48-7/8 X 30-3/16 + 66-11/16 X 48-7/8 X 30-3/16 | 1454 | 12.9 / 12.6 | 22.5 / 18.6 | 3.81 / 3.55 | 2.20 / 2.20 | 25.5 / 23.8 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-A-HR-16 | RELQ192TATJA | 16 | 2 (8+8) | 208V - 230V 3ph | 76.5 | 76.5 | - | 153 | 80 | 80 | - | 160 | 38.1 | 38.1 | - | 76.2 | 66-11/16 X 48-7/8 X 30-3/16 + 66-11/16 X 48-7/8 X 30-3/17 | 1586 | 12.5 / 12.7 | 22.1 / 19.0 | 3.85 / 3.57 | 2.15 / 2.17 | 25.5 / 21.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-A-A-HR-20 | RELQ240TATJA | 20 | 2 (10+10) | 208V - 230V 3ph | 83.4 | 83.4 | - | 166.8 | 90 | 90 | - | 180 | 40.4 | 40.4 | - | 80.8 | 66-11/16 X 48-7/8 X 30-3/16 + 66-11/16 X 48-7/8 X 30-3/18 | 1586 | 12.3 / 11.7 | 21.1 / 18.6 | 3.68 / 3.49 | 2.13 / 2.16 | 24.9 / 20.8 | n/a / n/a | n/a / n/a
| WATER COOLED | T SERIES | HEAT RECOVERY | 208-W-T-HR-6 | RWEYQ72PCTJ | 6 | 1 | 208V - 230V 3ph | 22.4 | - | - | 22.4 | 30 | - | - | 30 | 11.6 | - | - | 11.6 | 39-3/8 x 30-3/4 x 21-11/16 | 330 | 14.0 / 14.0 | 24.1 / 22.3 | 4.89 / 4.78 | Note: the values to the left are COP at 68 degrees. | 17.8 / 19.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-8 | RWEQ96TATJA | 8 | 1 | 208V - 230V 3ph | 28.8 | - | - | 28.8 | 35 | - | - | 35 | 19 | - | - | 19 | 38-9/16 x 30-1/8 x 22-1/16 | 419 | 19.6 / 15.4 | 30.8 / 25.4 | 6.27 / 5.8 |  | 25.7 / 21.3 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-10 | RWEQ120TATJA | 10 | 1 | 208V - 230V 3ph | 36.5 | - | - | 36.5 | 45 | - | - | 45 | 20.9 | - | - | 20.9 | 38-9/16 x 30-1/8 x 22-1/16 | 423 | 16.0 / 13.6 | 29.4 / 23.5 | 6.1 / 5.55 |  | 26.3 / 22.5 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-12 | RWEQ144TATJA | 12 | 2 | 208V - 230V 3ph | 44.6 | - | - | 44.6 | 50 | - | - | 50 | 29.4 | - | - | 29.4 | 38-9/16 x 30-1/8 x 22-1/16 | 423 | 15.6 / 12.6 | 24.3 / 19.8 | 6.01 / 5.33 |  | 26.5 / 22.7 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-16 | RWEQ192TATJA | 16 | 2 | 208V - 230V 3ph | 28.8 | 28.8 | - | 57.6 | 35 | 35 | - | 70 | 19 | 19 | - | 38 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 838 | 16.5 / 14.6 | 26.8 / 24.7 | 5.82 / 5.82 |  | 26.0 / 22.9 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-18 | RWEQ216TATJA | 18 | 2 | 208V - 230V 3ph | 28.8 | 36.5 | - | 65.3 | 35 | 45 | - | 80 | 19 | 20.9 | - | 39.9 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 842 | 15.0 / 13.8 | 26.3 / 23.8 | 5.68 / 5.68 |  | 25.5 / 22.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-20 | RWEQ240TATJA | 20 | 2 | 208V - 230V 3ph | 36.5 | 36.5 | - | 73 | 45 | 45 | - | 90 | 20.9 | 20.9 | - | 41.8 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 846 | 14.0 / 12.8 | 25.7 / 22.7 | 5.52 / 5.49 |  | 25.4 / 21.9 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-22 | RWEQ264TATJA | 22 | 2 | 208V - 230V 3ph | 36.5 | 44.6 | - | 81.1 | 45 | 50 | - | 95 | 20.9 | 29.4 | - | 50.3 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 846 | 13.5 / 12.1 | 23.5 / 20.0 | 5.34 / 4.98 |  | 25.2 / 19.2 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-24 | RWEQ288TATJA | 24 | 2 | 208V - 230V 3ph | 44.6 | 44.6 | - | 89.2 | 50 | 50 | - | 100 | 29.4 | 29.4 | - | 58.8 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 846 | 13.1 / 11.5 | 20.9 / 18.8 | 5.3 / 4.92 |  | 23.5 / 20.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-26 | RWEQ312TATJA | 26 | 3 | 208V - 230V 3ph | 28.8 | 28.8 | 36.5 | 57.6 | 35 | 35 | 45 | 115 | 19 | 19 | 20.9 | 38 | 38-9/16 x 30-1/8 x 22-1/16 | 1261 | 13.7 / 12.7 | 21.9 / 21.8 | 5.5 / 4.86 |  | 24.5 / 20.7 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-28 | RWEQ336TATJA | 28 | 3 | 208V - 230V 3ph | 28.8 | 36.5 | 36.5 | 65.3 | 35 | 45 | 45 | 125 | 19 | 20.9 | 20.9 | 39.9 | 38-9/16 x 30-1/8 x 22-1/16 | 1265 | 13.5 / 12.3 | 21.5 / 21.4 | 5.42 / 4.73 |  | 23.5 / 20.0 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-30 | RWEQ360TATJA | 30 | 3 | 208V - 230V 3ph | 36.5 | 36.5 | 36.5 | 73 | 45 | 45 | 45 | 135 | 20.9 | 20.9 | 20.9 | 41.8 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 12.4 / 11.7 | 21.2 / 20.2 | 5.3 / 4.7 |  | 23.2 / 19.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-32 | RWEQ384TATJA | 32 | 3 | 208V - 230V 3ph | 36.5 | 36.5 | 44.6 | 73 | 45 | 45 | 50 | 140 | 20.9 | 20.9 | 29.4 | 41.8 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 12.0 / 11.0 | 19.5 / 17.9 | 4.53 / 4.12 |  | 22.0 / 19.1 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-34 | RWEQ408TATJA | 34 | 3 | 208V - 230V 3ph | 36.5 | 44.6 | 44.6 | 81.1 | 45 | 50 | 50 | 145 | 20.9 | 29.4 | 29.4 | 50.3 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 11.1 / 10.7 | 18.2 / 17.2 | 4.35 / 4.03 |  | 21.2 / 18.5 | n/a / n/a | n/a / n/a
|  |  |  | 208-W-T-HR-36 | RWEQ432TATJA | 36 | 3 | 208V - 230V 3ph | 44.6 | 44.6 | 44.6 | 89.2 | 50 | 50 | 50 | 150 | 29.4 | 29.4 | 29.4 | 58.8 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 10.5 / 10.3 | 17.0 / 16.6 | 4.19 / 3.92 |  | 20.5 / 17.7 | n/a / n/a | n/a / n/a
HEAT RECOVERY SYSTEM - 460V | VRV OUTDOOR UNITS
| AIR or WATER | FAMILY | HEAT RECOVERY | TAG | MODEL | NOMINAL TONNAGE | MODULES (Tonnage Combo's) | ELECTRICAL | [12 empty] | DIMENSIONS |  | EFFICIENCY (NonDucted/Ducted or Specific Combo) | [6 empty] | NOTES
[8 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
[9 empty] | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | (WxHxD) (inch) | WEIGHT (lbs) | EER | IEER | COP47 | COP17 | SCHE | SEER | HSPF
| AIR COOLED | IV-X | HEAT RECOVERY | 460-A-X-HR-6 | REYQ72XAYB | 6 | 1 | 460V 3ph | 18.9 | - | - | 18.9 | 25 | - | - | 25 | 9.4 | - | - | 9.4 | 66-11/16 x 48-7/8 x 30-3/16 | 727 | 15.8 / 13.9 | 25.2 / 21.3 | 4.3 / 3.7 | 2.5 / 2.3 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  |  | 460-A-X-HR-8 | REYQ96XAYDB | 8 | 1 | 460V 3ph | 21.1 | - | - | 21.1 | 25 | - | - | 25 | 10.5 | - | - | 10.5 | 66-11/16 x 48-7/8 x 30-3/16 | 727 | 14.6 / 12.5 | 27.8 / 21.9 | 4.2 / 3.6 | 2.6 / 2.3 | 26.4 / 21.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-10 | REYQ120XAYDB | 10 | 1 | 460V 3ph | 21.1 | - | - | 21.1 | 25 | - | - | 25 | 12.8 | - | - | 12.8 | 66-11/16 x 48-7/8 x 30-3/16 | 727 | 13.2 / 12.3 | 25.5 / 22.6 | 3.8 / 3.5 | 2.5 / 2.3 | 26.0 / 22.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-12 | REYQ144XAYDB | 12 | 1 | 460V 3ph | 27.9 | - | - | 27.9 | 40 | - | - | 40 | 19.3 | - | - | 19.3 | 66-11/16 x 48-7/8 x 30-3/16 | 793 | 11.9 / 11.6 | 23.5 / 21.6 | 3.8 / 3.4 | 2.2 / 2.1 | 25.5 / 22.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-14 | REYQ168XAYDB | 14 | 1 | 460V 3ph | 31.1 | - | - | 31.1 | 40 | - | - | 40 | 22.2 | - | - | 22.2 | 66-11/16 x 48-7/8 x 30-3/16 | 793 | 10.8 / 10.7 | 22.3 / 20.4 | 3.6 / 3.3 | 2.1 / 2.1 | 25.5 / 22.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-16 | REYQ192XAYDB | 16 | 2 | 460V 3ph | 21.1 | 21.1 | - | 42.2 | 25 | 25 | - | 25 | 11.2 | 11.2 | - | 22.4 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1454 | 13.0 / 13.0 | 22.6 / 21.4 | 3.9 / 3.7 | 2.5 / 2.4 | 26.6 / 22.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-18 | REYQ216XAYDB | 18 | 2 | 460V 3ph | 21.1 | 21.1 | - | 42.2 | 25 | 25 | - | 25 | 12.9 | 12.9 | - | 25.8 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1454 | 12.4 / 12.3 | 23.1 / 21.7 | 3.8 / 3.5 | 2.3 / 2.2 | 25.5 / 21.9 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-20 | REYQ240XAYDB | 20 | 2 | 460V 3ph | 21.1 | 21.1 | - | 42.2 | 25 | 25 | - | 25 | 13.5 | 13.5 | - | 27 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1454 | 11.6 / 11.7 | 22.2 / 20.0 | 3.7 / 3.4 | 2.3 / 2.2 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-22 | REYQ264XAYDB | 22 | 2 | 460V 3ph | 21.1 | 27.9 | - | 49 | 25 | 40 | - | 25 | 14.9 | 14.9 | - | 29.8 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1520 | 11.2 / 10.4 | 21.6 / 18.0 | 3.6 / 3.2 | 2.2 / 2.1 | 26.1 / 18.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-24 | REYQ288XAYDB | 24 | 2 | 460V 3ph | 27.9 | 27.9 | - | 55.8 | 40 | 40 | - | 40 | 19.7 | 19.7 | - | 39.4 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1586 | 11.0 / 10.3 | 21.0 / 17.9 | 3.5 / 3.2 | 2.2 / 2.1 | 23.3 / 19.9 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-26 | REYQ312XAYDB | 26 | 2 | 460V 3ph | 27.9 | 31.1 | - | 59 | 40 | 40 | - | 40 | 21 | 21 | - | 42 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1586 | 10.1 / 9.9 | 20.4 / 18.0 | 3.6 / 3.2 | 2.1 / 2.1 | 24.3 / 20.7 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-28 | REYQ336XAYDB | 28 | 2 | 460V 3ph | 31.1 | 31.1 | - | 62.2 | 40 | 40 | - | 40 | 22.7 | 22.7 | - | 45.4 | (2) 66-11/16 x 48-7/8 x 30-3/16 | 1586 | 9.9 / 9.5 | 20.0 / 17.3 | 3.5 / 3.2 | 2.1 / 2.1 | 23.3 / 19.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-30 | REYQ360XAYDB | 30 | 3 | 460V 3ph | 21.1 | 21.1 | 21.1 | 63.3 | 25 | 25 | 25 | 75 | 14.8 | 14.8 | 14.8 | 44.4 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2181 | 10.9 / 10.6 | 20.0 / 18.8 | 3.6 / 3.2 | 2.3 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-32 | REYQ384XAYDB | 32 | 3 | 460V 3ph | 21.1 | 21.1 | 27.9 | 70.1 | 25 | 25 | 40 | 90 | 15.3 | 15.3 | 19.8 | 50.4 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2247 | 9.7 / 9.9 | 19.0 / 17.6 | 3.2 / 3.2 | 2.2 / 2.1 | 21.9 / 17.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-34 | REYQ408XAYDB | 34 | 3 | 460V 3ph | 21.1 | 27.9 | 27.9 | 76.9 | 25 | 40 | 40 | 105 | 16.2 | 20.4 | 20.4 | 57 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2313 | 9.8 / 9.7 | 17.2 / 17.7 | 3.2 / 3.2 | 2.1 / 2.1 | 21.8 / 18.3 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-36 | REYQ432XAYDB | 36 | 3 | 460V 3ph | 27.9 | 27.9 | 27.9 | 83.7 | 40 | 40 | 40 | 120 | 20.4 | 20.4 | 20.4 | 61.2 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2379 | 9.8 / 9.7 | 16.2 / 17.3 | 3.2 / 3.2 | 2.1 / 2.1 | 20.2 / 18.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-X-HR-38 | REYQ456XAYDB | 38 | 3 | 460V 3ph | 27.9 | 27.9 | 31.1 | 86.9 | 40 | 40 | 40 | 120 | 21.3 | 21.3 | 21.3 | 63.9 | (3) 66-11/16 x 48-7/8 x 30-3/16 | 2379 | 9.3 / 9.5 | 16.2 / 16.7 | 3.2 / 3.2 | 2.1 / 2.1 | 18.8 / 17.9 | n/a / n/a | n/a / n/a
| AIR COOLED | EMERION | HEAT RECOVERY | 460-A-E-HR-6 | REYQ72AATDA | 6 | 1 | 460V 3ph | 12.4 | - | - | 12.4 | 15 | - | - | 15 | 5.1 | - | - | 5.1 | 36.7 x 65.4 x 30.1 | 509 | 15.7 / 12.8 | 28.0 / 23.0 | 4.4 / 3.6 | 2.5 / 2.4 | 26.1 / 22.0 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -13 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  |  | 460-A-E-HR-8 | REYQ96AATDA | 8 | 1 | 460V 3ph | 16.4 | - | - | 16.4 | 20 | - | - | 20 | 6.9 | - | - | 6.9 | 48.8 x 65.4 x 30.1 | 710 | 14.6 / 12.8 | 30.0 / 25.3 | 4.3 / 3.6 | 2.5 / 2.3 | 26.1 / 21.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-10 | REYQ120AATDA | 10 | 1 | 460V 3ph | 16.6 | - | - | 16.6 | 20 | - | - | 20 | 9.6 | - | - | 9.6 | 48.8 x 65.4 x 30.1 | 712 | 13.2 / 12.4 | 27.5 / 23.5 | 4.0 / 3.5 | 2.4 / 2.3 | 26.1 / 22.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-12 | REYQ144AATDA | 12 | 1 | 460V 3ph | 21.3 | - | - | 21.3 | 25 | - | - | 25 | 11.7 | - | - | 11.7 | 48.8 x 65.4 x 30.1 | 785 | 12.5 / 12.0 | 26.5 / 22.5 | 3.8 / 3.4 | 2.2 / 2.1 | 25.6 / 22.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-14 | REYQ168AATDA | 14 | 1 | 460V 3ph | 24.9 | - | - | 24.9 | 30 | - | - | 30 | 14.8 | - | - | 14.8 | 48.8 x 65.4 x 30.1 | 787 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-16 | REYQ192AATDA | 16 | 1 | 460V 3ph | 28.3 | - | - | 28.3 | 35 | - | - | 35 | 15.1 | - | - | 15.1 | 68.9 x 65.4 x 30.1 | 957 | 12.3 / 11.5 | 24.0 / 21.0 | 3.9 / 3.5 | 2.1 / 2.1 | 26.6 / 22.80 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-18 | REYQ216AATDA | 18 | 1 | 460V 3ph | 29.9 | - | - | 29.9 | 35 | - | - | 35 | 18.2 | - | - | 18.2 | 68.9 x 65.4 x 30.1 | 957 | 11.5 / 11.1 | 24.0 / 21.4 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 22.3 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-20 | REYQ240AATDA | 20 | 1 | 460V 3ph | 33.4 | - | - | 33.4 | 40 | - | - | 40 | 22.1 | - | - | 22.1 | 68.9 x 65.4 x 30.1 | 957 | 11.0 / 10.8 | 21.6 / 19.7 | 3.5 / 3.2 | 2.1 / 2.1 | 25.6 / 21.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-22 | REYQ264AATDA | 22 | 2 (12+10) | 460V 3ph | 16.6 | 21.3 | - | 37.9 | 20 | 25 | - | 45 | 9.6 | 11.7 | - | 21.3 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1497 | 12.0 / 10.6 | 23.9 / 19.2 | 3.7 / 3.2 | 2.4 / 2.1 | 26.2 / 18.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-24 | REYQ288AATDA | 24 | 2 (12+12) | 460V 3ph | 21.3 | 21.3 | - | 42.6 | 25 | 25 | - | 50 | 11.7 | 11.7 | - | 23.4 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1570 | 12.0 / 11.0 | 23.2 / 19.3 | 3.6 / 3.3 | 2.4 / 2.1 | 23.4 / 20.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-26 | REYQ312AATDA | 26 | 2 (14+12) | 460V 3ph | 21.3 | 24.9 | - | 46.2 | 25 | 30 | - | 55 | 11.7 | 14.8 | - | 26.5 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1572 | 11.3 / 10.8 | 22.8 / 19.2 | 3.6 / 3.3 | 2.4 / 2.1 | 24.4 / 20.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-28 | REYQ336AATDA | 28 | 2 (14+14) | 460V 3ph | 24.9 | 24.9 | - | 49.8 | 30 | 30 | - | 60 | 14.8 | 14.8 | - | 29.6 | 48.8 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1574 | 10.5 / 10.6 | 22.1 / 18.6 | 3.6 / 3.2 | 2.2 / 2.1 | 23.4 / 19.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-30 | REYQ360AATDA | 30 | 2 (16+14) | 460V 3ph | 24.9 | 28.3 | - | 53.2 | 30 | 35 | - | 65 | 14.8 | 15.1 | - | 29.9 | 68.9 x 65.4 x 30.1 + 48.8 x 65.4 x 30.1 | 1744 | 11.5 / 10.7 | 21.0 / 18.2 | 3.6 / 3.2 | 2.1 / 2.1 | 23.0 / 19.4 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-32 | REYQ384AATDA | 32 | 2 (16+16) | 460V 3ph | 28.3 | 28.3 | - | 56.6 | 35 | 35 | - | 70 | 15.1 | 15.1 | - | 30.2 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 10.7 / 10.5 | 22.0 / 18.8 | 3.4 / 3.3 | 2.1 / 2.1 | 22.0 / 17.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-34 | REYQ408AATDA | 34 | 2 (18+16) | 460V 3ph | 28.3 | 29.9 | - | 58.2 | 35 | 35 | - | 70 | 15.1 | 18.2 | - | 33.3 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 10.7 / 10.5 | 21.5 / 18.4 | 3.4 / 3.3 | 2.1 / 2.1 | 21.9 / 18.4 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-36 | REYQ432AATDA | 36 | 2 (18+18) | 460V 3ph | 29.9 | 29.9 | - | 59.8 | 35 | 35 | - | 70 | 18.2 | 18.2 | - | 36.4 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 10.7 / 10.1 | 21.1 / 18.1 | 3.4 / 3.3 | 2.1 / 2.1 | 20.3 / 18.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-38 | REYQ456AATDA | 38 | 2 (20+18) | 460V 3ph | 29.9 | 33.4 | - | 63.3 | 35 | 40 | - | 75 | 18.2 | 22.1 | - | 40.3 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 9.9 / 9.8 | 20.2 / 17.5 | 3.4 / 3.3 | 2.1 / 2.1 | 18.9 / 18.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-E-HR-40 | REYQ480AATDA | 40 | 2 (20+20) | 460V 3ph | 33.4 | 33.4 | - | 66.8 | 40 | 40 | - | 80 | 22.1 | 22.1 | - | 44.2 | 68.9 x 65.4 x 30.1 + 68.9 x 65.4 x 30.1 | 1914 | 9.7 / 9.6 | 19.4 / 17.2 | 3.4 / 3.3 | 2.1 / 2.1 | 16.9 / 16.5 | n/a / n/a | n/a / n/a
| AIR COOLED | AURORA | HEAT RECOVERY | 460-A-A-HR-6 | RELQ72TBYDA | 6 | 1 | 460V 3ph | 28.1 | - | - | 28.1 | 35 | - | - | 35 | 9.4 | - | - | 9.4 | 66-11/16 X 48-7/8 X 30-3/16 | 727 | 15.8 / 13.7 | 24.0 / 20.8 | 4.30 / 3.68 | 2.3 / 2.4 | 26.1 / 22.6 | n/a / n/a | n/a / n/a | ~ Heating operation range down to -22 F ~ Cooling operation down to -4 F with Technical Cooling
|  |  |  | 460-A-A-HR-8 | RELQ96TBYDA | 8 | 1 | 460V 3ph | 39.8 | - | - | 39.8 | 45 | - | - | 45 | 16.6 | - | - | 16.6 | 66-11/16 X 48-7/8 X 30-3/16 | 793 | 15.3 / 12.5 | 24.8 / 19.1 | 4.23 / 3.42 | 2.25 / 2.37 | 25.7 / 19.7 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-A-HR-10 | RELQ120TBYDA | 10 | 1 | 460V 3ph | 43.4 | - | - | 43.4 | 50 | - | - | 50 | 17.8 | - | - | 17.8 | 66-11/16 X 48-7/8 X 30-3/16 | 793 | 13.7 / 12.4 | 23.4 / 19.6 | 3.98 / 3.51 | 2.25 / 2.25 | 26.7 / 21.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-A-HR-12 | RELQ144TAYDA | 12 | 2 (6+6) | 460V 3ph | 28.1 | 28.1 | - | 56.2 | 35 | 35 | - | 70 | 9.8 | 9.8 | - | 19.6 | 66-11/16 X 48-7/8 X 30-3/16 + 66-11/16 X 48-7/8 X 30-3/16 | 1454 | 12.9 / 12.6 | 22.5 / 18.6 | 3.81 / 3.55 | 2.20 / 2.20 | 25.5 / 23.8 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-A-HR-16 | RELQ192TAYDA | 16 | 2 (8+8) | 460V 3ph | 39.8 | 39.8 | - | 79.6 | 45 | 45 | - | 90 | 17.3 | 17.3 | - | 34.6 | 66-11/16 X 48-7/8 X 30-3/16 + 66-11/16 X 48-7/8 X 30-3/17 | 1586 | 12.5 / 12.7 | 22.1 / 19.0 | 3.85 / 3.57 | 2.15 / 2.17 | 25.5 / 21.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-A-A-HR-20 | RELQ240TAYDA | 20 | 2 (10+10) | 460V 3ph | 43.4 | 43.4 | - | 86.8 | 50 | 50 | - | 100 | 18.3 | 18.3 | - | 36.6 | 66-11/16 X 48-7/8 X 30-3/16 + 66-11/16 X 48-7/8 X 30-3/18 | 1586 | 12.3 / 11.7 | 21.1 / 18.6 | 3.68 / 3.49 | 2.13 / 2.16 | 24.9 / 20.8 | n/a / n/a | n/a / n/a
| WATER COOLED | T SERIES | HEAT RECOVERY | 460-W-T-HR-6 | RWEYQ72PCYD | 6 | 1 | 460V 3ph | 10.2 | - | - | 10.2 | 15 | - | - | 15 | 5.3 | - | - | 5.3 | 39-3/8 x 30-3/4 x 21-11/16 | 330 | 14.0 / 14.0 | 24.1 / 22.3 | 4.89 / 4.78 | Note: the values to the left are COP at 68 degrees. | 17.8 / 19.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-8 | RWEQ96TAYDA | 8 | 1 | 460V 3ph | 13 | - | - | 13 | 15 | - | - | 15 | 8.6 | - | - | 8.6 | 38-9/16 x 30-1/8 x 22-1/16 | 419 | 19.6 / 15.4 | 30.8 / 25.4 | 6.27 / 5.8 |  | 25.7 / 21.3 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-10 | RWEQ120TAYDA | 10 | 1 | 460V 3ph | 16.5 | - | - | 16.5 | 20 | - | - | 20 | 9.4 | - | - | 9.4 | 38-9/16 x 30-1/8 x 22-1/16 | 423 | 16.0 / 13.6 | 29.4 / 23.5 | 6.1 / 5.55 |  | 26.3 / 22.5 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-12 | RWEQ144TAYDA | 12 | 2 | 460V 3ph | 20.2 | - | - | 20.2 | 25 | - | - | 25 | 13.3 | - | - | 13.3 | 38-9/16 x 30-1/8 x 22-1/16 | 423 | 15.6 / 12.6 | 24.3 / 19.8 | 6.01 / 5.33 |  | 26.5 / 22.7 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-16 | RWEQ192TAYDA | 16 | 2 | 460V 3ph | 13 | 13 | - | 26 | 15 | 15 | - | 30 | 8.6 | 8.6 | - | 17.2 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 838 | 16.5 / 14.6 | 26.8 / 24.7 | 5.82 / 5.82 |  | 26.0 / 22.9 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-18 | RWEQ216TAYDA | 18 | 2 | 460V 3ph | 13 | 16.5 | - | 29.5 | 15 | 20 | - | 35 | 8.6 | 9.4 | - | 18 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 842 | 15.0 / 13.8 | 26.3 / 23.8 | 5.68 / 5.68 |  | 25.5 / 22.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-20 | RWEQ240TAYDA | 20 | 2 | 460V 3ph | 16.5 | 16.5 | - | 33 | 20 | 20 | - | 40 | 9.4 | 9.4 | - | 18.8 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 846 | 14.0 / 12.8 | 25.7 / 22.7 | 5.52 / 5.49 |  | 25.4 / 21.9 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-22 | RWEQ264TAYDA | 22 | 2 | 460V 3ph | 16.5 | 20.2 | - | 36.7 | 20 | 25 | - | 45 | 9.4 | 13.3 | - | 22.7 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 846 | 13.5 / 12.1 | 23.5 / 20.0 | 5.34 / 4.98 |  | 25.2 / 19.2 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-24 | RWEQ288TAYDA | 24 | 2 | 460V 3ph | 20.2 | 20.2 | - | 40.4 | 25 | 25 | - | 50 | 13.3 | 13.3 | - | 26.6 | 38-9/16 x (30-1/8 x 2) x 22-1/16 | 846 | 13.1 / 11.5 | 20.9 / 18.8 | 5.3 / 4.92 |  | 23.5 / 20.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-26 | RWEQ312TAYDA | 26 | 3 | 460V 3ph | 13 | 13 | 16.5 | 26 | 15 | 15 | 20 | 50 | 8.6 | 8.6 | 9.4 | 17.2 | 38-9/16 x 30-1/8 x 22-1/16 | 1261 | 13.7 / 12.7 | 21.9 / 21.8 | 5.5 / 4.86 |  | 24.5 / 20.7 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-28 | RWEQ336TAYDA | 28 | 3 | 460V 3ph | 13 | 16.5 | 16.5 | 29.5 | 15 | 20 | 20 | 55 | 8.6 | 9.4 | 9.4 | 18 | 38-9/16 x 30-1/8 x 22-1/16 | 1265 | 13.5 / 12.3 | 21.5 / 21.4 | 5.42 / 4.73 |  | 23.5 / 20.0 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-30 | RWEQ360TAYDA | 30 | 3 | 460V 3ph | 16.5 | 16.5 | 16.5 | 33 | 20 | 20 | 20 | 60 | 9.4 | 9.4 | 9.4 | 18.8 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 12.4 / 11.7 | 21.2 / 20.2 | 5.3 / 4.7 |  | 23.2 / 19.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-32 | RWEQ384TAYDA | 32 | 3 | 460V 3ph | 16.5 | 16.5 | 20.2 | 33 | 20 | 20 | 25 | 65 | 9.4 | 9.4 | 13.3 | 18.8 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 12.0 / 11.0 | 19.5 / 17.9 | 4.53 / 4.12 |  | 22.0 / 19.1 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-34 | RWEQ408TAYDA | 34 | 3 | 460V 3ph | 16.5 | 20.2 | 20.2 | 36.7 | 20 | 25 | 25 | 70 | 9.4 | 13.3 | 13.3 | 22.7 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 11.1 / 10.7 | 18.2 / 17.2 | 4.35 / 4.03 |  | 21.2 / 18.5 | n/a / n/a | n/a / n/a
|  |  |  | 460-W-T-HR-36 | RWEQ432TAYDA | 36 | 3 | 460V 3ph | 20.2 | 20.2 | 20.2 | 40.4 | 25 | 25 | 25 | 75 | 13.3 | 13.3 | 13.3 | 26.6 | 38-9/16 x 30-1/8 x 22-1/16 | 1269 | 10.5 / 10.3 | 17.0 / 16.6 | 4.19 / 3.92 |  | 20.5 / 17.7 | n/a / n/a | n/a / n/a
HEAT PUMP SYTEM - 208V | VRV OUTDOOR UNITS
| AIR or WATER | FAMILY | HEAT PUMP | TAG | MODEL | NOMINAL TONNAGE | MODULES (Tonnage Combo's) | ELECTRICAL | [12 empty] | DIMENSIONS |  | EFFICIENCY (NonDucted/Ducted or Specific Combo) | [6 empty] | NOTES
[8 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
[9 empty] | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | (WxHxD) (inch) | WEIGHT (lbs) | EER | IEER | COP47 | COP17 | SCHE | SEER | HSPF
| AIR COOLED | IV-X | HEAT PUMP | 208-A-X-HP-6 | RXYQ72AATJB | 6 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-8 | RXYQ96AATJB | 8 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-10 | RXYQ120AATJB | 10 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-12 | RXYQ144AATJB | 12 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-14 | RXYQ168AATJB | 14 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-16 | RXYQ192AATJB | 16 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-18 | RXYQ216AATJB | 18 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-20 | RXYQ240AATJB | 20 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-22 | RXYQ264AATJB | 22 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-24 | RXYQ288AATJB | 24 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-26 | RXYQ312AATJB | 26 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-28 | RXYQ336AATJB | 28 | 2 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-30 | RXYQ360AATJB | 30 | 3 | 208V - 230V 3ph
|  |  |  | 208-A-X-HP-32 | RXYQ384AATJB | 32 | 3 | 208V - 230V 3ph
| AIR COOLED | EMERION | HEAT PUMP | 208-A-E-HP-6 | RXYQ72AATJB | 6 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-8 | RXYQ96AATJB | 8 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-10 | RXYQ120AATJB | 10 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-12 | RXYQ144AATJB | 12 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-14 | RXYQ168AATJB | 14 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-16 | RXYQ192AATJB | 16 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-18 | RXYQ216AATJB | 18 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-20 | RXYQ240AATJB | 20 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-22 | RXYQ264AATJB | 22 | 2 (12+10) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-24 | RXYQ288AATJB | 24 | 2 (12+12) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-26 | RXYQ312AATJB | 26 | 2 (14+12) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-28 | RXYQ336AATJB | 28 | 2 (14+14) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-30 | RXYQ360AATJB | 30 | 2 (16+14) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-32 | RXYQ384AATJB | 32 | 2 (16+16) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-34 | RXYQ408AATJB | 34 | 2 (18+16) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-36 | RXYQ432AATJB | 36 | 2 (18+18) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-38 | RXYQ456AATJB | 38 | 2 (20+18) | 208V - 230V 3ph
|  |  |  | 208-A-E-HP-40 | RXYQ480AATJB | 40 | 2 (20+20) | 208V - 230V 3ph
| AIR COOLED | AURORA | HEAT PUMP | 208-A-A-HP-6 | RXLQ72TBTJA | 6 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-A-HP-8 | RXLQ96TBTJA | 8 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-A-HP-10 | RXLQ120TBTJA | 10 | 1 | 208V - 230V 3ph
|  |  |  | 208-A-A-HP-12 | RXLQ144TBTJA | 12 | 2 (6+6) | 208V - 230V 3ph
|  |  |  | 208-A-A-HP-16 | RXLQ192TBTJA | 16 | 2 (8+8) | 208V - 230V 3ph
|  |  |  | 208-A-A-HP-20 | RXLQ240TBTJA | 20 | 2 (10+10) | 208V - 230V 3ph
| WATER COOLED | T SERIES | HEAT PUMP | 208-W-T-HP-6 | RWEQ72TBTJA | 6 | 1 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-8 | RWEQ96TBTJA | 8 | 1 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-10 | RWEQ120TBTJA | 10 | 1 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-12 | RWEQ144TBTJA | 12 | 2 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-16 | RWEQ196TBTJA | 16 | 2 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-18 | RWEQ216TBTJA | 18 | 2 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-20 | RWEQ240TBTJA | 20 | 2 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-22 | RWEQ264TBTJA | 22 | 2 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-24 | RWEQ288TBTJA | 24 | 2 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-26 | RWEQ312TBTJA | 26 | 3 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-28 | RWEQ336TBTJA | 28 | 3 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-30 | RWEQ360TBTJA | 30 | 3 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-32 | RWEQ388TBTJA | 32 | 3 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-34 | RWEE408TBTJA | 34 | 3 | 208V - 230V 3ph
|  |  |  | 208-W-T-HP-36 | RWEQ432TBTJA | 36 | 3 | 208V - 230V 3ph
HEAT PUMP SYTEM - 406V | VRV OUTDOOR UNITS
| AIR or WATER | FAMILY | HEAT PUMP | TAG | MODEL | NOMINAL TONNAGE | MODULES (Tonnage Combo's) | ELECTRICAL | [12 empty] | DIMENSIONS |  | EFFICIENCY (NonDucted/Ducted or Specific Combo) | [6 empty] | NOTES
[8 empty] | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) |  |  |  | MAX OVERCURRENT PROTECTION (MOP) |  |  |  | RUNNING CURRENT(RLA)
[9 empty] | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | mod #1 | mod #2 | mod #3 | TOTAL | (WxHxD) (inch) | WEIGHT (lbs) | EER | IEER | COP47 | COP17 | SCHE | SEER | HSPF
| AIR COOLED | IV-X | HEAT PUMP | 460-A-X-HP-6 | RXYQ72AAYDA | 6 | 1 | 460V 3ph
|  |  |  | 460-A-X-HP-8 | RXYQ96AAYDA | 8 | 1 | 460V 3ph
|  |  |  | 460-A-X-HP-10 | RXYQ120AAYDA | 10 | 1 | 460V 3ph
|  |  |  | 460-A-X-HP-12 | RXYQ144AAYDA | 12 | 1 | 460V 3ph
|  |  |  | 460-A-X-HP-14 | RXYQ168AAYDA | 14 | 1 | 460V 3ph
|  |  |  | 460-A-X-HP-16 | RXYQ192AAYDA | 16 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-18 | RXYQ196AAYDA | 18 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-20 | RXYQ240AAYDA | 20 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-22 | RXYQ264AAYDA | 22 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-24 | RXYQ288AAYDA | 24 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-26 | RXYQ312AAYDA | 26 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-28 | RXYQ336AAYDA | 28 | 2 | 460V 3ph
|  |  |  | 460-A-X-HP-30 | RXYQ360AAYDA | 30 | 3 | 460V 3ph
|  |  |  | 460-A-X-HP-32 | RXYQ384AAYDA | 32 | 3 | 460V 3ph
|  |  |  | 460-A-X-HP-34 | RXYQ408AAYDA | 34 | 3 | 460V 3ph
|  |  |  | 460-A-X-HP-36 | RXYQ432AAYDA | 36 | 3 | 460V 3ph
|  |  |  | 460-A-X-HP-38 | RXYQ456AAYDA | 38 | 3 | 460V 3ph
| AIR COOLED | EMERION | HEAT PUMP | 460-A-E-HP-6 | RXYQ72AATJB | 6 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-8 | RXYQ96AATJB | 8 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-10 | RXYQ120AATDA | 10 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-12 | RXYQ144AATDA | 12 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-14 | RXYQ168AATDA | 14 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-16 | RXYQ192AATDA | 16 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-18 | RXYQ216AATDA | 18 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-20 | RXYQ240AATDA | 20 | 1 | 460V 3ph
|  |  |  | 460-A-E-HP-22 | RXYQ264AATDA | 22 | 2 (12+10) | 460V 3ph
|  |  |  | 460-A-E-HP-24 | RXYQ288AATDA | 24 | 2 (12+12) | 460V 3ph
|  |  |  | 460-A-E-HP-26 | RXYQ312AATDA | 26 | 2 (14+12) | 460V 3ph
|  |  |  | 460-A-E-HP-28 | RXYQ336AATDA | 28 | 2 (14+14) | 460V 3ph
|  |  |  | 460-A-E-HP-30 | RXYQ360AATDA | 30 | 2 (16+14) | 460V 3ph
|  |  |  | 460-A-E-HP-32 | RXYQ384AATDA | 32 | 2 (16+16) | 460V 3ph
|  |  |  | 460-A-E-HP-34 | RXYQ408AATDA | 34 | 2 (18+16) | 460V 3ph
|  |  |  | 460-A-E-HP-36 | RXYQ432AATDA | 36 | 2 (18+18) | 460V 3ph
|  |  |  | 460-A-E-HP-38 | RXYQ456AATDA | 38 | 2 (20+18) | 460V 3ph
|  |  |  | 460-A-E-HP-40 | RXYQ480AATDA | 40 | 2 (20+20) | 460V 3ph
| AIR COOLED | AURORA | HEAT PUMP | 460-A-A-HP-6 | RXLQ72TBYDA | 6 | 1 | 460V 3ph
|  |  |  | 460-A-A-HP-8 | RXLQ96TBYDA | 8 | 1 | 460V 3ph
|  |  |  | 460-A-A-HP-10 | RXLQ120TBYDA | 10 | 1 | 460V 3ph
|  |  |  | 460-A-A-HP-12 | RXLQ144TAYDA | 12 | 2 (6+6) | 460V 3ph
|  |  |  | 460-A-A-HP-14 | RXLQ192TAYDA | 16 | 2 (8+8) | 460V 3ph
|  |  |  | 460-A-A-HP-16 | RXLQ240TAYDA | 20 | 2 (10+10) | 460V 3ph
| WATER COOLED | T SERIES | HEAT PUMP | 460-W-T-HP-6 | RWEQ72TAYDA | 6 | 1 | 460V 3ph
|  |  |  | 460-W-T-HP-8 | RWEQ96TAYDA | 8 | 1 | 460V 3ph
|  |  |  | 460-W-T-HP-10 | RWEQ120TAYDA | 10 | 1 | 460V 3ph
|  |  |  | 460-W-T-HP-12 | RWEQ144TAYDA | 12 | 2 | 460V 3ph
|  |  |  | 460-W-T-HP-16 | RWEQ192TAYDA | 16 | 2 | 460V 3ph
|  |  |  | 460-W-T-HP-18 | RWEQ216TAYDA | 18 | 2 | 460V 3ph
|  |  |  | 460-W-T-HP-20 | RWEQ240TAYDA | 20 | 2 | 460V 3ph
|  |  |  | 460-W-T-HP-22 | RWEQ264TAYDA | 22 | 2 | 460V 3ph
|  |  |  | 460-W-T-HP-24 | RWEQ288TAYDA | 24 | 2 | 460V 3ph
|  |  |  | 460-W-T-HP-26 | RWEQ312TAYDA | 26 | 3 | 460V 3ph
|  |  |  | 460-W-T-HP-28 | RWEQ336TAYDA | 28 | 3 | 460V 3ph
|  |  |  | 460-W-T-HP-30 | RWEQ360TAYDA | 30 | 3 | 460V 3ph
|  |  |  | 460-W-T-HP-32 | RWEQ384TAYDA | 32 | 3 | 460V 3ph
|  |  |  | 460-W-T-HP-34 | RWEQ408TAYDA | 34 | 3 | 460V 3ph
|  |  |  | 460-W-T-HP-36 | RWEQ432TAYDA | 36 | 3 | 460V 3ph

## R410a BSB
DATE REVISED: AT/WN-MAR 2025
R410A | [5 empty] | NOTES: 1. To Include Service Ball Valves on both inlet and outlet ports 2. No condensate pump required
BSB | VRV - BSB's
| FAMILY | TAG | # PORTS | MODEL | VOLTAGE- PHASE | MIN CIRCUIT AMPS (MCA) | MAX OVERCURRENT PROTECTION (MOP) | MAX CAPACITY (per Port) | MAX CAPACITY (per Box) | DIMENSIONS (WxHxD inch) | WEIGHT (lbs) | NOTES
| Single Port | BS-1 | 1 | BSQ36TAVJ | 208-230V 1ph | 0.1 | 15 | 36000 | 36000 | 8-1/8 x 15-1/4 x 12-13/16 | 24
|  | BS-1 | 1 | BSQ60TAVJ | 208-230V 1ph | 0.1 | 15 | 60000 | 60000 | 8-1/8 x 15-1/4 x 12-13/16 | 24
|  | BS-1 | 1 | BSQ96TAVJ | 208-230V 1ph | 0.1 | 15 | 96000 | 96000 | 8-1/8 x 15-1/4 x 12-13/16 | 31
| Flex Series | BSF-4 | 4 | BSF4Q54TVJ | 208-230V 1ph | 0.4 | 15 | 54000 | 144000 | 9-1/2 x 13-3/4 x 23-3/4 | 49 | Capable of Left, Right, or Pass-through configurations. Can connect in parallel or series. Limited to 12 ports when connected in series.
|  | BSF-6 | 6 | BSF6Q54TVJ | 208-230V 1ph | 0.6 | 15 | 54000 | 216000 | 9-1/2 x 23-3/8 x 23-3/4 | 73
|  | BSF-8 | 8 | BSF8Q54TVJ | 208-230V 1ph | 0.8 | 15 | 54000 | 290000 | 9-1/2 x 23-3/8 x 23-3/4 | 81.6
| R410a Series | BS-4 | 4 | BS4Q54TAVJ | 208-230V 1ph | 0.4 | 15 | 54000 | 144000 | 11-3/4 x 14-9/16 x 18-15/16 | 49
|  | BS-10 | 10 | BS10Q54TAVJ | 208-230V 1ph | 1 | 15 | 54000 | 290000 | 11-3/4 x 32-5/16 x 18-15/16 | 101
|  | BS-12 | 12 | BS12Q54TAVJ | 208-230V 1ph | 1.2 | 15 | 54000 | 290000 | 11-3/4 x 32-5/16 x 18-15/16 | 106

## R410a IDU
DATE REVISED: AT/WN-MAR 2025
R410A |  |  |  | NOTES: 1. Standard Limited Warranty: 10-year warranty on compressor and all parts 2. 360 degree airflow distribution and three room sensors enables optimized occupant comfort and efficiency (FXFQ) 3. Optional self-cleaning filter panel to further increase efficiency and reduce maintenance costs (FXFQ) 4. Built-in condensate pump (FXDQ_M, FXFQ_P, FXFQ_T, FXMQ_M, FXMQ_P, FXUQ_P, FXZQ_M)
VARIABLE REFRIGERANT VOLUME - INDOOR UNIT SCHEDULE
| IMAGE | BASIS OF DESIGN (DAIKIN) | NOMINAL TONNAGE | TYPE | SUPPLY FAN | COOLING CAPACITY |  |  |  | HEATING CAPACITY |  | ELECTRICAL |  |  | DIMENSIONS | WEIGHT | NOTES | Options and Accessories
[5 empty] | AIR FLOW RATE cfm | TOTAL BTU/h | SENSIBLE BTU/h | ENTERING AIR |  | TOTAL BTU/h | ENTERING AIR °Fdb | Voltage - Phase | MCA | MOP | WxHxD | lbs
[8 empty] | °F DB | °F WB
DUCTED UNITS | #VALUE! | FXSQ05TBVJU | 0.5 | MSP Concealed Ducted Unit (Medium Static) | 281 | 5800 | 4060 | 80 | 66.7 | 6500 | 68 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55 |  | BRC1E73 (1)
|  | FXSQ07TBVJU | 0.6 |  | 281 | 7200 | 5040 | 80 | 66.7 | 8500 | 68 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55
|  | FXSQ09TBVJU | 0.75 |  | 318 | 9500 | 6650 | 80 | 66.7 | 10500 | 68 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55
|  | FXSQ12TBVJU | 1 |  | 335 | 12000 | 8400 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 0.8 | 15 | 21-11/16 x 9-11/16 x 31-1/2 | 55
|  | FXSQ15TBVJU | 1.25 |  | 530 | 15000 | 10500 | 80 | 66.7 | 17000 | 68 | 208-230V 1ph | 1.4 | 15 | 27-9/16 x 9-11/16 x 31-1/2 | 60
|  | FXSQ18TBVJU | 1.5 |  | 600 | 18000 | 12600 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 1.6 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 77
|  | FXSQ24TBVJU | 2 |  | 742 | 24000 | 16800 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 1.8 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 77
|  | FXSQ30TBVJU | 2.5 |  | 812 | 30000 | 21000 | 80 | 66.7 | 34000 | 68 | 208-230V 1ph | 1.8 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 82
|  | FXSQ36TBVJU | 3 |  | 1130 | 36000 | 25200 | 80 | 66.7 | 40000 | 68 | 208-230V 1ph | 2.5 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 101
|  | FXSQ48TBVJU | 4 |  | 1307 | 48000 | 33600 | 80 | 66.7 | 54000 | 68 | 208-230V 1ph | 2.8 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 104
|  | FXSQ54TBVJU | 4.5 |  | 1377 | 54000 | 37800 | 80 | 66.7 | 60000 | 68 | 208-230V 1ph | 3.3 | 15 | 61 x 9-11/16 x 31-1/2 | 115
| #VALUE! | FXMQ15TBVJU | 1.25 | HSP Concealed Ducted Unit (High Static 0.8") | 560 | 14200 | 9940 | 80 | 66.7 | 17000 | 68 | 208-230V 1ph | 1.8 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 77 |  | BRC1E73 (1)
|  | FXMQ18TBVJU | 1.5 |  | 635 | 18000 | 12600 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 1.9 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 77
|  | FXMQ24TBVJU | 2 |  | 742 | 24000 | 16800 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 1.9 | 15 | 39-3/8 x 9-11/16 x 31-1/2 | 82
|  | FXMQ30TBVJU | 2.5 |  | 1094 | 30000 | 21000 | 80 | 66.7 | 34000 | 68 | 208-230V 1ph | 3 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 101
|  | FXMQ36TBVJU | 3 |  | 1130 | 36000 | 25200 | 80 | 66.7 | 40000 | 68 | 208-230V 1ph | 3.1 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 101
|  | FXMQ48TBVJU | 4 |  | 1377 | 48000 | 33600 | 80 | 66.7 | 54000 | 68 | 208-230V 1ph | 3.6 | 15 | 55-1/8 x 9-11/16 x 31-1/2 | 104
|  | FXMQ54TBVJU | 4.5 |  | 1518 | 54000 | 37800 | 80 | 66.7 | 63000 | 68 | 208-230V 1ph | 3.6 | 15 | 61 x 9-11/16 x 31-1/2 | 115
| #VALUE! | FXTQ09TBVJUD | 0.75 | Multi Position Air Handler (Factory Disconnect) | 300 | 9500 | 6650 | 80 | 66.7 | 10500 | 68 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 108 |  | BRC1E73 (1)
|  | FXTQ12TBVJUD | 1 |  | 400 | 12000 | 8400 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 115
|  | FXTQ18TBVJUD | 1.5 |  | 600 | 18000 | 12600 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 118
|  | FXTQ24TBVJUD | 2 |  | 800 | 24000 | 16800 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 115
|  | FXTQ30TBVJUD | 2.5 |  | 1000 | 30000 | 21000 | 80 | 66.7 | 34000 | 68 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 116
|  | FXTQ36TBVJUD | 3 |  | 1050 | 36000 | 25200 | 80 | 66.7 | 40000 | 68 | 208-230V 1ph | 4.9 | 15 | 17-1/2 x 45 x 21 | 116
|  | FXTQ42TBVJUD | 3.5 |  | 1400 | 42000 | 29400 | 80 | 66.7 | 46000 | 68 | 208-230V 1ph | 6.5 | 15 | 21 x 53-1/2 x 21 | 147
|  | FXTQ48TBVJUD | 4 |  | 1520 | 48000 | 33600 | 80 | 66.7 | 54000 | 68 | 208-230V 1ph | 6.5 | 15 | 21 x 53-1/2 x 21 | 147
|  | FXTQ54TBVJUD | 4.5 |  | 1800 | 54000 | 37800 | 80 | 66.7 | 60000 | 68 | 208-230V 1ph | 8.6 | 15 | 21 x 58 x 24-1/2 | 168
|  | FXTQ60TBVJUD | 5 |  | 1800 | 60000 | 42000 | 80 | 66.7 | 66000 | 68 | 208-230V 1ph | 8.6 | 15 | 21 x 58 x 24-1/2 | 168
NON DUCTED UNITS | #VALUE! | FXAQ07PVJU | 0.6 | Wall Mounted Unit | 260 | 7500 | 5250 | 80 | 66.7 | 8500 | 68 | 208-230V 1ph | 0.4 | 15 | 31-1/4 x 11-3/8 x 9 | 26 |  | BRC1E73 (1)
|  | FXAQ09PVJU | 0.75 |  | 280 | 9500 | 6650 | 80 | 66.7 | 10500 | 68 | 208-230V 1ph | 0.4 | 15 | 31-1/4 x 11-3/8 x 9 | 26
|  | FXAQ12PVJU | 1 |  | 290 | 12000 | 8400 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 0.4 | 15 | 31-1/4 x 11-3/8 x 9 | 26
|  | FXAQ18PVJU | 1.5 |  | 500 | 18000 | 12600 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 0.5 | 15 | 41-3/8 x 11-3/8 x 9 | 31
|  | FXAQ24PVJU | 2 |  | 635 | 24000 | 16800 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 0.6 | 15 | 41-3/8 x 11-3/8 x 9 | 31
| #VALUE! | FXFQ07TVJU | 0.6 | Round Flow Sensing Cassette | 420 | 7500 | 6000 | 80 | 66.7 | 8500 | 68 | 208-230V 1ph | 0.3 | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42 |  | BRC1E73 (1), BYCQ125B-W1 (1)
|  | FXFQ09TVJU | 0.75 |  | 441 | 9500 | 7600 | 80 | 66.7 | 10500 | 68 | 208-230V 1ph | 0.3 | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFQ12TVJU | 1 |  | 441 | 12000 | 9600 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 0.3 | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFQ15TVJU | 1.25 |  | 512 | 15000 | 12000 | 80 | 66.7 | 17000 | 68 | 208-230V 1ph | 0.4 | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFQ18TVJU | 1.5 |  | 742 | 18000 | 14400 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 0.6 | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFQ24TVJU | 2 |  | 777 | 24000 | 19200 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 0.7 | 15 | 33-1/16 x 9-11/16 x 33-1/16 | 42
|  | FXFQ30TVJU | 2.5 |  | 1112 | 30000 | 24000 | 80 | 66.7 | 34000 | 68 | 208-230V 1ph | 1.3 | 15 | 33-1/16 x 11-11/32 x 33-1/16 | 58
|  | FXFQ36TVJU | 3 |  | 1165 | 36000 | 28800 | 80 | 66.7 | 40000 | 68 | 208-230V 1ph | 1.5 | 15 | 33-1/16 x 11-11/32 x 33-1/16 | 58
|  | FXFQ48TVJU | 4 |  | 1218 | 48000 | 38400 | 80 | 66.7 | 54000 | 68 | 208-230V 1ph | 1.8 | 15 | 33-1/16 x 11-11/32 x 33-1/16 | 58
| #VALUE! | FXZQ05TBVJU | 0.5 | 4-Way Discharge Ceiling Cassette Vista (2' x 2') white | 300 | 5800 | 4060 | 80 | 66.7 | 6500 | 68 | 208-230V 1ph | 0.3 | 15 | 10-1/4 x 22-5/8 x 22-5/8 | 40.4 |  | BRC1E73 (1), BYFQ60C3W2W (1)
|  | FXZQ07TBVJU | 0.6 |  | 307 | 7500 | 5250 | 80 | 66.7 | 8500 | 68 | 208-230V 1ph | 0.3 | 15 | 10-1/4 x 22-5/8 x 22-5/8 | 40.4
|  | FXZQ09TBVJU | 0.75 |  | 317 | 9500 | 6650 | 80 | 66.7 | 10500 | 68 | 208-230V 1ph | 0.3 | 15 | 10-1/4 x 22-5/8 x 22-5/8 | 40.4
|  | FXZQ12TBVJU | 1 |  | 353 | 12000 | 8400 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 0.4 | 15 | 10-1/4 x 22-5/8 x 22-5/8 | 42.6
|  | FXZQ15TBVJU | 1.25 |  | 405 | 15000 | 10500 | 80 | 66.7 | 17000 | 68 | 208-230V 1ph | 0.4 | 15 | 10-1/4 x 22-5/8 x 22-5/8 | 42.6
|  | FXZQ18TBVJU | 1.5 |  | 511 | 18000 | 12600 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 0.6 | 15 | 10-1/4 x 22-5/8 x 22-5/8 | 47
| #VALUE! | FXEQ07PVJU | 0.6 | Ceiling Mounted Cassette (Single Flow) | 212 | 7500 | 5250 | 80 | 66.7 | 8500 | 68 | 208-230V 1ph | 0.3 | 15 | 7-7∕8 x 18-½ x 33-1-1/16 | 38 |  | BRC1E73 (1), BYEP63AW1 (1)
|  | FXEQ09PVJU | 0.75 |  | 244 | 9500 | 6650 | 80 | 66.7 | 10500 | 68 | 208-230V 1ph | 0.4 | 15 | 7-7∕8 x 18-½ x 33-1-1/16 | 38
|  | FXEQ12PVJU | 1 |  | 283 | 12000 | 8400 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 0.4 | 15 | 7-7∕8 x 18-½ x 33-1-1/16 | 38
|  | FXEQ15PVJU | 1.25 |  | 346 | 15000 | 10500 | 80 | 66.7 | 17000 | 68 | 208-230V 1ph | 0.5 | 15 | 7-7∕8 x 18-½ x 33-1-1/16 | 40
|  | FXEQ18PVJU | 1.5 |  | 441 | 18000 | 12600 | 80 | 66.7 | 20000 | 68 | 208-230V 1ph | 0.5 | 15 | 7-7∕8 x 18-½ x 48-13/16 | 51
|  | FXEQ24PVJU | 2 |  | 597 | 24000 | 16800 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 0.7 | 15 | 7-7∕8 x 18-½ x 48-13/16 | 51
| #VALUE! | FXHQ12MVJU | 1 | Ceiling Suspended Unit | 410 | 12000 | 8400 | 80 | 66.7 | 13500 | 68 | 208-230V 1ph | 0.8 | 15 | 37-13/16 x 7-11/16 x 26-3/4 | 55 |  | BRC1E73 (1)
|  | FXHQ24MVJU | 2 |  | 710 | 24000 | 16800 | 80 | 66.7 | 27000 | 68 | 208-230V 1ph | 1 | 15 | 55-1/8 x 7-11/16 x 26-3/4 | 80
|  | FXHQ36MVJU | 3 |  | 830 | 36000 | 25200 | 80 | 66.7 | 40000 | 68 | 208-230V 1ph | 1.4 | 15 | 62-5/8 x 7-11/16 x 26-3/4 | 90