## Calculate Duct - Formulas (hidden)
Duct Calculators
6
VER 1 | If you would like to calculate duct diameter based upon CFM and Velocity please see below
|  | CFM in duct |  | 1000 |  | Based upon the information given the suggested
|  | Desired Velocity |  | 4500 |  | duct with a diameter of 6 inches with a velocity of 4500 FEET / MIN
40.7436
[6 empty] | DIAMETER INCHES |  | VELOCITY |  | AIR VOLUNE |  | VELOCITY
|  | FIND THE OPTIMAL DUCT DIAMETER |  |  |  | (CALCULATED) |  | (CALCULATED) |  | (SPECIFIED) |  | (OFF THE DESIRED VALUE)
15.163
| 15.17 | DUCT SIZE (BASED UPON THE VELOCITY) |  |  |  | 6.3831 | inches | 4500 | FEET/MIN | 1000 | CFM
no |  | DUCT SIZE (ROUNDED UP TIL NEXT SIZE) |  |  |  | 7 | inches | 3741.7564 | FEET/MIN | 1000 | CFM | 16.85% | off
yes |  | DUCT SIZE (ROUNDED DOWN TIL NEXT SIZE) |  |  |  | 6 | inches | 5092.9463 | FEET/MIN | 1000 | CFM | 13.18% | off
6 |  | Within 3% |  | Within 6% |  | Within 10% |  | More than 10% off |  | -0.1685 | 0.13177
| As you can see from above the calculated size is: | [5 empty] | 6.3831 | inches which means the closest size is: |  |  |  | 6 | inches
VER 2 | If you would like to calculate your total amount of CFM requirement you can do that below.
Simply fill out the quantity of drops and/or duct diameters you would like the combine / know
the combined diameter duct for:
5092.9463 | Based upon the 9 drops / ducts entered below @4500 ft / min velocity we have 5643 CFM
5093 | which I deally would be a 15.16 inch duct - rounded closest diameter would be a 15 inch diameter duct
| 9 | [16 empty] | #N/A |  | ROUND | ROUND
| Quantiy | DUCT Ø | 2000 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5500 | 6000 | 6500 | 7000 |  |  | 5643 |  | 5643 | DUCT Ø | DOWN | UP
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 3 | 5643CFM |  | 5643CFM
Clamp-Together | 1 | 3 | 100 | 125 | 150 | 170 | 195 | 220 | 245 | 270 | 295 | 320 | 345 | 220.7812 | 4 | 220.7812 | 220.7812 | 220.7812 | 3 | 3 | 4
Clamp-Together | 4 | 4 | 175 | 220 | 260 | 305 | 350 | 395 | 440 | 485 | 525 | 570 | 615 | 392.5 | 5 | 1570 | 392.5 | 1570 | 4 | 4 | 5
Clamp-Together |  | 5 | 275 | 340 | 410 | 475 | 545 | 615 | 680 | 750 | 820 | 885 | 955 | 613.2813 | 6 | 0 | 613.2813 | 0 | 5 | 5 | 6
Clamp-Together | 3 | 6 | 395 | 490 | 590 | 685 | 785 | 885 | 980 | 1080 | 1180 | 1275 | 1375 | 883.125 | 7 | 2649.375 | 883.125 | 2649.375 | 6 | 6 | 7
Clamp-Together | 1 | 7 | 535 | 670 | 800 | 935 | 1070 | 1205 | 1335 | 1470 | 1605 | 1735 | 1870 | 1202.0312 | 8 | 1202.0312 | 1202.0312 | 1202.0312 | 7 | 7 | 8
Clamp-Together |  | 8 | 700 | 875 | 1050 | 1220 | 1395 | 1570 | 1745 | 1920 | 2095 | 2270 | 2445 | 1570 | 9 | 0 | 1570 | 0 | 8 | 8 | 9
Clamp-Together |  | 9 | 885 | 1105 | 1325 | 1545 | 1765 | 1990 | 2210 | 2430 | 2650 | 2870 | 3090 | 1987.0312 | 10 | 0 | 1987.0312 | 0 | 9 | 9 | 10
Clamp-Together |  | 10 | 1090 | 1365 | 1635 | 1910 | 2180 | 2455 | 2725 | 3000 | 3270 | 3545 | 3820 | 2453.125 | 11 | 0 | 2453.125 | 0 | 10 | 10 | 11
Clamp-Together |  | 11 | 1320 | 1650 | 1980 | 2310 | 2640 | 2970 | 3300 | 3630 | 3960 | 4290 | 4620 | 2968.2813 | 12 | 0 | 2968.2813 | 0 | 11 | 11 | 12
Clamp-Together |  | 12 | 1570 | 1965 | 2355 | 2750 | 3140 | 3535 | 3925 | 4320 | 4710 | 5105 | 5500 | 3532.5 | 13 | 0 | 3532.5 | 0 | 12 | 12 | 13
Clamp-Together |  | 13 | 1850 | 2300 | 2770 | 3225 | 3685 | 4150 | 4610 | 5070 | 5530 | 5990 | 6450 | 4145.7813 | 14 | 0 | 4145.7813 | 0 | 13 | 13 | 14
Clamp-Together |  | 14 | 2140 | 2675 | 3205 | 3740 | 4275 | 4810 | 5345 | 5880 | 6415 | 6950 | 7485 | 4808.125 | 15 | 0 | 4808.125 | 0 | 14 | 14 | 15
Clamp-Together |  | 15 | 2450 | 3070 | 3680 | 4300 | 4900 | 5520 | 6130 | 6750 | 7360 | 7970 | 8590 | 5519.5313 | 16 | 0 | 5519.5313 | 0 | 15 | 15 | 16
Clamp-Together |  | 16 | 2790 | 3490 | 4190 | 4885 | 5585 | 6285 | 6980 | 7680 | 8380 | 9075 | 9775 | 6280 | 17 | 0 | 6280 | 0 | 16 | 16 | 17
Clamp-Together |  | 17 | 3150 | 3940 | 4730 | 5515 | 6300 | 7090 | 7880 | 8670 | 9450 | 10240 | 11030 | 7089.5313 | 18 | 0 | 7089.5313 | 0 | 17 | 17 | 18
Clamp-Together |  | 18 | 3535 | 4420 | 5300 | 6185 | 7070 | 7950 | 8835 | 9720 | 10600 | 11485 | 12370 | 7948.125 | 20 | 0 | 7948.125 | 0 | 18 | 18 | 20
Clamp-Together |  | 20 | 4365 | 5455 | 6545 | 7635 | 8725 | 9815 | 10910 | 12000 | 13090 | 14180 | 15270 | 9812.5 | 22 | 0 | 9812.5 | 0 | 20 | 20 | 22
Clamp-Together |  | 22 | 5280 | 6600 | 7920 | 9240 | 10560 | 11880 | 13200 | 14520 | 15840 | 17160 | 18480 | 11873.125 | 24 | 0 | 11873.125 | 0 | 22 | 22 | 24
Clamp-Together |  | 24 | 6285 | 7855 | 9425 | 10995 | 12656 | 14135 | 15710 | 17280 | 18850 | 20420 | 21995 | 14130 | 26 | 0 | 14130 | 0 | 24 | 24 | 26
FLANGED |  | 26 | 7370 | 9210 | 11055 | 12900 | 14740 | 16580 | 18420 | 20270 | 22110 | 23950 | 25800 | 16583.125 | 28 | 0 | 16583.125 | 0 | 26 | 26 | 28
FLANGED |  | 28 | 8550 | 10685 | 12820 | 14960 | 17100 | 19230 | 21310 | 23500 | 25650 | 27780 | 29920 | 19232.5 | 30 | 0 | 19232.5 | 0 | 28 | 28 | 30
FLANGED |  | 30 | 9800 | 12260 | 14700 | 17170 | 19625 | 22080 | 24530 | 26990 | 29440 | 31890 | 34350 | 22078.125 | 32 | 0 | 22078.125 | 0 | 30 | 30 | 32
FLANGED |  | 32 | 11160 | 13950 | 16750 | 19541 | 22330 | 25120 | 17910 | 30700 | 33490 | 26280 | 39070 | 25120 | 34 | 0 | 25120 | 0 | 32 | 32 | 34
FLANGED |  | 34 | 12600 | 15755 | 18905 | 22055 | 25210 | 28360 | 31510 | 34660 | 37810 | 40965 | 44115 | 28358.125 | 36 | 0 | 28358.125 | 0 | 34 | 34 | 36
FLANGED |  | 36 | 14130 | 17665 | 21195 | 24730 | 28260 | 31800 | 35325 | 38860 | 42390 | 45925 | 49455 | 31792.5 | 38 | 0 | 31792.5 | 0 | 36 | 36 | 38
FLANGED |  | 38 | 15745 | 19680 | 23615 | 27550 | 31490 | 35425 | 39360 | 43295 | 47230 | 51170 | 55100 | 35423.125 | 40 | 0 | 35423.125 | 0 | 38 | 38 | 40
FLANGED |  | 40 | 17445 | 21800 | 26170 | 30530 | 34890 | 39250 | 43610 | 47975 | 52330 | 56700 | 61055 | 39250 |  | 0 |  | 0 | 40 | 40 | PLEASE CALL
| 9 | [14 empty] | 5643 |  | 5643 | 1000 | PLEASE CALL | PLEASE CALL
| 15.16 | Based upon the amount of either drops or different size duct added together / filled out above the combined duct diameter
|  | should ideally be: | 2: 15.163; 3: Inches - or rounded to nearest number:; 8: 15; 9: inch diameter duct
Below you can see more details for the closest diameter above and below the calculated size
CFM From Above
|  | CFM in duct | 2: 5643; 3: <--------; 4: Based upon the information given the suggested
|  | Desired Velocity | 2: 4500; 4: duct with a diameter of 6 inches with a velocity of FEET / MIN
229.916
[6 empty] | DIAMETER INCHES |  | VELOCITY |  | AIR VOLUNE |  | VELOCITY
|  | FIND THE OPTIMAL DUCT DIAMETER | 4: (CALCULATED); 6: (CALCULATED); 8: (SPECIFIED); 10: (OFF THE DESIRED VALUE)
0
| 0 | DUCT SIZE (BASED UPON THE VELOCITY) | 4: 15.163; 5: inches; 6: 4500; 7: FEET/MIN; 8: 5643; 9: CFM
|  | DUCT SIZE (ROUNDED UP TIL NEXT SIZE) |  |  |  | 16 | inches | 4041.4916 | FEET/MIN | 5643 | CFM | 10.19% | off
|  | DUCT SIZE (ROUNDED DOWN TIL NEXT SIZE) |  |  |  | 15 | inches | 4598.3193 | FEET/MIN | 5643 | CFM | 2.185% | off
|  | Within 3% | 2: Within 6%; 4: Within 10%; 6: More than 10% off; 8: -0.10189; 9: 0.021849

## Calculate Duct size (2) (hidden)
Duct Calculators
6
VER 1 | If you would like to calculate duct diameter based upon CFM and Velocity please see below
|  | CFM in duct |  | 1000 |  | Based upon the information given the suggested
|  | Desired Velocity |  | 4500 |  | duct with a diameter of 6 inches with a velocity of 4500 FEET / MIN
40.7436
[6 empty] | DIAMETER INCHES |  | VELOCITY |  | AIR VOLUNE |  | VELOCITY
|  | FIND THE OPTIMAL DUCT DIAMETER |  |  |  | (CALCULATED) |  | (CALCULATED) |  | (SPECIFIED) |  | (OFF THE DESIRED VALUE)
6.9279
| 6.93 | DUCT SIZE (BASED UPON THE VELOCITY) |  |  |  | 6.3831 | inches | 4500 | FEET/MIN | 1000 | CFM
no |  | DUCT SIZE (ROUNDED UP TIL NEXT SIZE) |  |  |  | 7 | inches | 3741.7564 | FEET/MIN | 1000 | CFM | 16.85% | off
yes |  | DUCT SIZE (ROUNDED DOWN TIL NEXT SIZE) |  |  |  | 6 | inches | 5092.9463 | FEET/MIN | 1000 | CFM | 13.18% | off
6 |  | Within 3% |  | Within 6% |  | Within 10% |  | More than 10% off |  | -0.1685 | 0.13177
| As you can see from above the calculated size is: | [5 empty] | 6.3831 | inches which means the closest size is: |  |  |  | 6 | inches
VER 2 | If you would like to calculate your total amount of CFM requirement you can do that below.
Simply fill out the quantity of drops and/or duct diameters you would like the combine / know
the combined diameter duct for:
5092.9463 | Based upon the 3 drops / ducts entered below @4500 ft / min velocity we have 1178 CFM
5093 | which I deally would be a 6.93 inch duct - rounded closest diameter would be a 7 inch diameter duct
| 3 | [16 empty] | #N/A |  | ROUND | ROUND
| Quantiy | DUCT Ø | 2000 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5500 | 6000 | 6500 | 7000 |  |  | 1178 |  | 1178 | DUCT Ø | DOWN | UP
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 3 | 1178CFM |  | 1178CFM
Clamp-Together |  | 3 | 100 | 125 | 150 | 170 | 195 | 220 | 245 | 270 | 295 | 320 | 345 | 220.7812 | 4 | 0 | 220.7812 | 0 | 3 | 3 | 4
Clamp-Together | 3 | 4 | 175 | 220 | 260 | 305 | 350 | 395 | 440 | 485 | 525 | 570 | 615 | 392.5 | 5 | 1177.5 | 392.5 | 1177.5 | 4 | 4 | 5
Clamp-Together |  | 5 | 275 | 340 | 410 | 475 | 545 | 615 | 680 | 750 | 820 | 885 | 955 | 613.2813 | 6 | 0 | 613.2813 | 0 | 5 | 5 | 6
Clamp-Together |  | 6 | 395 | 490 | 590 | 685 | 785 | 885 | 980 | 1080 | 1180 | 1275 | 1375 | 883.125 | 7 | 0 | 883.125 | 0 | 6 | 6 | 7
Clamp-Together |  | 7 | 535 | 670 | 800 | 935 | 1070 | 1205 | 1335 | 1470 | 1605 | 1735 | 1870 | 1202.0312 | 8 | 0 | 1202.0312 | 0 | 7 | 7 | 8
Clamp-Together |  | 8 | 700 | 875 | 1050 | 1220 | 1395 | 1570 | 1745 | 1920 | 2095 | 2270 | 2445 | 1570 | 9 | 0 | 1570 | 0 | 8 | 8 | 9
Clamp-Together |  | 9 | 885 | 1105 | 1325 | 1545 | 1765 | 1990 | 2210 | 2430 | 2650 | 2870 | 3090 | 1987.0312 | 10 | 0 | 1987.0312 | 0 | 9 | 9 | 10
Clamp-Together |  | 10 | 1090 | 1365 | 1635 | 1910 | 2180 | 2455 | 2725 | 3000 | 3270 | 3545 | 3820 | 2453.125 | 11 | 0 | 2453.125 | 0 | 10 | 10 | 11
Clamp-Together |  | 11 | 1320 | 1650 | 1980 | 2310 | 2640 | 2970 | 3300 | 3630 | 3960 | 4290 | 4620 | 2968.2813 | 12 | 0 | 2968.2813 | 0 | 11 | 11 | 12
Clamp-Together |  | 12 | 1570 | 1965 | 2355 | 2750 | 3140 | 3535 | 3925 | 4320 | 4710 | 5105 | 5500 | 3532.5 | 13 | 0 | 3532.5 | 0 | 12 | 12 | 13
Clamp-Together |  | 13 | 1850 | 2300 | 2770 | 3225 | 3685 | 4150 | 4610 | 5070 | 5530 | 5990 | 6450 | 4145.7813 | 14 | 0 | 4145.7813 | 0 | 13 | 13 | 14
Clamp-Together |  | 14 | 2140 | 2675 | 3205 | 3740 | 4275 | 4810 | 5345 | 5880 | 6415 | 6950 | 7485 | 4808.125 | 15 | 0 | 4808.125 | 0 | 14 | 14 | 15
Clamp-Together |  | 15 | 2450 | 3070 | 3680 | 4300 | 4900 | 5520 | 6130 | 6750 | 7360 | 7970 | 8590 | 5519.5313 | 16 | 0 | 5519.5313 | 0 | 15 | 15 | 16
Clamp-Together |  | 16 | 2790 | 3490 | 4190 | 4885 | 5585 | 6285 | 6980 | 7680 | 8380 | 9075 | 9775 | 6280 | 17 | 0 | 6280 | 0 | 16 | 16 | 17
Clamp-Together |  | 17 | 3150 | 3940 | 4730 | 5515 | 6300 | 7090 | 7880 | 8670 | 9450 | 10240 | 11030 | 7089.5313 | 18 | 0 | 7089.5313 | 0 | 17 | 17 | 18
Clamp-Together |  | 18 | 3535 | 4420 | 5300 | 6185 | 7070 | 7950 | 8835 | 9720 | 10600 | 11485 | 12370 | 7948.125 | 20 | 0 | 7948.125 | 0 | 18 | 18 | 20
Clamp-Together |  | 20 | 4365 | 5455 | 6545 | 7635 | 8725 | 9815 | 10910 | 12000 | 13090 | 14180 | 15270 | 9812.5 | 22 | 0 | 9812.5 | 0 | 20 | 20 | 22
Clamp-Together |  | 22 | 5280 | 6600 | 7920 | 9240 | 10560 | 11880 | 13200 | 14520 | 15840 | 17160 | 18480 | 11873.125 | 24 | 0 | 11873.125 | 0 | 22 | 22 | 24
Clamp-Together |  | 24 | 6285 | 7855 | 9425 | 10995 | 12656 | 14135 | 15710 | 17280 | 18850 | 20420 | 21995 | 14130 | 26 | 0 | 14130 | 0 | 24 | 24 | 26
FLANGED |  | 26 | 7370 | 9210 | 11055 | 12900 | 14740 | 16580 | 18420 | 20270 | 22110 | 23950 | 25800 | 16583.125 | 28 | 0 | 16583.125 | 0 | 26 | 26 | 28
FLANGED |  | 28 | 8550 | 10685 | 12820 | 14960 | 17100 | 19230 | 21310 | 23500 | 25650 | 27780 | 29920 | 19232.5 | 30 | 0 | 19232.5 | 0 | 28 | 28 | 30
FLANGED |  | 30 | 9800 | 12260 | 14700 | 17170 | 19625 | 22080 | 24530 | 26990 | 29440 | 31890 | 34350 | 22078.125 | 32 | 0 | 22078.125 | 0 | 30 | 30 | 32
FLANGED |  | 32 | 11160 | 13950 | 16750 | 19541 | 22330 | 25120 | 17910 | 30700 | 33490 | 26280 | 39070 | 25120 | 34 | 0 | 25120 | 0 | 32 | 32 | 34
FLANGED |  | 34 | 12600 | 15755 | 18905 | 22055 | 25210 | 28360 | 31510 | 34660 | 37810 | 40965 | 44115 | 28358.125 | 36 | 0 | 28358.125 | 0 | 34 | 34 | 36
FLANGED |  | 36 | 14130 | 17665 | 21195 | 24730 | 28260 | 31800 | 35325 | 38860 | 42390 | 45925 | 49455 | 31792.5 | 38 | 0 | 31792.5 | 0 | 36 | 36 | 38
FLANGED |  | 38 | 15745 | 19680 | 23615 | 27550 | 31490 | 35425 | 39360 | 43295 | 47230 | 51170 | 55100 | 35423.125 | 40 | 0 | 35423.125 | 0 | 38 | 38 | 40
FLANGED |  | 40 | 17445 | 21800 | 26170 | 30530 | 34890 | 39250 | 43610 | 47975 | 52330 | 56700 | 61055 | 39250 |  | 0 |  | 0 | 40 | 40 | PLEASE CALL
| 3 | [14 empty] | 1178 |  | 1178 | 1000 | PLEASE CALL | PLEASE CALL
| 6.93 | Based upon the amount of either drops or different size duct added together / filled out above the combined duct diameter
|  | should ideally be: | 2: 6.9279; 3: Inches - or rounded to nearest number:; 8: 7; 9: inch diameter duct
Below you can see more details for the closest diameter above and below the calculated size
CFM From Above
|  | CFM in duct | 2: 1178; 3: <--------; 4: Based upon the information given the suggested
|  | Desired Velocity | 2: 4500; 4: duct with a diameter of 6 inches with a velocity of FEET / MIN
47.9959
[6 empty] | DIAMETER INCHES |  | VELOCITY |  | AIR VOLUNE |  | VELOCITY
|  | FIND THE OPTIMAL DUCT DIAMETER | 4: (CALCULATED); 6: (CALCULATED); 8: (SPECIFIED); 10: (OFF THE DESIRED VALUE)
0
| 0 | DUCT SIZE (BASED UPON THE VELOCITY) | 4: 6.9279; 5: inches; 6: 4500; 7: FEET/MIN; 8: 1178; 9: CFM
|  | DUCT SIZE (ROUNDED UP TIL NEXT SIZE) |  |  |  | 7 | inches | 4407.7891 | FEET/MIN | 1178 | CFM | 2.049% | off
|  | DUCT SIZE (ROUNDED DOWN TIL NEXT SIZE) |  |  |  | 6 | inches | 5999.4907 | FEET/MIN | 1178 | CFM | 33.32% | off
|  | Within 3% | 2: Within 6%; 4: Within 10%; 6: More than 10% off; 8: -0.020491; 9: 0.33322

## Calculate Duct size (hidden)
6
Please fill in the blue fields and the program will tell you which size duct to use.
|  |  |  | Type in | 1570CFM
|  | CFM in duct |  | 2685 | <-------- | Based upon the information given the suggested
|  | Desired Velocity |  | 4500 |  | duct with a diameter of 10 inches with a velocity of 4923 FEET / MIN
109.3965
[6 empty] | DIAMETER INCHES |  | VELOCITY |  | AIR VOLUNE |  | VELOCITY
|  | FIND THE OPTIMAL DUCT DIAMETER |  |  |  | (CALCULATED) |  | (CALCULATED) |  | (SPECIFIED) |  | (OFF THE DESIRED VALUE)
7.998
| 8 | DUCT SIZE (BASED UPON THE VELOCITY) |  |  |  | 10.4593 | inches | 4500 | FEET/MIN | 2685 | CFM
no |  | DUCT SIZE (ROUNDED UP TIL NEXT SIZE) |  |  |  | 11 | inches | 4068.4644 | FEET/MIN | 2685 | CFM | 9.59% | off
yes |  | DUCT SIZE (ROUNDED DOWN TIL NEXT SIZE) |  |  |  | 10 | inches | 4922.8419 | FEET/MIN | 2685 | CFM | 9.396% | off
10 |  | Within 3% |  | Within 6% |  | Within 10% |  | More than 10% off |  | -0.095897 | 0.093965
4923
4922.8419 | BASED UPON THE ENTERED CONNECTION POINTS YOU WILL
4923 | NEED A TOTAL OF 1570CFM (8''Ø @ 4500FEET/MIN)
| AMOUNT OF | [14 empty] | 9Ø |  | ROUND | ROUND
| CONECTIONS | DUCT Ø | 2000 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5500 | 6000 | 6500 | 7000 |  |  | 1570 | DUCT Ø | DOWN | UP
| 4 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 3 | 1570CFM
Clamp-Together |  | 3 | 100 | 125 | 150 | 170 | 195 | 220 | 245 | 270 | 295 | 320 | 345 | 220.7812 | 4 | 0 | 3 | 3 | 4
Clamp-Together | 4 | 4 | 175 | 220 | 260 | 305 | 350 | 395 | 440 | 485 | 525 | 570 | 615 | 392.5 | 5 | 1570 | 4 | 4 | 5
Clamp-Together |  | 5 | 275 | 340 | 410 | 475 | 545 | 615 | 680 | 750 | 820 | 885 | 955 | 613.2813 | 6 | 0 | 5 | 5 | 6
Clamp-Together |  | 6 | 395 | 490 | 590 | 685 | 785 | 885 | 980 | 1080 | 1180 | 1275 | 1375 | 883.125 | 7 | 0 | 6 | 6 | 7
Clamp-Together |  | 7 | 535 | 670 | 800 | 935 | 1070 | 1205 | 1335 | 1470 | 1605 | 1735 | 1870 | 1202.0312 | 8 | 0 | 7 | 7 | 8
Clamp-Together |  | 8 | 700 | 875 | 1050 | 1220 | 1395 | 1570 | 1745 | 1920 | 2095 | 2270 | 2445 | 1570 | 9 | 0 | 8 | 8 | 9
Clamp-Together |  | 9 | 885 | 1105 | 1325 | 1545 | 1765 | 1990 | 2210 | 2430 | 2650 | 2870 | 3090 | 1987.0312 | 10 | 0 | 9 | 9 | 10
Clamp-Together |  | 10 | 1090 | 1365 | 1635 | 1910 | 2180 | 2455 | 2725 | 3000 | 3270 | 3545 | 3820 | 2453.125 | 11 | 0 | 10 | 10 | 11
Clamp-Together |  | 11 | 1320 | 1650 | 1980 | 2310 | 2640 | 2970 | 3300 | 3630 | 3960 | 4290 | 4620 | 2968.2813 | 12 | 0 | 11 | 11 | 12
Clamp-Together |  | 12 | 1570 | 1965 | 2355 | 2750 | 3140 | 3535 | 3925 | 4320 | 4710 | 5105 | 5500 | 3532.5 | 13 | 0 | 12 | 12 | 13
Clamp-Together |  | 13 | 1850 | 2300 | 2770 | 3225 | 3685 | 4150 | 4610 | 5070 | 5530 | 5990 | 6450 | 4145.7813 | 14 | 0 | 13 | 13 | 14
Clamp-Together |  | 14 | 2140 | 2675 | 3205 | 3740 | 4275 | 4810 | 5345 | 5880 | 6415 | 6950 | 7485 | 4808.125 | 15 | 0 | 14 | 14 | 15
Clamp-Together |  | 15 | 2450 | 3070 | 3680 | 4300 | 4900 | 5520 | 6130 | 6750 | 7360 | 7970 | 8590 | 5519.5313 | 16 | 0 | 15 | 15 | 16
Clamp-Together |  | 16 | 2790 | 3490 | 4190 | 4885 | 5585 | 6285 | 6980 | 7680 | 8380 | 9075 | 9775 | 6280 | 17 | 0 | 16 | 16 | 17
Clamp-Together |  | 17 | 3150 | 3940 | 4730 | 5515 | 6300 | 7090 | 7880 | 8670 | 9450 | 10240 | 11030 | 7089.5313 | 18 | 0 | 17 | 17 | 18
Clamp-Together |  | 18 | 3535 | 4420 | 5300 | 6185 | 7070 | 7950 | 8835 | 9720 | 10600 | 11485 | 12370 | 7948.125 | 20 | 0 | 18 | 18 | 20
Clamp-Together |  | 20 | 4365 | 5455 | 6545 | 7635 | 8725 | 9815 | 10910 | 12000 | 13090 | 14180 | 15270 | 9812.5 | 22 | 0 | 20 | 20 | 22
Clamp-Together |  | 22 | 5280 | 6600 | 7920 | 9240 | 10560 | 11880 | 13200 | 14520 | 15840 | 17160 | 18480 | 11873.125 | 24 | 0 | 22 | 22 | 24
Clamp-Together |  | 24 | 6285 | 7855 | 9425 | 10995 | 12656 | 14135 | 15710 | 17280 | 18850 | 20420 | 21995 | 14130 | 26 | 0 | 24 | 24 | 26
FLANGED |  | 26 | 7370 | 9210 | 11055 | 12900 | 14740 | 16580 | 18420 | 20270 | 22110 | 23950 | 25800 | 16583.125 | 28 | 0 | 26 | 26 | 28
FLANGED |  | 28 | 8550 | 10685 | 12820 | 14960 | 17100 | 19230 | 21310 | 23500 | 25650 | 27780 | 29920 | 19232.5 | 30 | 0 | 28 | 28 | 30
FLANGED |  | 30 | 9800 | 12260 | 14700 | 17170 | 19625 | 22080 | 24530 | 26990 | 29440 | 31890 | 34350 | 22078.125 | 32 | 0 | 30 | 30 | 32
FLANGED |  | 32 | 11160 | 13950 | 16750 | 19541 | 22330 | 25120 | 17910 | 30700 | 33490 | 26280 | 39070 | 25120 | 34 | 0 | 32 | 32 | 34
FLANGED |  | 34 | 12600 | 15755 | 18905 | 22055 | 25210 | 28360 | 31510 | 34660 | 37810 | 40965 | 44115 | 28358.125 | 36 | 0 | 34 | 34 | 36
FLANGED |  | 36 | 14130 | 17665 | 21195 | 24730 | 28260 | 31800 | 35325 | 38860 | 42390 | 45925 | 49455 | 31792.5 | 38 | 0 | 36 | 36 | 38
FLANGED |  | 38 | 15745 | 19680 | 23615 | 27550 | 31490 | 35425 | 39360 | 43295 | 47230 | 51170 | 55100 | 35423.125 | 40 | 0 | 38 | 38 | 40
FLANGED |  | 40 | 17445 | 21800 | 26170 | 30530 | 34890 | 39250 | 43610 | 47975 | 52330 | 56700 | 61055 | 39250 |  | 0 | 40 | 40 | PLEASE CALL
[17 empty] | 1000 | PLEASE CALL | PLEASE CALL
Reset conections
Front Page

## CFM Calculator
[11 empty] | Add trunk lines |  |  |  | CFM |  | Ø
|  | Total air volume | 9886.0938 | CFM @ 4500 ft/min |  |  | 4500 |  |  |  | 1 |  |  | 3949.5312 |  |  | 13 | [41 empty] | 12 |  | 13 |  | 3532.5 | 4145.7813 | -11.81% | 4.734% | 11.81% | 4.734% | 13 | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Main trunk line dia. | 20 inch | [7 empty] | 2 |  |  | 4219.375 |  |  | 13 | [41 empty] | 13 |  | 14 |  | 4145.7813 | 4808.125 | -1.775% | 12.24% | 1.775% | 12.24% | 13 | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[11 empty] | 5 |  |  | 0 | [38 empty] | 4500 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% | [11 empty] | 4500 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0%
|  | www.industsolutions.com | [8 empty] | CFM manually | [19 empty] | Custom | [31 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | [10 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Please call or email Niels Haugaard @ 702 454 0355 / nh@industsolutions.com with any questions | [9 empty] | Combined |  |  | 8168.9062 |  |  | 18 | [13 empty] | Diameter | [27 empty] | 18 |  | 20 |  | 7948.125 | 9812.5 | -2.778% | 16.75% | 2.778% | 16.75% | 18 | 3949.5312 | 4219.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3949.5312 | 4219.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Install | Machine | Machine | Machine | Machine | Usage / day | Total trunk | CFM @ | Duct | Velocity | Trunk | Enter number of connection points | [18 empty] | 24 | Trunk | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 24 | Machine |  |  | 4500 |  | 20 | 20 |  | 22 |  | 9812.5 | 11873.125 | -0.75% | 16.74% | 0.75% | 16.74% | 20 | [10 empty] | Trunk line |  |  | 4500 |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Phase | Type | Fabricate | Model | Voltage | Hours | line Ø | 4500 Ft/Min | Ø | Ft / min | line # | 2" | 3" | 4" | 5" | 6" | 7" | 8" | 9" | 10" | 11" | 12" | 13" | 14" | 15" | 16" | 17" | 18" | 19" | 20" |  | line Ø | 98.125 | 220.7812 | 392.5 | 613.2813 | 883.125 | 1202.0312 | 1570 | 1987.0312 | 2453.125 | 2968.2813 | 3532.5 | 4145.7813 | 4808.125 | 5519.5313 | 6280 | 7089.5313 | 7948.125 | 8855.7813 | 9812.5 |  | Air volume | [16 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Air volume | [16 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[34 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | Band Saw |  |  |  |  | 4 | 392.5 | 4" | 4500 | 1 | [20 empty] | 4 | 0 | 0 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392.5 | 2 | 98.125 | 98.125 | 2 | 4 | 4 | or | 5 | Duct | 392.5 | 613.2813 | 0% | 36% | 0% | 36% | 4 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392.5 | 2 | 98.125 | 98.125 | 2 | 4 | 4 | or | 5 | Duct | 392.5 | 613.2813 | 0% | 36% | 0% | 36% | 4 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 4"
2 | 1 | Table Saw 1 |  |  |  |  | 5 | 392.5 | 4" | 4500 | 1 | [20 empty] | 5 | 0 | 0 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392.5 | 3 | 220.7812 | 220.7812 | 3 | 4 | 4 | or | 5 | Duct | 392.5 | 613.2813 | 0% | 36% | 0% | 36% | 4 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 3 | 220.7812 | 220.7812 | 3 | 5 | 5 | or | 6 | Duct | 613.2813 | 883.125 | 36% | 55.56% | 36% | 55.56% | 5 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 4"
3 | 1 | Table Saw 2 |  |  |  |  | 7 | 613.2813 | 5" | 4500 | 1 | [20 empty] | 7 | 0 | 0 | 0 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613.2813 | 4 | 392.5 | 392.5 | 4 | 5 | 5 | or | 6 | Duct | 613.2813 | 883.125 | 0% | 30.56% | 0% | 30.56% | 5 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.2812 | 4 | 392.5 | 392.5 | 4 | 7 | 7 | or | 8 | Duct | 1202.0312 | 1570 | 48.98% | 60.94% | 48.98% | 60.94% | 7 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 5"
4 | 1 | Wide Belt Sander |  |  |  |  | 9 | 883.125 | 6" | 4500 | 1 | [20 empty] | 9 | 0 | 0 | 0 | 0 | 883.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883.125 | 5 | 613.2813 | 613.2813 | 5 | 6 | 6 | or | 7 | Duct | 883.125 | 1202.0312 | 0% | 26.53% | 0% | 26.53% | 6 | 883.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281.4062 | 5 | 613.2813 | 613.2813 | 5 | 9 | 9 | or | 10 | Duct | 1987.0312 | 2453.125 | 55.56% | 64% | 55.56% | 64% | 9 | 883.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 6"
5 | 1 | Edge Bander |  |  |  |  | 11 | 1054.8438 | 7" | 4500 | 1 | 3": 3; 4": 1 |  | 11 | 0 | 662.3438 | 392.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.8438 | 6 | 883.125 | 883.125 | 6 | 7 | 6 | or | 7 | Duct | 883.125 | 1202.0312 | -19.44% | 12.24% | 19.44% | 12.24% | 7 | 1054.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3336.25 | 6 | 883.125 | 883.125 | 6 | 11 | 11 | or | 12 | Duct | 2968.2813 | 3532.5 | 64.46% | 70.14% | 64.46% | 70.14% | 11 | 1054.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | Planer |  |  |  |  | 12 | 613.2813 | 5" | 4500 | 1 | [20 empty] | 12 | 0 | 0 | 0 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613.2813 | 7 | 1202.0312 | 1202.0312 | 7 | 5 | 5 | or | 6 | Duct | 613.2813 | 883.125 | 0% | 30.56% | 0% | 30.56% | 5 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3949.5312 | 7 | 1202.0312 | 1202.0312 | 7 | 12 | 12 | or | 13 | Duct | 3532.5 | 4145.7813 | 82.64% | 85.21% | 82.64% | 85.21% | 12 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 5"
7 | 1 | CNC |  |  |  |  | 18 | 4219.375 | 13" | 4500 | 2 | 6": 3; 8": 1 |  | 18 | 0 | 0 | 0 | 0 | 2649.375 | 0 | 1570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4219.375 | 8 | 1570 | 1570 | 8 | 13 | 13 | or | 14 | Duct | 4145.7813 | 4808.125 | -1.775% | 12.24% | 1.775% | 12.24% | 13 | 0 | 4219.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8168.9062 | 8 | 1570 | 1570 | 8 | 18 | 18 | or | 20 | Duct | 7948.125 | 9812.5 | 46.91% | 57% | 46.91% | 57% | 18 | 0 | 4219.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | Planer 2 |  | (plan to be on line 1 in the future) |  |  | 18 | 883.125 | 6" | 4500 | [21 empty] | 18 | 0 | 0 | 0 | 0 | 883.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883.125 | 9 | 1987.0312 | 1987.0312 | 9 | 6 | 6 | or | 7 | Duct | 883.125 | 1202.0312 | 0% | 26.53% | 0% | 26.53% | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9052.0312 | 9 | 1987.0312 | 1987.0312 | 9 | 18 | 18 | or | 20 | Duct | 7948.125 | 9812.5 | 88.89% | 91% | 88.89% | 91% | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 6"
9 | 2 | Table Saw 3 |  | (plan to be on line 2 in the future) |  |  | 20 | 834.0625 | 6" | 4500 | [21 empty] | 20 | 0 | 220.7812 | 0 | 613.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 834.0625 | 10 | 2453.125 | 2453.125 | 10 | 6 | 5 | or | 6 | Duct | 613.2813 | 883.125 | -36% | 5.556% | 36% | 5.556% | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 10 | 2453.125 | 2453.125 | 10 | 20 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 91.5% | 92.98% | 91.5% | 92.98% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: 3"; 5"
10 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2968.2813 | 2968.2813 | 11 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 11 | 2968.2813 | 2968.2813 | 11 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3532.5 | 3532.5 | 12 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 12 | 3532.5 | 3532.5 | 12 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 |  | List of machines in the shop - first 7 are there |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4145.7813 | 4145.7813 | 13 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 13 | 4145.7813 | 4145.7813 | 13 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 |  | last 2 machines are for phase two |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 4808.125 | 4808.125 | 14 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 14 | 4808.125 | 4808.125 | 14 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5519.5313 | 5519.5313 | 15 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 15 | 5519.5313 | 5519.5313 | 15 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 |  | (try and type "1" in L17 and "2" in L18 and see what happens) |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6280 | 6280 | 16 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 16 | 6280 | 6280 | 16 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7089.5313 | 7089.5313 | 17 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 17 | 7089.5313 | 7089.5313 | 17 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 |  | I have broken this up on two small interior dust collectors |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7948.125 | 7948.125 | 18 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 18 | 7948.125 | 7948.125 | 18 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 |  | but you can see that one dust collector would be an |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 9812.5 | 9812.5 | 20 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 20 | 9812.5 | 9812.5 | 20 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 |  | 18" line (8,169 CFM) right now and after phase 2 being |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11873.125 | 11873.125 | 22 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 22 | 11873.125 | 11873.125 | 22 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 |  | implemented it would need to be a 20" line (9,886 CFM) |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 14130 | 14130 | 24 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 24 | 14130 | 14130 | 24 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16583.125 | 16583.125 | 26 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 26 | 16583.125 | 16583.125 | 26 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 |  | Please note that the calculations are for a FULL OPEN system |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 19232.5 | 19232.5 | 28 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 28 | 19232.5 | 19232.5 | 28 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 |  | (meaning "non-blast gated system). |  |  |  |  | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 22078.125 | 22078.125 | 30 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 30 | 22078.125 | 22078.125 | 30 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 25120 | 25120 | 32 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 32 | 25120 | 25120 | 32 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 28358.125 | 28358.125 | 34 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 34 | 28358.125 | 28358.125 | 34 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 31792.5 | 31792.5 | 36 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 36 | 31792.5 | 31792.5 | 36 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 35423.125 | 35423.125 | 38 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 38 | 35423.125 | 35423.125 | 38 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 39250 | 39250 | 40 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 40 | 39250 | 39250 | 40 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 43273.125 | 43273.125 | 42 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 42 | 43273.125 | 43273.125 | 42 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 47492.5 | 47492.5 | 44 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 44 | 47492.5 | 47492.5 | 44 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 51908.125 | 51908.125 | 46 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 46 | 51908.125 | 51908.125 | 46 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 56520 | 56520 | 48 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 48 | 56520 | 56520 | 48 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 61328.125 | 61328.125 | 50 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 50 | 61328.125 | 61328.125 | 50 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 66332.5 | 66332.5 | 52 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 52 | 66332.5 | 66332.5 | 52 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 71533.125 | 71533.125 | 54 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 54 | 71533.125 | 71533.125 | 54 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 76930 | 76930 | 56 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 56 | 76930 | 76930 | 56 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 82523.125 | 82523.125 | 58 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 58 | 82523.125 | 82523.125 | 58 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | [6 empty] | 22 | 0 |  | 4500 | 5 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 88312.5 | 88312.5 | 60 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 60 | 88312.5 | 88312.5 | 60 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 94298.125 | 94298.125 | 62 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 62 | 94298.125 | 94298.125 | 62 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 100480 | 100480 | 64 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 64 | 100480 | 100480 | 64 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 106858.125 | 106858.125 | 66 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 66 | 106858.125 | 106858.125 | 66 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 113432.5 | 113432.5 | 68 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 68 | 113432.5 | 113432.5 | 68 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 120203.125 | 120203.125 | 70 |  |  | or |  | Duct | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 | 70 | 120203.125 | 120203.125 | 70 | 22 | 20 | or | 22 | Duct | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | [6 empty] | 22 | 0 |  | 4500 | 2 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | [6 empty] | 22 | 0 |  | 4500 | 1 | [20 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | [6 empty] | 22 | 0 |  | 4500 | [21 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [9 empty] | #N/A | #N/A | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.0938 |  |  |  |  | 22 | 20 |  | 22 |  | 9812.5 | 11873.125 | 0% | 0% | 0% | 0% | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Printed CFM Numbers
3.1416
|  |  |  | Change velocity to next column | 100 |  | Table showing the CFM (cubic ft / min) volume in different duct sizes at different velocities | [9 empty] | Add volumes when sizing duct: for instance (2) 5" = 7", (4) 5" = 10"
Duct Diameter inches | 3.1416 | [15 empty] | Std Wood Velocity
Velocity FPM (ft per min)
|  | 3000 | 3100 | 3200 | 3300 | 3400 | 3500 | 3600 | 3700 | 3800 | 3900 | 4000 | 4100 | 4200 | 4300 | 4400 | 4500 | 4600 | 4700 | 4800 | 4900 | 5000 | 5100 | 5200 | 5300 | 5400 | 5500 | 5600 | 5700 | 5800 | 5900 | 6000 | 6100 | 6200 | 6300 | 6400 | 6500 | 6600 | 6700 | 6800 | 6900 | 7000 | 7100 | 7200 | 7300 | 7400 | 7500 | 7600 | 7700 | 7800 | 7900 | 8000 | 8100 | 8200 | 8300 | 8400 | 8500 | 8600
1.25 | 0.0085221 | 25.5663 | 26.4186 | 27.2708 | 28.123 | 28.9752 | 29.8274 | 30.6796 | 31.5318 | 32.384 | 33.2363 | 34.0885 | 34.9407 | 35.7929 | 36.6451 | 37.4973 | 38.3495 | 39.2017 | 40.0539 | 40.9062 | 41.7584 | 42.6106 | 43.4628 | 44.315 | 45.1672 | 46.0194 | 46.8716 | 47.7238 | 48.5761 | 49.4283 | 50.2805 | 51.1327 | 51.9849 | 52.8371 | 53.6893 | 54.5415 | 55.3938 | 56.246 | 57.0982 | 57.9504 | 58.8026 | 59.6548 | 60.507 | 61.3592 | 62.2114 | 63.0637 | 63.9159 | 64.7681 | 65.6203 | 66.4725 | 67.3247 | 68.1769 | 69.0291 | 69.8813 | 70.7336 | 71.5858 | 72.438 | 73.2902
2 | 0.021817 | 65.4498 | 67.6315 | 69.8132 | 71.9948 | 74.1765 | 76.3582 | 78.5398 | 80.7215 | 82.9031 | 85.0848 | 87.2665 | 89.4481 | 91.6298 | 93.8114 | 95.9931 | 98.1748 | 100.3564 | 102.5381 | 104.7198 | 106.9014 | 109.0831 | 111.2647 | 113.4464 | 115.6281 | 117.8097 | 119.9914 | 122.173 | 124.3547 | 126.5364 | 128.718 | 130.8997 | 133.0814 | 135.263 | 137.4447 | 139.6263 | 141.808 | 143.9897 | 146.1713 | 148.353 | 150.5346 | 152.7163 | 154.898 | 157.0796 | 159.2613 | 161.443 | 163.6246 | 165.8063 | 167.9879 | 170.1696 | 172.3513 | 174.5329 | 176.7146 | 178.8962 | 181.0779 | 183.2596 | 185.4412 | 187.6229
3 | 0.049087 | 147.2622 | 152.1709 | 157.0796 | 161.9884 | 166.8971 | 171.8058 | 176.7146 | 181.6233 | 186.5321 | 191.4408 | 196.3495 | 201.2583 | 206.167 | 211.0758 | 215.9845 | 220.8932 | 225.802 | 230.7107 | 235.6194 | 240.5282 | 245.4369 | 250.3457 | 255.2544 | 260.1631 | 265.0719 | 269.9806 | 274.8894 | 279.7981 | 284.7068 | 289.6156 | 294.5243 | 299.433 | 304.3418 | 309.2505 | 314.1593 | 319.068 | 323.9767 | 328.8855 | 333.7942 | 338.703 | 343.6117 | 348.5204 | 353.4292 | 358.3379 | 363.2467 | 368.1554 | 373.0641 | 377.9729 | 382.8816 | 387.7903 | 392.6991 | 397.6078 | 402.5166 | 407.4253 | 412.334 | 417.2428 | 422.1515
4 | 0.087266 | 261.7994 | 270.526 | 279.2527 | 287.9793 | 296.706 | 305.4326 | 314.1593 | 322.8859 | 331.6126 | 340.3392 | 349.0659 | 357.7925 | 366.5191 | 375.2458 | 383.9724 | 392.6991 | 401.4257 | 410.1524 | 418.879 | 427.6057 | 436.3323 | 445.059 | 453.7856 | 462.5123 | 471.2389 | 479.9655 | 488.6922 | 497.4188 | 506.1455 | 514.8721 | 523.5988 | 532.3254 | 541.0521 | 549.7787 | 558.5054 | 567.232 | 575.9587 | 584.6853 | 593.4119 | 602.1386 | 610.8652 | 619.5919 | 628.3185 | 637.0452 | 645.7718 | 654.4985 | 663.2251 | 671.9518 | 680.6784 | 689.4051 | 698.1317 | 706.8583 | 715.585 | 724.3116 | 733.0383 | 741.7649 | 750.4916
5 | 0.13635 | 409.0615 | 422.6969 | 436.3323 | 449.9677 | 463.6031 | 477.2385 | 490.8739 | 504.5092 | 518.1446 | 531.78 | 545.4154 | 559.0508 | 572.6862 | 586.3215 | 599.9569 | 613.5923 | 627.2277 | 640.8631 | 654.4985 | 668.1339 | 681.7692 | 695.4046 | 709.04 | 722.6754 | 736.3108 | 749.9462 | 763.5815 | 777.2169 | 790.8523 | 804.4877 | 818.1231 | 831.7585 | 845.3939 | 859.0292 | 872.6646 | 886.3 | 899.9354 | 913.5708 | 927.2062 | 940.8415 | 954.4769 | 968.1123 | 981.7477 | 995.3831 | 1009.0185 | 1022.6539 | 1036.2892 | 1049.9246 | 1063.56 | 1077.1954 | 1090.8308 | 1104.4662 | 1118.1016 | 1131.7369 | 1145.3723 | 1159.0077 | 1172.6431
6 | 0.19635 | 589.0486 | 608.6836 | 628.3185 | 647.9535 | 667.5884 | 687.2234 | 706.8583 | 726.4933 | 746.1283 | 765.7632 | 785.3982 | 805.0331 | 824.6681 | 844.303 | 863.938 | 883.5729 | 903.2079 | 922.8428 | 942.4778 | 962.1128 | 981.7477 | 1001.3827 | 1021.0176 | 1040.6526 | 1060.2875 | 1079.9225 | 1099.5574 | 1119.1924 | 1138.8273 | 1158.4623 | 1178.0972 | 1197.7322 | 1217.3672 | 1237.0021 | 1256.6371 | 1276.272 | 1295.907 | 1315.5419 | 1335.1769 | 1354.8118 | 1374.4468 | 1394.0817 | 1413.7167 | 1433.3516 | 1452.9866 | 1472.6216 | 1492.2565 | 1511.8915 | 1531.5264 | 1551.1614 | 1570.7963 | 1590.4313 | 1610.0662 | 1629.7012 | 1649.3361 | 1668.9711 | 1688.6061
7 | 0.26725 | 801.7606 | 828.486 | 855.2113 | 881.9367 | 908.662 | 935.3874 | 962.1128 | 988.8381 | 1015.5635 | 1042.2888 | 1069.0142 | 1095.7395 | 1122.4649 | 1149.1902 | 1175.9156 | 1202.6409 | 1229.3663 | 1256.0916 | 1282.817 | 1309.5424 | 1336.2677 | 1362.9931 | 1389.7184 | 1416.4438 | 1443.1691 | 1469.8945 | 1496.6198 | 1523.3452 | 1550.0705 | 1576.7959 | 1603.5213 | 1630.2466 | 1656.972 | 1683.6973 | 1710.4227 | 1737.148 | 1763.8734 | 1790.5987 | 1817.3241 | 1844.0494 | 1870.7748 | 1897.5001 | 1924.2255 | 1950.9509 | 1977.6762 | 2004.4016 | 2031.1269 | 2057.8523 | 2084.5776 | 2111.303 | 2138.0283 | 2164.7537 | 2191.479 | 2218.2044 | 2244.9298 | 2271.6551 | 2298.3805
8 | 0.34907 | 1047.1976 | 1082.1041 | 1117.0107 | 1151.9173 | 1186.8239 | 1221.7305 | 1256.6371 | 1291.5436 | 1326.4502 | 1361.3568 | 1396.2634 | 1431.17 | 1466.0766 | 1500.9832 | 1535.8897 | 1570.7963 | 1605.7029 | 1640.6095 | 1675.5161 | 1710.4227 | 1745.3293 | 1780.2358 | 1815.1424 | 1850.049 | 1884.9556 | 1919.8622 | 1954.7688 | 1989.6753 | 2024.5819 | 2059.4885 | 2094.3951 | 2129.3017 | 2164.2083 | 2199.1149 | 2234.0214 | 2268.928 | 2303.8346 | 2338.7412 | 2373.6478 | 2408.5544 | 2443.461 | 2478.3675 | 2513.2741 | 2548.1807 | 2583.0873 | 2617.9939 | 2652.9005 | 2687.807 | 2722.7136 | 2757.6202 | 2792.5268 | 2827.4334 | 2862.34 | 2897.2466 | 2932.1531 | 2967.0597 | 3001.9663
9 | 0.44179 | 1325.3594 | 1369.538 | 1413.7167 | 1457.8953 | 1502.074 | 1546.2526 | 1590.4313 | 1634.6099 | 1678.7886 | 1722.9672 | 1767.1459 | 1811.3245 | 1855.5032 | 1899.6818 | 1943.8605 | 1988.0391 | 2032.2177 | 2076.3964 | 2120.575 | 2164.7537 | 2208.9323 | 2253.111 | 2297.2896 | 2341.4683 | 2385.6469 | 2429.8256 | 2474.0042 | 2518.1829 | 2562.3615 | 2606.5402 | 2650.7188 | 2694.8974 | 2739.0761 | 2783.2547 | 2827.4334 | 2871.612 | 2915.7907 | 2959.9693 | 3004.148 | 3048.3266 | 3092.5053 | 3136.6839 | 3180.8626 | 3225.0412 | 3269.2199 | 3313.3985 | 3357.5771 | 3401.7558 | 3445.9344 | 3490.1131 | 3534.2917 | 3578.4704 | 3622.649 | 3666.8277 | 3711.0063 | 3755.185 | 3799.3636
10 | 0.54542 | 1636.2462 | 1690.7877 | 1745.3293 | 1799.8708 | 1854.4123 | 1908.9539 | 1963.4954 | 2018.0369 | 2072.5785 | 2127.12 | 2181.6616 | 2236.2031 | 2290.7446 | 2345.2862 | 2399.8277 | 2454.3693 | 2508.9108 | 2563.4523 | 2617.9939 | 2672.5354 | 2727.077 | 2781.6185 | 2836.16 | 2890.7016 | 2945.2431 | 2999.7847 | 3054.3262 | 3108.8677 | 3163.4093 | 3217.9508 | 3272.4923 | 3327.0339 | 3381.5754 | 3436.117 | 3490.6585 | 3545.2 | 3599.7416 | 3654.2831 | 3708.8247 | 3763.3662 | 3817.9077 | 3872.4493 | 3926.9908 | 3981.5324 | 4036.0739 | 4090.6154 | 4145.157 | 4199.6985 | 4254.2401 | 4308.7816 | 4363.3231 | 4417.8647 | 4472.4062 | 4526.9477 | 4581.4893 | 4636.0308 | 4690.5724
11 | 0.65995 | 1979.8579 | 2045.8531 | 2111.8484 | 2177.8437 | 2243.8389 | 2309.8342 | 2375.8294 | 2441.8247 | 2507.82 | 2573.8152 | 2639.8105 | 2705.8058 | 2771.801 | 2837.7963 | 2903.7915 | 2969.7868 | 3035.7821 | 3101.7773 | 3167.7726 | 3233.7679 | 3299.7631 | 3365.7584 | 3431.7536 | 3497.7489 | 3563.7442 | 3629.7394 | 3695.7347 | 3761.73 | 3827.7252 | 3893.7205 | 3959.7157 | 4025.711 | 4091.7063 | 4157.7015 | 4223.6968 | 4289.6921 | 4355.6873 | 4421.6826 | 4487.6778 | 4553.6731 | 4619.6684 | 4685.6636 | 4751.6589 | 4817.6542 | 4883.6494 | 4949.6447 | 5015.6399 | 5081.6352 | 5147.6305 | 5213.6257 | 5279.621 | 5345.6162 | 5411.6115 | 5477.6068 | 5543.602 | 5609.5973 | 5675.5926
12 | 0.7854 | 2356.1945 | 2434.7343 | 2513.2741 | 2591.8139 | 2670.3538 | 2748.8936 | 2827.4334 | 2905.9732 | 2984.513 | 3063.0528 | 3141.5927 | 3220.1325 | 3298.6723 | 3377.2121 | 3455.7519 | 3534.2917 | 3612.8316 | 3691.3714 | 3769.9112 | 3848.451 | 3926.9908 | 4005.5306 | 4084.0704 | 4162.6103 | 4241.1501 | 4319.6899 | 4398.2297 | 4476.7695 | 4555.3093 | 4633.8492 | 4712.389 | 4790.9288 | 4869.4686 | 4948.0084 | 5026.5482 | 5105.0881 | 5183.6279 | 5262.1677 | 5340.7075 | 5419.2473 | 5497.7871 | 5576.327 | 5654.8668 | 5733.4066 | 5811.9464 | 5890.4862 | 5969.026 | 6047.5659 | 6126.1057 | 6204.6455 | 6283.1853 | 6361.7251 | 6440.2649 | 6518.8048 | 6597.3446 | 6675.8844 | 6754.4242
13 | 0.92175 | 2765.256 | 2857.4312 | 2949.6064 | 3041.7816 | 3133.9568 | 3226.132 | 3318.3072 | 3410.4824 | 3502.6576 | 3594.8328 | 3687.008 | 3779.1832 | 3871.3584 | 3963.5336 | 4055.7088 | 4147.8841 | 4240.0593 | 4332.2345 | 4424.4097 | 4516.5849 | 4608.7601 | 4700.9353 | 4793.1105 | 4885.2857 | 4977.4609 | 5069.6361 | 5161.8113 | 5253.9865 | 5346.1617 | 5438.3369 | 5530.5121 | 5622.6873 | 5714.8625 | 5807.0377 | 5899.2129 | 5991.3881 | 6083.5633 | 6175.7385 | 6267.9137 | 6360.0889 | 6452.2641 | 6544.4393 | 6636.6145 | 6728.7897 | 6820.9649 | 6913.1401 | 7005.3153 | 7097.4905 | 7189.6657 | 7281.8409 | 7374.0161 | 7466.1913 | 7558.3665 | 7650.5417 | 7742.7169 | 7834.8921 | 7927.0673
14 | 1.069 | 3207.0425 | 3313.9439 | 3420.8453 | 3527.7468 | 3634.6482 | 3741.5496 | 3848.451 | 3955.3524 | 4062.2538 | 4169.1553 | 4276.0567 | 4382.9581 | 4489.8595 | 4596.7609 | 4703.6623 | 4810.5638 | 4917.4652 | 5024.3666 | 5131.268 | 5238.1694 | 5345.0708 | 5451.9723 | 5558.8737 | 5665.7751 | 5772.6765 | 5879.5779 | 5986.4793 | 6093.3808 | 6200.2822 | 6307.1836 | 6414.085 | 6520.9864 | 6627.8878 | 6734.7893 | 6841.6907 | 6948.5921 | 7055.4935 | 7162.3949 | 7269.2963 | 7376.1978 | 7483.0992 | 7590.0006 | 7696.902 | 7803.8034 | 7910.7048 | 8017.6063 | 8124.5077 | 8231.4091 | 8338.3105 | 8445.2119 | 8552.1133 | 8659.0148 | 8765.9162 | 8872.8176 | 8979.719 | 9086.6204 | 9193.5218
15 | 1.2272 | 3681.5539 | 3804.2724 | 3926.9908 | 4049.7093 | 4172.4277 | 4295.1462 | 4417.8647 | 4540.5831 | 4663.3016 | 4786.0201 | 4908.7385 | 5031.457 | 5154.1754 | 5276.8939 | 5399.6124 | 5522.3308 | 5645.0493 | 5767.7678 | 5890.4862 | 6013.2047 | 6135.9232 | 6258.6416 | 6381.3601 | 6504.0785 | 6626.797 | 6749.5155 | 6872.2339 | 6994.9524 | 7117.6709 | 7240.3893 | 7363.1078 | 7485.8262 | 7608.5447 | 7731.2632 | 7853.9816 | 7976.7001 | 8099.4186 | 8222.137 | 8344.8555 | 8467.5739 | 8590.2924 | 8713.0109 | 8835.7293 | 8958.4478 | 9081.1663 | 9203.8847 | 9326.6032 | 9449.3217 | 9572.0401 | 9694.7586 | 9817.477 | 9940.1955 | 10062.914 | 10185.6324 | 10308.3509 | 10431.0694 | 10553.7878
16 | 1.3963 | 4188.7902 | 4328.4165 | 4468.0429 | 4607.6692 | 4747.2956 | 4886.9219 | 5026.5482 | 5166.1746 | 5305.8009 | 5445.4273 | 5585.0536 | 5724.6799 | 5864.3063 | 6003.9326 | 6143.559 | 6283.1853 | 6422.8116 | 6562.438 | 6702.0643 | 6841.6907 | 6981.317 | 7120.9433 | 7260.5697 | 7400.196 | 7539.8224 | 7679.4487 | 7819.075 | 7958.7014 | 8098.3277 | 8237.9541 | 8377.5804 | 8517.2067 | 8656.8331 | 8796.4594 | 8936.0858 | 9075.7121 | 9215.3385 | 9354.9648 | 9494.5911 | 9634.2175 | 9773.8438 | 9913.4702 | 10053.0965 | 10192.7228 | 10332.3492 | 10471.9755 | 10611.6019 | 10751.2282 | 10890.8545 | 11030.4809 | 11170.1072 | 11309.7336 | 11449.3599 | 11588.9862 | 11728.6126 | 11868.2389 | 12007.8653
17 | 1.5763 | 4728.7514 | 4886.3765 | 5044.0015 | 5201.6266 | 5359.2516 | 5516.8767 | 5674.5017 | 5832.1268 | 5989.7518 | 6147.3769 | 6305.0019 | 6462.627 | 6620.252 | 6777.8771 | 6935.5021 | 7093.1272 | 7250.7522 | 7408.3773 | 7566.0023 | 7723.6274 | 7881.2524 | 8038.8775 | 8196.5025 | 8354.1275 | 8511.7526 | 8669.3776 | 8827.0027 | 8984.6277 | 9142.2528 | 9299.8778 | 9457.5029 | 9615.1279 | 9772.753 | 9930.378 | 10088.0031 | 10245.6281 | 10403.2532 | 10560.8782 | 10718.5033 | 10876.1283 | 11033.7534 | 11191.3784 | 11349.0035 | 11506.6285 | 11664.2536 | 11821.8786 | 11979.5037 | 12137.1287 | 12294.7537 | 12452.3788 | 12610.0038 | 12767.6289 | 12925.2539 | 13082.879 | 13240.504 | 13398.1291 | 13555.7541
18 | 1.7671 | 5301.4376 | 5478.1522 | 5654.8668 | 5831.5814 | 6008.2959 | 6185.0105 | 6361.7251 | 6538.4397 | 6715.1543 | 6891.8689 | 7068.5835 | 7245.2981 | 7422.0126 | 7598.7272 | 7775.4418 | 7952.1564 | 8128.871 | 8305.5856 | 8482.3002 | 8659.0148 | 8835.7293 | 9012.4439 | 9189.1585 | 9365.8731 | 9542.5877 | 9719.3023 | 9896.0169 | 10072.7314 | 10249.446 | 10426.1606 | 10602.8752 | 10779.5898 | 10956.3044 | 11133.019 | 11309.7336 | 11486.4481 | 11663.1627 | 11839.8773 | 12016.5919 | 12193.3065 | 12370.0211 | 12546.7357 | 12723.4502 | 12900.1648 | 13076.8794 | 13253.594 | 13430.3086 | 13607.0232 | 13783.7378 | 13960.4524 | 14137.1669 | 14313.8815 | 14490.5961 | 14667.3107 | 14844.0253 | 15020.7399 | 15197.4545
20 | 2.1817 | 6544.9847 | 6763.1509 | 6981.317 | 7199.4832 | 7417.6493 | 7635.8155 | 7853.9816 | 8072.1478 | 8290.3139 | 8508.4801 | 8726.6463 | 8944.8124 | 9162.9786 | 9381.1447 | 9599.3109 | 9817.477 | 10035.6432 | 10253.8094 | 10471.9755 | 10690.1417 | 10908.3078 | 11126.474 | 11344.6401 | 11562.8063 | 11780.9725 | 11999.1386 | 12217.3048 | 12435.4709 | 12653.6371 | 12871.8032 | 13089.9694 | 13308.1355 | 13526.3017 | 13744.4679 | 13962.634 | 14180.8002 | 14398.9663 | 14617.1325 | 14835.2986 | 15053.4648 | 15271.631 | 15489.7971 | 15707.9633 | 15926.1294 | 16144.2956 | 16362.4617 | 16580.6279 | 16798.7941 | 17016.9602 | 17235.1264 | 17453.2925 | 17671.4587 | 17889.6248 | 18107.791 | 18325.9571 | 18544.1233 | 18762.2895
22 | 2.6398 | 7919.4315 | 8183.4125 | 8447.3936 | 8711.3746 | 8975.3557 | 9239.3367 | 9503.3178 | 9767.2988 | 10031.2799 | 10295.2609 | 10559.242 | 10823.223 | 11087.2041 | 11351.1851 | 11615.1662 | 11879.1472 | 12143.1283 | 12407.1093 | 12671.0904 | 12935.0714 | 13199.0525 | 13463.0335 | 13727.0146 | 13990.9956 | 14254.9767 | 14518.9577 | 14782.9388 | 15046.9198 | 15310.9009 | 15574.8819 | 15838.863 | 16102.844 | 16366.8251 | 16630.8061 | 16894.7872 | 17158.7682 | 17422.7493 | 17686.7303 | 17950.7114 | 18214.6924 | 18478.6735 | 18742.6545 | 19006.6356 | 19270.6166 | 19534.5977 | 19798.5787 | 20062.5598 | 20326.5408 | 20590.5219 | 20854.5029 | 21118.4839 | 21382.465 | 21646.446 | 21910.4271 | 22174.4081 | 22438.3892 | 22702.3702
24 | 3.1416 | 9424.778 | 9738.9372 | 10053.0965 | 10367.2558 | 10681.415 | 10995.5743 | 11309.7336 | 11623.8928 | 11938.0521 | 12252.2113 | 12566.3706 | 12880.5299 | 13194.6891 | 13508.8484 | 13823.0077 | 14137.1669 | 14451.3262 | 14765.4855 | 15079.6447 | 15393.804 | 15707.9633 | 16022.1225 | 16336.2818 | 16650.4411 | 16964.6003 | 17278.7596 | 17592.9189 | 17907.0781 | 18221.2374 | 18535.3967 | 18849.5559 | 19163.7152 | 19477.8745 | 19792.0337 | 20106.193 | 20420.3522 | 20734.5115 | 21048.6708 | 21362.83 | 21676.9893 | 21991.1486 | 22305.3078 | 22619.4671 | 22933.6264 | 23247.7856 | 23561.9449 | 23876.1042 | 24190.2634 | 24504.4227 | 24818.582 | 25132.7412 | 25446.9005 | 25761.0598 | 26075.219 | 26389.3783 | 26703.5376 | 27017.6968
26 | 3.687 | 11061.0241 | 11429.7249 | 11798.4257 | 12167.1265 | 12535.8274 | 12904.5282 | 13273.229 | 13641.9298 | 14010.6306 | 14379.3314 | 14748.0322 | 15116.733 | 15485.4338 | 15854.1346 | 16222.8354 | 16591.5362 | 16960.237 | 17328.9378 | 17697.6386 | 18066.3394 | 18435.0402 | 18803.741 | 19172.4418 | 19541.1426 | 19909.8434 | 20278.5442 | 20647.2451 | 21015.9459 | 21384.6467 | 21753.3475 | 22122.0483 | 22490.7491 | 22859.4499 | 23228.1507 | 23596.8515 | 23965.5523 | 24334.2531 | 24702.9539 | 25071.6547 | 25440.3555 | 25809.0563 | 26177.7571 | 26546.4579 | 26915.1587 | 27283.8595 | 27652.5603 | 28021.2611 | 28389.9619 | 28758.6627 | 29127.3636 | 29496.0644 | 29864.7652 | 30233.466 | 30602.1668 | 30970.8676 | 31339.5684 | 31708.2692
28 | 4.2761 | 12828.17 | 13255.7757 | 13683.3813 | 14110.987 | 14538.5927 | 14966.1983 | 15393.804 | 15821.4097 | 16249.0153 | 16676.621 | 17104.2267 | 17531.8323 | 17959.438 | 18387.0437 | 18814.6493 | 19242.255 | 19669.8607 | 20097.4663 | 20525.072 | 20952.6777 | 21380.2833 | 21807.889 | 22235.4947 | 22663.1003 | 23090.706 | 23518.3117 | 23945.9173 | 24373.523 | 24801.1287 | 25228.7343 | 25656.34 | 26083.9457 | 26511.5513 | 26939.157 | 27366.7627 | 27794.3683 | 28221.974 | 28649.5797 | 29077.1853 | 29504.791 | 29932.3967 | 30360.0023 | 30787.608 | 31215.2137 | 31642.8193 | 32070.425 | 32498.0307 | 32925.6363 | 33353.242 | 33780.8477 | 34208.4533 | 34636.059 | 35063.6647 | 35491.2703 | 35918.876 | 36346.4817 | 36774.0873
30 | 4.9087 | 14726.2156 | 15217.0894 | 15707.9633 | 16198.8371 | 16689.711 | 17180.5848 | 17671.4587 | 18162.3325 | 18653.2064 | 19144.0802 | 19634.9541 | 20125.8279 | 20616.7018 | 21107.5756 | 21598.4495 | 22089.3233 | 22580.1972 | 23071.071 | 23561.9449 | 24052.8188 | 24543.6926 | 25034.5665 | 25525.4403 | 26016.3142 | 26507.188 | 26998.0619 | 27488.9357 | 27979.8096 | 28470.6834 | 28961.5573 | 29452.4311 | 29943.305 | 30434.1788 | 30925.0527 | 31415.9265 | 31906.8004 | 32397.6742 | 32888.5481 | 33379.4219 | 33870.2958 | 34361.1696 | 34852.0435 | 35342.9174 | 35833.7912 | 36324.6651 | 36815.5389 | 37306.4128 | 37797.2866 | 38288.1605 | 38779.0343 | 39269.9082 | 39760.782 | 40251.6559 | 40742.5297 | 41233.4036 | 41724.2774 | 42215.1513
32 | 5.5851 | 16755.1608 | 17313.6662 | 17872.1715 | 18430.6769 | 18989.1823 | 19547.6876 | 20106.193 | 20664.6983 | 21223.2037 | 21781.7091 | 22340.2144 | 22898.7198 | 23457.2251 | 24015.7305 | 24574.2359 | 25132.7412 | 25691.2466 | 26249.7519 | 26808.2573 | 27366.7627 | 27925.268 | 28483.7734 | 29042.2788 | 29600.7841 | 30159.2895 | 30717.7948 | 31276.3002 | 31834.8056 | 32393.3109 | 32951.8163 | 33510.3216 | 34068.827 | 34627.3324 | 35185.8377 | 35744.3431 | 36302.8484 | 36861.3538 | 37419.8592 | 37978.3645 | 38536.8699 | 39095.3752 | 39653.8806 | 40212.386 | 40770.8913 | 41329.3967 | 41887.902 | 42446.4074 | 43004.9128 | 43563.4181 | 44121.9235 | 44680.4289 | 45238.9342 | 45797.4396 | 46355.9449 | 46914.4503 | 47472.9557 | 48031.461
34 | 6.305 | 18915.0058 | 19545.506 | 20176.0062 | 20806.5063 | 21437.0065 | 22067.5067 | 22698.0069 | 23328.5071 | 23959.0073 | 24589.5075 | 25220.0077 | 25850.5079 | 26481.0081 | 27111.5083 | 27742.0085 | 28372.5087 | 29003.0088 | 29633.509 | 30264.0092 | 30894.5094 | 31525.0096 | 32155.5098 | 32786.01 | 33416.5102 | 34047.0104 | 34677.5106 | 35308.0108 | 35938.511 | 36569.0112 | 37199.5113 | 37830.0115 | 38460.5117 | 39091.0119 | 39721.5121 | 40352.0123 | 40982.5125 | 41613.0127 | 42243.5129 | 42874.0131 | 43504.5133 | 44135.0135 | 44765.5137 | 45396.0138 | 46026.514 | 46657.0142 | 47287.5144 | 47918.0146 | 48548.5148 | 49179.015 | 49809.5152 | 50440.0154 | 51070.5156 | 51701.0158 | 52331.516 | 52962.0162 | 53592.5163 | 54223.0165
36 | 7.0686 | 21205.7504 | 21912.6088 | 22619.4671 | 23326.3255 | 24033.1838 | 24740.0421 | 25446.9005 | 26153.7588 | 26860.6172 | 27567.4755 | 28274.3339 | 28981.1922 | 29688.0506 | 30394.9089 | 31101.7673 | 31808.6256 | 32515.484 | 33222.3423 | 33929.2007 | 34636.059 | 35342.9174 | 36049.7757 | 36756.634 | 37463.4924 | 38170.3507 | 38877.2091 | 39584.0674 | 40290.9258 | 40997.7841 | 41704.6425 | 42411.5008 | 43118.3592 | 43825.2175 | 44532.0759 | 45238.9342 | 45945.7926 | 46652.6509 | 47359.5093 | 48066.3676 | 48773.2259 | 49480.0843 | 50186.9426 | 50893.801 | 51600.6593 | 52307.5177 | 53014.376 | 53721.2344 | 54428.0927 | 55134.9511 | 55841.8094 | 56548.6678 | 57255.5261 | 57962.3845 | 58669.2428 | 59376.1012 | 60082.9595 | 60789.8178
38 | 7.8758 | 23627.3947 | 24414.9746 | 25202.5544 | 25990.1342 | 26777.714 | 27565.2939 | 28352.8737 | 29140.4535 | 29928.0333 | 30715.6132 | 31503.193 | 32290.7728 | 33078.3526 | 33865.9325 | 34653.5123 | 35441.0921 | 36228.6719 | 37016.2518 | 37803.8316 | 38591.4114 | 39378.9912 | 40166.5711 | 40954.1509 | 41741.7307 | 42529.3105 | 43316.8904 | 44104.4702 | 44892.05 | 45679.6298 | 46467.2097 | 47254.7895 | 48042.3693 | 48829.9491 | 49617.529 | 50405.1088 | 51192.6886 | 51980.2684 | 52767.8483 | 53555.4281 | 54343.0079 | 55130.5877 | 55918.1676 | 56705.7474 | 57493.3272 | 58280.907 | 59068.4869 | 59856.0667 | 60643.6465 | 61431.2263 | 62218.8062 | 63006.386 | 63793.9658 | 64581.5456 | 65369.1255 | 66156.7053 | 66944.2851 | 67731.8649
40 | 8.7266 | 26179.9388 | 27052.6034 | 27925.268 | 28797.9327 | 29670.5973 | 30543.2619 | 31415.9265 | 32288.5912 | 33161.2558 | 34033.9204 | 34906.585 | 35779.2497 | 36651.9143 | 37524.5789 | 38397.2435 | 39269.9082 | 40142.5728 | 41015.2374 | 41887.902 | 42760.5667 | 43633.2313 | 44505.8959 | 45378.5606 | 46251.2252 | 47123.8898 | 47996.5544 | 48869.2191 | 49741.8837 | 50614.5483 | 51487.2129 | 52359.8776 | 53232.5422 | 54105.2068 | 54977.8714 | 55850.5361 | 56723.2007 | 57595.8653 | 58468.5299 | 59341.1946 | 60213.8592 | 61086.5238 | 61959.1884 | 62831.8531 | 63704.5177 | 64577.1823 | 65449.8469 | 66322.5116 | 67195.1762 | 68067.8408 | 68940.5055 | 69813.1701 | 70685.8347 | 71558.4993 | 72431.164 | 73303.8286 | 74176.4932 | 75049.1578
42 | 9.6211 | 28863.3825 | 29825.4953 | 30787.608 | 31749.7208 | 32711.8335 | 33673.9463 | 34636.059 | 35598.1718 | 36560.2845 | 37522.3973 | 38484.51 | 39446.6228 | 40408.7355 | 41370.8483 | 42332.961 | 43295.0738 | 44257.1865 | 45219.2993 | 46181.412 | 47143.5248 | 48105.6375 | 49067.7503 | 50029.863 | 50991.9758 | 51954.0885 | 52916.2013 | 53878.314 | 54840.4268 | 55802.5395 | 56764.6523 | 57726.765 | 58688.8778 | 59650.9905 | 60613.1033 | 61575.216 | 62537.3288 | 63499.4415 | 64461.5543 | 65423.667 | 66385.7798 | 67347.8925 | 68310.0053 | 69272.118 | 70234.2308 | 71196.3435 | 72158.4563 | 73120.569 | 74082.6818 | 75044.7945 | 76006.9073 | 76969.02 | 77931.1328 | 78893.2455 | 79855.3583 | 80817.471 | 81779.5838 | 82741.6965
44 | 10.5592 | 31677.7259 | 32733.6501 | 33789.5743 | 34845.4985 | 35901.4227 | 36957.3469 | 38013.2711 | 39069.1953 | 40125.1195 | 41181.0437 | 42236.9679 | 43292.8921 | 44348.8163 | 45404.7405 | 46460.6647 | 47516.5889 | 48572.5131 | 49628.4373 | 50684.3615 | 51740.2857 | 52796.2099 | 53852.1341 | 54908.0583 | 55963.9825 | 57019.9067 | 58075.8309 | 59131.7551 | 60187.6793 | 61243.6035 | 62299.5276 | 63355.4518 | 64411.376 | 65467.3002 | 66523.2244 | 67579.1486 | 68635.0728 | 69690.997 | 70746.9212 | 71802.8454 | 72858.7696 | 73914.6938 | 74970.618 | 76026.5422 | 77082.4664 | 78138.3906 | 79194.3148 | 80250.239 | 81306.1632 | 82362.0874 | 83418.0116 | 84473.9358 | 85529.86 | 86585.7842 | 87641.7084 | 88697.6326 | 89753.5568 | 90809.481
46 | 11.541 | 34622.969 | 35777.068 | 36931.167 | 38085.2659 | 39239.3649 | 40393.4639 | 41547.5628 | 42701.6618 | 43855.7608 | 45009.8597 | 46163.9587 | 47318.0577 | 48472.1567 | 49626.2556 | 50780.3546 | 51934.4536 | 53088.5525 | 54242.6515 | 55396.7505 | 56550.8494 | 57704.9484 | 58859.0474 | 60013.1463 | 61167.2453 | 62321.3443 | 63475.4432 | 64629.5422 | 65783.6412 | 66937.7401 | 68091.8391 | 69245.9381 | 70400.037 | 71554.136 | 72708.235 | 73862.3339 | 75016.4329 | 76170.5319 | 77324.6308 | 78478.7298 | 79632.8288 | 80786.9278 | 81941.0267 | 83095.1257 | 84249.2247 | 85403.3236 | 86557.4226 | 87711.5216 | 88865.6205 | 90019.7195 | 91173.8185 | 92327.9174 | 93482.0164 | 94636.1154 | 95790.2143 | 96944.3133 | 98098.4123 | 99252.5112
48 | 12.5664 | 37699.1118 | 38955.7489 | 40212.386 | 41469.023 | 42725.6601 | 43982.2972 | 45238.9342 | 46495.5713 | 47752.2083 | 49008.8454 | 50265.4825 | 51522.1195 | 52778.7566 | 54035.3936 | 55292.0307 | 56548.6678 | 57805.3048 | 59061.9419 | 60318.5789 | 61575.216 | 62831.8531 | 64088.4901 | 65345.1272 | 66601.7643 | 67858.4013 | 69115.0384 | 70371.6754 | 71628.3125 | 72884.9496 | 74141.5866 | 75398.2237 | 76654.8607 | 77911.4978 | 79168.1349 | 80424.7719 | 81681.409 | 82938.0461 | 84194.6831 | 85451.3202 | 86707.9572 | 87964.5943 | 89221.2314 | 90477.8684 | 91734.5055 | 92991.1425 | 94247.7796 | 95504.4167 | 96761.0537 | 98017.6908 | 99274.3279 | 100530.9649 | 101787.602 | 103044.239 | 104300.8761 | 105557.5132 | 106814.1502 | 108070.7873
50 | 13.6354 | 40906.1543 | 42269.6928 | 43633.2313 | 44996.7698 | 46360.3083 | 47723.8467 | 49087.3852 | 50450.9237 | 51814.4622 | 53178.0006 | 54541.5391 | 55905.0776 | 57268.6161 | 58632.1546 | 59995.693 | 61359.2315 | 62722.77 | 64086.3085 | 65449.8469 | 66813.3854 | 68176.9239 | 69540.4624 | 70904.0009 | 72267.5393 | 73631.0778 | 74994.6163 | 76358.1548 | 77721.6933 | 79085.2317 | 80448.7702 | 81812.3087 | 83175.8472 | 84539.3856 | 85902.9241 | 87266.4626 | 88630.0011 | 89993.5396 | 91357.078 | 92720.6165 | 94084.155 | 95447.6935 | 96811.2319 | 98174.7704 | 99538.3089 | 100901.8474 | 102265.3859 | 103628.9243 | 104992.4628 | 106356.0013 | 107719.5398 | 109083.0782 | 110446.6167 | 111810.1552 | 113173.6937 | 114537.2322 | 115900.7706 | 117264.3091
52 | 14.748 | 44244.0965 | 45718.8998 | 47193.703 | 48668.5062 | 50143.3094 | 51618.1126 | 53092.9158 | 54567.7191 | 56042.5223 | 57517.3255 | 58992.1287 | 60466.9319 | 61941.7352 | 63416.5384 | 64891.3416 | 66366.1448 | 67840.948 | 69315.7512 | 70790.5545 | 72265.3577 | 73740.1609 | 75214.9641 | 76689.7673 | 78164.5706 | 79639.3738 | 81114.177 | 82588.9802 | 84063.7834 | 85538.5866 | 87013.3899 | 88488.1931 | 89962.9963 | 91437.7995 | 92912.6027 | 94387.4059 | 95862.2092 | 97337.0124 | 98811.8156 | 100286.6188 | 101761.422 | 103236.2253 | 104711.0285 | 106185.8317 | 107660.6349 | 109135.4381 | 110610.2413 | 112085.0446 | 113559.8478 | 115034.651 | 116509.4542 | 117984.2574 | 119459.0607 | 120933.8639 | 122408.6671 | 123883.4703 | 125358.2735 | 126833.0767
54 | 15.9043 | 47712.9384 | 49303.3697 | 50893.801 | 52484.2323 | 54074.6635 | 55665.0948 | 57255.5261 | 58845.9574 | 60436.3887 | 62026.82 | 63617.2512 | 65207.6825 | 66798.1138 | 68388.5451 | 69978.9764 | 71569.4076 | 73159.8389 | 74750.2702 | 76340.7015 | 77931.1328 | 79521.564 | 81111.9953 | 82702.4266 | 84292.8579 | 85883.2892 | 87473.7204 | 89064.1517 | 90654.583 | 92245.0143 | 93835.4456 | 95425.8769 | 97016.3081 | 98606.7394 | 100197.1707 | 101787.602 | 103378.0333 | 104968.4645 | 106558.8958 | 108149.3271 | 109739.7584 | 111330.1897 | 112920.6209 | 114511.0522 | 116101.4835 | 117691.9148 | 119282.3461 | 120872.7773 | 122463.2086 | 124053.6399 | 125644.0712 | 127234.5025 | 128824.9338 | 130415.365 | 132005.7963 | 133596.2276 | 135186.6589 | 136777.0902
56 | 17.1042 | 51312.68 | 53023.1027 | 54733.5253 | 56443.948 | 58154.3707 | 59864.7933 | 61575.216 | 63285.6387 | 64996.0613 | 66706.484 | 68416.9067 | 70127.3293 | 71837.752 | 73548.1747 | 75258.5973 | 76969.02 | 78679.4427 | 80389.8653 | 82100.288 | 83810.7107 | 85521.1333 | 87231.556 | 88941.9787 | 90652.4013 | 92362.824 | 94073.2467 | 95783.6693 | 97494.092 | 99204.5147 | 100914.9374 | 102625.36 | 104335.7827 | 106046.2054 | 107756.628 | 109467.0507 | 111177.4734 | 112887.896 | 114598.3187 | 116308.7414 | 118019.164 | 119729.5867 | 121440.0094 | 123150.432 | 124860.8547 | 126571.2774 | 128281.7 | 129992.1227 | 131702.5454 | 133412.968 | 135123.3907 | 136833.8134 | 138544.236 | 140254.6587 | 141965.0814 | 143675.504 | 145385.9267 | 147096.3494
58 | 18.3478 | 55043.3213 | 56878.0987 | 58712.876 | 60547.6534 | 62382.4308 | 64217.2082 | 66051.9855 | 67886.7629 | 69721.5403 | 71556.3177 | 73391.095 | 75225.8724 | 77060.6498 | 78895.4272 | 80730.2046 | 82564.9819 | 84399.7593 | 86234.5367 | 88069.3141 | 89904.0914 | 91738.8688 | 93573.6462 | 95408.4236 | 97243.2009 | 99077.9783 | 100912.7557 | 102747.5331 | 104582.3104 | 106417.0878 | 108251.8652 | 110086.6426 | 111921.4199 | 113756.1973 | 115590.9747 | 117425.7521 | 119260.5295 | 121095.3068 | 122930.0842 | 124764.8616 | 126599.639 | 128434.4163 | 130269.1937 | 132103.9711 | 133938.7485 | 135773.5258 | 137608.3032 | 139443.0806 | 141277.858 | 143112.6353 | 144947.4127 | 146782.1901 | 148616.9675 | 150451.7448 | 152286.5222 | 154121.2996 | 155956.077 | 157790.8543
60 | 19.635 | 58904.8623 | 60868.3577 | 62831.8531 | 64795.3485 | 66758.8439 | 68722.3393 | 70685.8347 | 72649.3301 | 74612.8255 | 76576.3209 | 78539.8163 | 80503.3117 | 82466.8072 | 84430.3026 | 86393.798 | 88357.2934 | 90320.7888 | 92284.2842 | 94247.7796 | 96211.275 | 98174.7704 | 100138.2658 | 102101.7612 | 104065.2567 | 106028.7521 | 107992.2475 | 109955.7429 | 111919.2383 | 113882.7337 | 115846.2291 | 117809.7245 | 119773.2199 | 121736.7153 | 123700.2107 | 125663.7061 | 127627.2016 | 129590.697 | 131554.1924 | 133517.6878 | 135481.1832 | 137444.6786 | 139408.174 | 141371.6694 | 143335.1648 | 145298.6602 | 147262.1556 | 149225.651 | 151189.1465 | 153152.6419 | 155116.1373 | 157079.6327 | 159043.1281 | 161006.6235 | 162970.1189 | 164933.6143 | 166897.1097 | 168860.6051
62 | 20.9658 | 62897.3029 | 64993.8797 | 67090.4564 | 69187.0332 | 71283.61 | 73380.1867 | 75476.7635 | 77573.3403 | 79669.917 | 81766.4938 | 83863.0706 | 85959.6473 | 88056.2241 | 90152.8009 | 92249.3776 | 94345.9544 | 96442.5311 | 98539.1079 | 100635.6847 | 102732.2614 | 104828.8382 | 106925.415 | 109021.9917 | 111118.5685 | 113215.1453 | 115311.722 | 117408.2988 | 119504.8755 | 121601.4523 | 123698.0291 | 125794.6058 | 127891.1826 | 129987.7594 | 132084.3361 | 134180.9129 | 136277.4897 | 138374.0664 | 140470.6432 | 142567.2199 | 144663.7967 | 146760.3735 | 148856.9502 | 150953.527 | 153050.1038 | 155146.6805 | 157243.2573 | 159339.8341 | 161436.4108 | 163532.9876 | 165629.5644 | 167726.1411 | 169822.7179 | 171919.2946 | 174015.8714 | 176112.4482 | 178209.0249 | 180305.6017
64 | 22.3402 | 67020.6433 | 69254.6647 | 71488.6862 | 73722.7076 | 75956.729 | 78190.7505 | 80424.7719 | 82658.7934 | 84892.8148 | 87126.8363 | 89360.8577 | 91594.8791 | 93828.9006 | 96062.922 | 98296.9435 | 100530.9649 | 102764.9864 | 104999.0078 | 107233.0292 | 109467.0507 | 111701.0721 | 113935.0936 | 116169.115 | 118403.1365 | 120637.1579 | 122871.1793 | 125105.2008 | 127339.2222 | 129573.2437 | 131807.2651 | 134041.2866 | 136275.308 | 138509.3294 | 140743.3509 | 142977.3723 | 145211.3938 | 147445.4152 | 149679.4367 | 151913.4581 | 154147.4795 | 156381.501 | 158615.5224 | 160849.5439 | 163083.5653 | 165317.5867 | 167551.6082 | 169785.6296 | 172019.6511 | 174253.6725 | 176487.694 | 178721.7154 | 180955.7368 | 183189.7583 | 185423.7797 | 187657.8012 | 189891.8226 | 192125.8441
66 | 23.7583 | 71274.8833 | 73650.7128 | 76026.5422 | 78402.3717 | 80778.2011 | 83154.0305 | 85529.86 | 87905.6894 | 90281.5189 | 92657.3483 | 95033.1778 | 97409.0072 | 99784.8367 | 102160.6661 | 104536.4955 | 106912.325 | 109288.1544 | 111663.9839 | 114039.8133 | 116415.6428 | 118791.4722 | 121167.3017 | 123543.1311 | 125918.9605 | 128294.79 | 130670.6194 | 133046.4489 | 135422.2783 | 137798.1078 | 140173.9372 | 142549.7667 | 144925.5961 | 147301.4255 | 149677.255 | 152053.0844 | 154428.9139 | 156804.7433 | 159180.5728 | 161556.4022 | 163932.2317 | 166308.0611 | 168683.8905 | 171059.72 | 173435.5494 | 175811.3789 | 178187.2083 | 180563.0378 | 182938.8672 | 185314.6967 | 187690.5261 | 190066.3555 | 192442.185 | 194818.0144 | 197193.8439 | 199569.6733 | 201945.5028 | 204321.3322
68 | 25.22 | 75660.0231 | 78182.0238 | 80704.0246 | 83226.0254 | 85748.0262 | 88270.0269 | 90792.0277 | 93314.0285 | 95836.0292 | 98358.03 | 100880.0308 | 103402.0315 | 105924.0323 | 108446.0331 | 110968.0338 | 113490.0346 | 116012.0354 | 118534.0361 | 121056.0369 | 123578.0377 | 126100.0385 | 128622.0392 | 131144.04 | 133666.0408 | 136188.0415 | 138710.0423 | 141232.0431 | 143754.0438 | 146276.0446 | 148798.0454 | 151320.0461 | 153842.0469 | 156364.0477 | 158886.0485 | 161408.0492 | 163930.05 | 166452.0508 | 168974.0515 | 171496.0523 | 174018.0531 | 176540.0538 | 179062.0546 | 181584.0554 | 184106.0561 | 186628.0569 | 189150.0577 | 191672.0585 | 194194.0592 | 196716.06 | 199238.0608 | 201760.0615 | 204282.0623 | 206804.0631 | 209326.0638 | 211848.0646 | 214370.0654 | 216892.0661
70 | 26.7254 | 80176.0625 | 82848.5979 | 85521.1333 | 88193.6688 | 90866.2042 | 93538.7396 | 96211.275 | 98883.8104 | 101556.3459 | 104228.8813 | 106901.4167 | 109573.9521 | 112246.4875 | 114919.0229 | 117591.5584 | 120264.0938 | 122936.6292 | 125609.1646 | 128281.7 | 130954.2354 | 133626.7709 | 136299.3063 | 138971.8417 | 141644.3771 | 144316.9125 | 146989.4479 | 149661.9834 | 152334.5188 | 155007.0542 | 157679.5896 | 160352.125 | 163024.6604 | 165697.1959 | 168369.7313 | 171042.2667 | 173714.8021 | 176387.3375 | 179059.8729 | 181732.4084 | 184404.9438 | 187077.4792 | 189750.0146 | 192422.55 | 195095.0854 | 197767.6209 | 200440.1563 | 203112.6917 | 205785.2271 | 208457.7625 | 211130.298 | 213802.8334 | 216475.3688 | 219147.9042 | 221820.4396 | 224492.975 | 227165.5105 | 229838.0459
72 | 28.2743 | 84823.0016 | 87650.435 | 90477.8684 | 93305.3018 | 96132.7352 | 98960.1686 | 101787.602 | 104615.0354 | 107442.4688 | 110269.9021 | 113097.3355 | 115924.7689 | 118752.2023 | 121579.6357 | 124407.0691 | 127234.5025 | 130061.9359 | 132889.3692 | 135716.8026 | 138544.236 | 141371.6694 | 144199.1028 | 147026.5362 | 149853.9696 | 152681.403 | 155508.8364 | 158336.2697 | 161163.7031 | 163991.1365 | 166818.5699 | 169646.0033 | 172473.4367 | 175300.8701 | 178128.3035 | 180955.7368 | 183783.1702 | 186610.6036 | 189438.037 | 192265.4704 | 195092.9038 | 197920.3372 | 200747.7706 | 203575.204 | 206402.6373 | 209230.0707 | 212057.5041 | 214884.9375 | 217712.3709 | 220539.8043 | 223367.2377 | 226194.6711 | 229022.1044 | 231849.5378 | 234676.9712 | 237504.4046 | 240331.838 | 243159.2714
74 | 29.8669 | 89600.8405 | 92587.5352 | 95574.2298 | 98560.9245 | 101547.6192 | 104534.3139 | 107521.0086 | 110507.7033 | 113494.3979 | 116481.0926 | 119467.7873 | 122454.482 | 125441.1767 | 128427.8713 | 131414.566 | 134401.2607 | 137387.9554 | 140374.6501 | 143361.3448 | 146348.0394 | 149334.7341 | 152321.4288 | 155308.1235 | 158294.8182 | 161281.5129 | 164268.2075 | 167254.9022 | 170241.5969 | 173228.2916 | 176214.9863 | 179201.6809 | 182188.3756 | 185175.0703 | 188161.765 | 191148.4597 | 194135.1544 | 197121.849 | 200108.5437 | 203095.2384 | 206081.9331 | 209068.6278 | 212055.3225 | 215042.0171 | 218028.7118 | 221015.4065 | 224002.1012 | 226988.7959 | 229975.4906 | 232962.1852 | 235948.8799 | 238935.5746 | 241922.2693 | 244908.964 | 247895.6586 | 250882.3533 | 253869.048 | 256855.7427
76 | 31.5032 | 94509.579 | 97659.8983 | 100810.2176 | 103960.5369 | 107110.8562 | 110261.1755 | 113411.4948 | 116561.8141 | 119712.1334 | 122862.4527 | 126012.772 | 129163.0913 | 132313.4106 | 135463.7299 | 138614.0492 | 141764.3685 | 144914.6878 | 148065.0071 | 151215.3264 | 154365.6457 | 157515.965 | 160666.2843 | 163816.6036 | 166966.9229 | 170117.2422 | 173267.5615 | 176417.8808 | 179568.2001 | 182718.5194 | 185868.8387 | 189019.158 | 192169.4773 | 195319.7966 | 198470.1159 | 201620.4352 | 204770.7545 | 207921.0738 | 211071.3931 | 214221.7124 | 217372.0317 | 220522.351 | 223672.6703 | 226822.9896 | 229973.3089 | 233123.6282 | 236273.9475 | 239424.2668 | 242574.5861 | 245724.9054 | 248875.2247 | 252025.544 | 255175.8633 | 258326.1826 | 261476.5019 | 264626.8212 | 267777.1405 | 270927.4598
78 | 33.1831 | 99549.2172 | 102867.5245 | 106185.8317 | 109504.1389 | 112822.4462 | 116140.7534 | 119459.0607 | 122777.3679 | 126095.6751 | 129413.9824 | 132732.2896 | 136050.5969 | 139368.9041 | 142687.2113 | 146005.5186 | 149323.8258 | 152642.1331 | 155960.4403 | 159278.7475 | 162597.0548 | 165915.362 | 169233.6693 | 172551.9765 | 175870.2837 | 179188.591 | 182506.8982 | 185825.2055 | 189143.5127 | 192461.8199 | 195780.1272 | 199098.4344 | 202416.7417 | 205735.0489 | 209053.3561 | 212371.6634 | 215689.9706 | 219008.2779 | 222326.5851 | 225644.8923 | 228963.1996 | 232281.5068 | 235599.8141 | 238918.1213 | 242236.4285 | 245554.7358 | 248873.043 | 252191.3503 | 255509.6575 | 258827.9647 | 262146.272 | 265464.5792 | 268782.8865 | 272101.1937 | 275419.5009 | 278737.8082 | 282056.1154 | 285374.4227
80 | 34.9066 | 104719.7551 | 108210.4136 | 111701.0721 | 115191.7306 | 118682.3891 | 122173.0476 | 125663.7061 | 129154.3646 | 132645.0232 | 136135.6817 | 139626.3402 | 143116.9987 | 146607.6572 | 150098.3157 | 153588.9742 | 157079.6327 | 160570.2912 | 164060.9497 | 167551.6082 | 171042.2667 | 174532.9252 | 178023.5837 | 181514.2422 | 185004.9007 | 188495.5592 | 191986.2177 | 195476.8762 | 198967.5347 | 202458.1932 | 205948.8517 | 209439.5102 | 212930.1687 | 216420.8272 | 219911.4858 | 223402.1443 | 226892.8028 | 230383.4613 | 233874.1198 | 237364.7783 | 240855.4368 | 244346.0953 | 247836.7538 | 251327.4123 | 254818.0708 | 258308.7293 | 261799.3878 | 265290.0463 | 268780.7048 | 272271.3633 | 275762.0218 | 279252.6803 | 282743.3388 | 286233.9973 | 289724.6558 | 293215.3143 | 296705.9728 | 300196.6313
82 | 36.6737 | 110021.1927 | 113688.5658 | 117355.9389 | 121023.312 | 124690.6851 | 128358.0582 | 132025.4313 | 135692.8044 | 139360.1774 | 143027.5505 | 146694.9236 | 150362.2967 | 154029.6698 | 157697.0429 | 161364.416 | 165031.7891 | 168699.1622 | 172366.5353 | 176033.9084 | 179701.2814 | 183368.6545 | 187036.0276 | 190703.4007 | 194370.7738 | 198038.1469 | 201705.52 | 205372.8931 | 209040.2662 | 212707.6393 | 216375.0124 | 220042.3854 | 223709.7585 | 227377.1316 | 231044.5047 | 234711.8778 | 238379.2509 | 242046.624 | 245713.9971 | 249381.3702 | 253048.7433 | 256716.1164 | 260383.4894 | 264050.8625 | 267718.2356 | 271385.6087 | 275052.9818 | 278720.3549 | 282387.728 | 286055.1011 | 289722.4742 | 293389.8473 | 297057.2204 | 300724.5934 | 304391.9665 | 308059.3396 | 311726.7127 | 315394.0858
84 | 38.4845 | 115453.53 | 119301.981 | 123150.432 | 126998.883 | 130847.334 | 134695.785 | 138544.236 | 142392.687 | 146241.138 | 150089.589 | 153938.04 | 157786.491 | 161634.942 | 165483.393 | 169331.844 | 173180.295 | 177028.746 | 180877.197 | 184725.648 | 188574.099 | 192422.55 | 196271.001 | 200119.452 | 203967.903 | 207816.354 | 211664.805 | 215513.256 | 219361.707 | 223210.158 | 227058.609 | 230907.06 | 234755.511 | 238603.962 | 242452.413 | 246300.864 | 250149.315 | 253997.766 | 257846.217 | 261694.668 | 265543.119 | 269391.57 | 273240.021 | 277088.472 | 280936.923 | 284785.374 | 288633.825 | 292482.276 | 296330.727 | 300179.1781 | 304027.6291 | 307876.0801 | 311724.5311 | 315572.9821 | 319421.4331 | 323269.8841 | 327118.3351 | 330966.7861
86 | 40.3389 | 121016.767 | 125050.6592 | 129084.5515 | 133118.4437 | 137152.3359 | 141186.2282 | 145220.1204 | 149254.0126 | 153287.9049 | 157321.7971 | 161355.6893 | 165389.5816 | 169423.4738 | 173457.366 | 177491.2583 | 181525.1505 | 185559.0427 | 189592.935 | 193626.8272 | 197660.7194 | 201694.6117 | 205728.5039 | 209762.3962 | 213796.2884 | 217830.1806 | 221864.0729 | 225897.9651 | 229931.8573 | 233965.7496 | 237999.6418 | 242033.534 | 246067.4263 | 250101.3185 | 254135.2107 | 258169.103 | 262202.9952 | 266236.8874 | 270270.7797 | 274304.6719 | 278338.5641 | 282372.4564 | 286406.3486 | 290440.2408 | 294474.1331 | 298508.0253 | 302541.9175 | 306575.8098 | 310609.702 | 314643.5942 | 318677.4865 | 322711.3787 | 326745.2709 | 330779.1632 | 334813.0554 | 338846.9476 | 342880.8399 | 346914.7321
88 | 42.237 | 126710.9037 | 130934.6005 | 135158.2973 | 139381.9941 | 143605.6909 | 147829.3876 | 152053.0844 | 156276.7812 | 160500.478 | 164724.1748 | 168947.8716 | 173171.5684 | 177395.2652 | 181618.962 | 185842.6588 | 190066.3555 | 194290.0523 | 198513.7491 | 202737.4459 | 206961.1427 | 211184.8395 | 215408.5363 | 219632.2331 | 223855.9299 | 228079.6267 | 232303.3234 | 236527.0202 | 240750.717 | 244974.4138 | 249198.1106 | 253421.8074 | 257645.5042 | 261869.201 | 266092.8978 | 270316.5945 | 274540.2913 | 278763.9881 | 282987.6849 | 287211.3817 | 291435.0785 | 295658.7753 | 299882.4721 | 304106.1689 | 308329.8657 | 312553.5624 | 316777.2592 | 321000.956 | 325224.6528 | 329448.3496 | 333672.0464 | 337895.7432 | 342119.44 | 346343.1368 | 350566.8336 | 354790.5303 | 359014.2271 | 363237.9239
90 | 44.1786 | 132535.9401 | 136953.8047 | 141371.6694 | 145789.5341 | 150207.3987 | 154625.2634 | 159043.1281 | 163460.9928 | 167878.8574 | 172296.7221 | 176714.5868 | 181132.4514 | 185550.3161 | 189968.1808 | 194386.0454 | 198803.9101 | 203221.7748 | 207639.6394 | 212057.5041 | 216475.3688 | 220893.2335 | 225311.0981 | 229728.9628 | 234146.8275 | 238564.6921 | 242982.5568 | 247400.4215 | 251818.2861 | 256236.1508 | 260654.0155 | 265071.8801 | 269489.7448 | 273907.6095 | 278325.4742 | 282743.3388 | 287161.2035 | 291579.0682 | 295996.9328 | 300414.7975 | 304832.6622 | 309250.5268 | 313668.3915 | 318086.2562 | 322504.1208 | 326921.9855 | 331339.8502 | 335757.7149 | 340175.5795 | 344593.4442 | 349011.3089 | 353429.1735 | 357847.0382 | 362264.9029 | 366682.7675 | 371100.6322 | 375518.4969 | 379936.3615
92 | 46.164 | 138491.8761 | 143108.272 | 147724.6679 | 152341.0638 | 156957.4596 | 161573.8555 | 166190.2514 | 170806.6472 | 175423.0431 | 180039.439 | 184655.8349 | 189272.2307 | 193888.6266 | 198505.0225 | 203121.4183 | 207737.8142 | 212354.2101 | 216970.606 | 221587.0018 | 226203.3977 | 230819.7936 | 235436.1894 | 240052.5853 | 244668.9812 | 249285.3771 | 253901.7729 | 258518.1688 | 263134.5647 | 267750.9605 | 272367.3564 | 276983.7523 | 281600.1482 | 286216.544 | 290832.9399 | 295449.3358 | 300065.7316 | 304682.1275 | 309298.5234 | 313914.9193 | 318531.3151 | 323147.711 | 327764.1069 | 332380.5027 | 336996.8986 | 341613.2945 | 346229.6904 | 350846.0862 | 355462.4821 | 360078.878 | 364695.2739 | 369311.6697 | 373928.0656 | 378544.4615 | 383160.8573 | 387777.2532 | 392393.6491 | 397010.045
94 | 48.1929 | 144578.7119 | 149398.0023 | 154217.2927 | 159036.5831 | 163855.8735 | 168675.1639 | 173494.4543 | 178313.7447 | 183133.0351 | 187952.3255 | 192771.6159 | 197590.9063 | 202410.1967 | 207229.4871 | 212048.7775 | 216868.0679 | 221687.3583 | 226506.6487 | 231325.9391 | 236145.2295 | 240964.5199 | 245783.8103 | 250603.1006 | 255422.391 | 260241.6814 | 265060.9718 | 269880.2622 | 274699.5526 | 279518.843 | 284338.1334 | 289157.4238 | 293976.7142 | 298796.0046 | 303615.295 | 308434.5854 | 313253.8758 | 318073.1662 | 322892.4566 | 327711.747 | 332531.0374 | 337350.3278 | 342169.6182 | 346988.9086 | 351808.199 | 356627.4894 | 361446.7798 | 366266.0702 | 371085.3606 | 375904.651 | 380723.9414 | 385543.2318 | 390362.5222 | 395181.8126 | 400001.103 | 404820.3934 | 409639.6838 | 414458.9741
96 | 50.2655 | 150796.4474 | 155822.9956 | 160849.5439 | 165876.0921 | 170902.6404 | 175929.1886 | 180955.7368 | 185982.2851 | 191008.8333 | 196035.3816 | 201061.9298 | 206088.4781 | 211115.0263 | 216141.5746 | 221168.1228 | 226194.6711 | 231221.2193 | 236247.7675 | 241274.3158 | 246300.864 | 251327.4123 | 256353.9605 | 261380.5088 | 266407.057 | 271433.6053 | 276460.1535 | 281486.7018 | 286513.25 | 291539.7983 | 296566.3465 | 301592.8947 | 306619.443 | 311645.9912 | 316672.5395 | 321699.0877 | 326725.636 | 331752.1842 | 336778.7325 | 341805.2807 | 346831.829 | 351858.3772 | 356884.9254 | 361911.4737 | 366938.0219 | 371964.5702 | 376991.1184 | 382017.6667 | 387044.2149 | 392070.7632 | 397097.3114 | 402123.8597 | 407150.4079 | 412176.9562 | 417203.5044 | 422230.0526 | 427256.6009 | 432283.1491
98 | 52.3817 | 157145.0825 | 162383.2519 | 167621.4214 | 172859.5908 | 178097.7602 | 183335.9296 | 188574.099 | 193812.2684 | 199050.4379 | 204288.6073 | 209526.7767 | 214764.9461 | 220003.1155 | 225241.285 | 230479.4544 | 235717.6238 | 240955.7932 | 246193.9626 | 251432.132 | 256670.3015 | 261908.4709 | 267146.6403 | 272384.8097 | 277622.9791 | 282861.1485 | 288099.318 | 293337.4874 | 298575.6568 | 303813.8262 | 309051.9956 | 314290.1651 | 319528.3345 | 324766.5039 | 330004.6733 | 335242.8427 | 340481.0121 | 345719.1816 | 350957.351 | 356195.5204 | 361433.6898 | 366671.8592 | 371910.0286 | 377148.1981 | 382386.3675 | 387624.5369 | 392862.7063 | 398100.8757 | 403339.0452 | 408577.2146 | 413815.384 | 419053.5534 | 424291.7228 | 429529.8922 | 434768.0617 | 440006.2311 | 445244.4005 | 450482.5699
100 | 54.5415 | 163624.6174 | 169078.7713 | 174532.9252 | 179987.0791 | 185441.233 | 190895.3869 | 196349.5408 | 201803.6948 | 207257.8487 | 212712.0026 | 218166.1565 | 223620.3104 | 229074.4643 | 234528.6182 | 239982.7721 | 245436.9261 | 250891.08 | 256345.2339 | 261799.3878 | 267253.5417 | 272707.6956 | 278161.8495 | 283616.0034 | 289070.1574 | 294524.3113 | 299978.4652 | 305432.6191 | 310886.773 | 316340.9269 | 321795.0808 | 327249.2347 | 332703.3887 | 338157.5426 | 343611.6965 | 349065.8504 | 354520.0043 | 359974.1582 | 365428.3121 | 370882.466 | 376336.62 | 381790.7739 | 387244.9278 | 392699.0817 | 398153.2356 | 403607.3895 | 409061.5434 | 414515.6973 | 419969.8513 | 425424.0052 | 430878.1591 | 436332.313 | 441786.4669 | 447240.6208 | 452694.7747 | 458148.9286 | 463603.0826 | 469057.2365
102 | 56.745 | 170235.0519 | 175909.5536 | 181584.0554 | 187258.5571 | 192933.0588 | 198607.5606 | 204282.0623 | 209956.564 | 215631.0658 | 221305.5675 | 226980.0692 | 232654.571 | 238329.0727 | 244003.5744 | 249678.0761 | 255352.5779 | 261027.0796 | 266701.5813 | 272376.0831 | 278050.5848 | 283725.0865 | 289399.5883 | 295074.09 | 300748.5917 | 306423.0934 | 312097.5952 | 317772.0969 | 323446.5986 | 329121.1004 | 334795.6021 | 340470.1038 | 346144.6056 | 351819.1073 | 357493.609 | 363168.1108 | 368842.6125 | 374517.1142 | 380191.6159 | 385866.1177 | 391540.6194 | 397215.1211 | 402889.6229 | 408564.1246 | 414238.6263 | 419913.1281 | 425587.6298 | 431262.1315 | 436936.6333 | 442611.135 | 448285.6367 | 453960.1384 | 459634.6402 | 465309.1419 | 470983.6436 | 476658.1454 | 482332.6471 | 488007.1488
104 | 58.9921 | 176976.3862 | 182875.599 | 188774.8119 | 194674.0248 | 200573.2376 | 206472.4505 | 212371.6634 | 218270.8763 | 224170.0891 | 230069.302 | 235968.5149 | 241867.7277 | 247766.9406 | 253666.1535 | 259565.3664 | 265464.5792 | 271363.7921 | 277263.005 | 283162.2178 | 289061.4307 | 294960.6436 | 300859.8565 | 306759.0693 | 312658.2822 | 318557.4951 | 324456.7079 | 330355.9208 | 336255.1337 | 342154.3466 | 348053.5594 | 353952.7723 | 359851.9852 | 365751.198 | 371650.4109 | 377549.6238 | 383448.8367 | 389348.0495 | 395247.2624 | 401146.4753 | 407045.6882 | 412944.901 | 418844.1139 | 424743.3268 | 430642.5396 | 436541.7525 | 442440.9654 | 448340.1783 | 454239.3911 | 460138.604 | 466037.8169 | 471937.0297 | 477836.2426 | 483735.4555 | 489634.6684 | 495533.8812 | 501433.0941 | 507332.307
106 | 61.2829 | 183848.6201 | 189976.9074 | 196105.1948 | 202233.4821 | 208361.7694 | 214490.0568 | 220618.3441 | 226746.6314 | 232874.9188 | 239003.2061 | 245131.4934 | 251259.7808 | 257388.0681 | 263516.3555 | 269644.6428 | 275772.9301 | 281901.2175 | 288029.5048 | 294157.7921 | 300286.0795 | 306414.3668 | 312542.6541 | 318670.9415 | 324799.2288 | 330927.5161 | 337055.8035 | 343184.0908 | 349312.3782 | 355440.6655 | 361568.9528 | 367697.2402 | 373825.5275 | 379953.8148 | 386082.1022 | 392210.3895 | 398338.6768 | 404466.9642 | 410595.2515 | 416723.5389 | 422851.8262 | 428980.1135 | 435108.4009 | 441236.6882 | 447364.9755 | 453493.2629 | 459621.5502 | 465749.8375 | 471878.1249 | 478006.4122 | 484134.6995 | 490262.9869 | 496391.2742 | 502519.5616 | 508647.8489 | 514776.1362 | 520904.4236 | 527032.7109
108 | 63.6173 | 190851.7537 | 197213.4788 | 203575.204 | 209936.9291 | 216298.6542 | 222660.3793 | 229022.1044 | 235383.8296 | 241745.5547 | 248107.2798 | 254469.0049 | 260830.7301 | 267192.4552 | 273554.1803 | 279915.9054 | 286277.6306 | 292639.3557 | 299001.0808 | 305362.8059 | 311724.5311 | 318086.2562 | 324447.9813 | 330809.7064 | 337171.4315 | 343533.1567 | 349894.8818 | 356256.6069 | 362618.332 | 368980.0572 | 375341.7823 | 381703.5074 | 388065.2325 | 394426.9577 | 400788.6828 | 407150.4079 | 413512.133 | 419873.8582 | 426235.5833 | 432597.3084 | 438959.0335 | 445320.7586 | 451682.4838 | 458044.2089 | 464405.934 | 470767.6591 | 477129.3843 | 483491.1094 | 489852.8345 | 496214.5596 | 502576.2848 | 508938.0099 | 515299.735 | 521661.4601 | 528023.1853 | 534384.9104 | 540746.6355 | 547108.3606

## Project information
How the duct systems needs to be quoted | [12 empty] | What to quote | What to quote | How the duct systems needs to be quoted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How the duct systems needs to be quoted |  |  |  | The quoted duct system includes
[14 empty] | What is included | 0 | 0 | 0 | 0 | Standard Gauge | 0 | Rolled Lip / Clamp-Together | 0 | 0 | 0 |  |  | Standard Gauge | Rolled Lip / Clamp-Together |  |  | Standard Gauge | Rolled Lip / Clamp-Together
[15 empty] | 0 | 0 | 0 | 0 | 20 Gauge | 0 | Flanged Duct | 0 | 0 | 0 |  |  | 20 Gauge | Flanged Duct |  |  | 20 Gauge | Flanged Duct
[10 empty] | Date | 2024-02-19 |  |  |  | 0 | 0 | 0 | 0 | 18 Gauge | 0 | Tubing | 0 | 0 | 0 |  |  | 18 Gauge | Tubing |  |  | 18 Gauge | Tubing
[15 empty] | 0 | 0 | 0 | 0 | 16 Gauge | 0 | Mix of different style duct | 0 | 0 | 0 |  |  | 16 Gauge | Mix of different style duct |  |  | 16 Gauge | Mix of different style duct
|  | Quote # | Indust Sol #1 |  | Amout of CFM | [9 empty] | 0 | 0 | 0 | 0 | 14 Gauge | 0 | See notes | 0 | 0 | 0 |  |  | 14 Gauge | See notes |  |  | 14 Gauge | See notes
[15 empty] | 0 | 0 | 0 | 0 | 12 Gauge | 0 | 0 | 0 | 0 | 0 |  |  | 12 Gauge |  |  |  | 12 Gauge
|  | Blast Gated System (yes/no) | No |  | Desired Velocity |  | FPM | Style | Mix of different style duct | [5 empty] | 0 | 0 | 0 | 0 | 10 Gauge | 0 | 0 | 0 | 0 | 0 |  |  | 10 Gauge |  |  |  | 10 Gauge
[15 empty] | 0 | 0 | 0 | 0 | Mix of different gauges | 0 | 0 | 0 | 0 | 0 |  |  | Mix of different gauges |  |  |  | Mix of different gauges
|  | Include Cut Offs (Blast Gates) | No |  | Hangers | No hangers included |  |  | Material | Galvanized |  |  |  |  | Yes | 0 | 0 | 0 | See notes | 0 | 0 | 0 | 0 | 0 | Yes |  | See notes |  | Yes |  | See notes
[15 empty] | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  |  |  | No
|  | Hard pipe or flex hose connections | Flex Hose |  | Wall Flashing | No wall flashing included |  |  | Gauge | Standard Gauge |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | How many feet per drop | 3 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Branches | Only 45 degree branches |  |  | Ball Joints for CNC | No CNC |  |  |  |  | Flex Hose | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Flex Hose |  |  |  | Flex Hose
|  | Desired trunk line height | 12 FT | [11 empty] | Machine adapter | 0 | 0 | Galvanized | 0 | 0 | No CNC | 0 | 0 | 0 | Machine adapter | Galvanized |  | No CNC | Machine adapter | Galvanized |  | No CNC
[5 empty] | Special notes | No Return Air Duct included | [8 empty] | RAW ends | 0 | 0 | SS304 | 0 | 0 | No ball joint needed on CNC | 0 | 0 | 0 | RAW ends | SS304 |  | No ball joint needed on CNC | RAW ends | SS304 |  | No ball joint included on CNC
|  | Pieces of 5ft duct per drop | 2 | [11 empty] | Mix of different ends | 0 | 0 | SS316 | 0 | 0 | Ball Joint with Rolled Lips | 0 | 0 | 0 | Mix of different ends | SS316 |  | Ball Joint with Rolled Lips | Mix of different ends | SS316 |  | Ball Joint with Rolled Lips
[15 empty] | See notes | 0 | 0 | 0 | 0 | 0 | Ball Joint with RL on top and RAW bottom | 0 | 0 | 0 |  |  |  | Ball Joint with RL on top and RAW bottom |  |  |  | Ball Joint with RL on top and RAW bottom
|  | Amount of Floor Sweeps | None | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | See notes | 0 | 0 | 0 |  |  |  | See notes |  |  |  | See notes
[15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | No hangers needed | 0 | 0 | No wall flashing needed | 0 | 0 | 0 | 0 | 0 | 0 | No hangers needed | No wall flashing needed |  |  | No hangers included | No wall flashing included
[15 empty] | Cable Hangers needed | 0 | 0 | Yes wall flashing needed | 0 | 0 | 0 | 0 | 0 | 0 | Cable Hangers needed | Yes wall flashing needed |  |  | Cable Hangers included | Yes wall flashing included
|  | If any machines have HORIZONTAL outlets please fill out the amount of each diameter below in order to make sure a 90 degree elbow will be included | [12 empty] | Other hangers needed | 0 | 0 | See notes | 0 | 0 | 0 | 0 | 0 | 0 | Other hangers needed | See notes |  |  | Other hangers included | See notes
| (Help for manual take offs as well) |  |  | Parts that will be included for the vertical drops | [10 empty] | See notes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See notes |  |  |  | See notes
|  |  | Amount of drops |  | Amount of | Amount of | Amount of | Amount of | Amount of | Amount of | Amount of | Amount of |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diameter | Amount of drops | needing 90 deg | Diameter | Cut Offs | Duct | Adj Sleeve | 90 (45) Deg | Hose Adapt | Worm Clamps | Flex Hose | Machine Adapt |  |  | 0 | 0 | 0 | Only 45 degree branches | 0 | 0 | 0 | 0 | 0 | 0 |  | Only 45 degree branches |  |  |  | Only 45 degree branches
|  |  | elbows at bottom | [11 empty] | 0 | 0 | 0 | Only 30 degree branches | 0 | 0 | 0 | 0 | 0 | 0 |  | Only 30 degree branches |  |  |  | Only 30 degree branches
| 3" |  |  | 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | Both 30 and 45 degrees | 0 | 0 | 0 | 0 | 0 | 0 |  | Both 30 and 45 degrees |  |  |  | Both 30 and 45 degrees
| 4" | 8 |  | 4" | 0 | 16 | 8 | 8 | 8 | 16 | 25 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5" | 1 |  | 5" | 0 | 2 | 1 | 1 | 1 | 2 | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6" | 7 |  | 6" | 0 | 14 | 7 | 7 | 7 | 14 | 25 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7" |  |  | 7" | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8" |  |  | 8" | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9" |  |  | 9" | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10" |  |  | 10" | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11" |  |  | 11" | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 12" |  |  | 12" | 0 | 0 | 0 | 0 | 0 | 0 | 0