## Instructions
Step 1 | Print 1 inspection sheet for every fire hydrant and fill in the information for
each one. Put the sheets in a binder and you are ready to begin.
Step 2 | Fill in the 1st column of the inspection sheet with the data from your
inspection/flow testing
Step 3 | After flow testing fire hydrants the testing data can be entered into the
"BLUE CELLS" on the 20 PSI Flow Tab. The Yellow number or calculated
flow rate should be entered into the last line on your inspection sheet.
Make sure the color codes are correct and re-paint if needed.
Step 4 | Make a list of hydrant problems and get them fixed and/or painted A.S.A.P.
The Calculated fow rate at 20 psi is used to color code the fire hydrants.
COLOR CODING CHART
RED……….......Below 500 GPM
ORANGE…......500 - 999 GPM
GREEN………..1,000 - 1,499 GPM
LIGHT BLUE....1,500 GPM or MORE

## Definitions
Useful definitions for the inspection sheet
Municipality | The Water System Name
Hydrant Number | The assigned number for that particular hydrant
Location | The physical address of the hydrant
GPS | The GPS coodinates of the hydrant
Make | The Manufacturer of the hydrant
Model | The manufacturers model number for the hydrant
Year | The year the hydrant was made
Size | The nominal size of the hydrant (i.e. 4-1/2 or 5-1/4)
2-1/4" Nozzles | How many 2-1/4" nozzles does the hydrant have
Steamer Nozzles | How many larger nozzles does the hydrant have
Opens | Clockwise or Counter Clockwise
Size Main Line | What size is the water main that the hydrant is on
Flow Color | Designates the flow rate at 20 psi (see bottom of Inspection sheet)
Date | The date of the current inspection
Paint | The overall condition of the paint
Caps | The condition of all the nozzle caps (i.e. Working, Cross threaded, Needs gasket)
Chains | The condition of the chains holding the nozzle caps
Operating nut | The condition of the operating nut on top of the hydrant
Lubricant | Did you lubricate the hydrant upon inspection
Valve Operation | How easy was the hydrant to open and close
Valve seat | Did the hydrant close completely
Weep hole | Did the fire hydrant drain out the weep hole after closing
Static pressure | The pressure at the hydrant with no flow
Residual pressure | The pressure at the hydrant with the water flowing wide open
Secondary Residual PSI | The pressure at the closest hydrant up stream while flowing water from the test hydrant
Flow Rate in GPM | How many Gallons Per Minute the hydrant flows while wide open
Minutes Flushed | How many minutes was the hydrant flowing water
Inspected By | The Initials of the inspector
Flow rate at 20 PSI | The calculated flow rate for the hydrant from the "20 PSI Flow" tab
Inspected By | The Initials of the inspector

## Inspection
HYDRANT INSPECTION REPORT
Municipality- |  |  |  |  | Hydrant Number-
Location- |  |  |  | GPS-
Make- |  |  |  | Model- |  |  | Year-
Size- |  |  | Qty. 2 1/2" Nozzles- |  |  |  | Steamer Nozzles-
Opens- |  |  | Size Main Line- |  |  |  | Flow Color-
When flowing hydrants, DO NOT let pressure fall below 20 psi
Condition and Inspection Dates
Date………………
Paint
Caps
Chains
Operating Nut
Lubricant
Valve Operation
Valve Seat
Weep Hole
Static Pressure
Residual Pressure
Secondary Rsdl. PSI
Flow Rate in GPM
Minutes Flushed
Inspected By
Flow Rate @ 20 PSI
Condition Abbreviations
| Abbreviation |  | Stands For
| OK………………… |  | Satisfactory Condition
| P…………………… |  | Poor Condition
| NR…………………. |  | Needs Repaired A.S.A.P. (Broken)
Color Codes for Hydrants
| BLACK….. | Dead or Unusable Hydrants
Body only, for all hydrants on lines smaller than 6"
| RED…….. | Below 500 GPM |  |  | GREEN…. | 1,000 - 1,499 GPM
| ORANGE. | 500 - 999 GPM |  |  | Light Blue… | 1,500 GPM or MORE

## 20 PSI Flow
Hydrant Flow at 20 PSI calculator |  |  | PF= | 20
Static Pressure (Still) | 140 | PSI
Residual Pressure (Running) | 60 | PSI
Gallons per Minute | 900
1.5
Calculated Flow at 20 PSI | 1120.2934 | GPM