## Information
#VALUE!
Single Hydrant Testing and Inpecting Spreadsheet
PSC Rule §150-7-12 Compliant
1. All information should be entered into the Testing Report tab.
2. Dates that are Red need to be tested or inspected
3. Entering the flow rate will automatically tell you what color the hydrant needs to be and what hydrant classification it is.
4. You can hide Notes column to print the Testing Report
5. The Testing Procedure and Inspection Procedure tabs can be edited to fit your needs as long as it complies with rule 12.8

## Inspection Procedure
HYDRANT INSPECTION PROCEDURE (DRY-BARREL) Write any issues in the Note section of the Testing Report Tab
1. Hydrant Appearance
a. Remove obstructions around the hydrant
b. Paint/mark the hydrant if needed
c. Check the hydrant's clearance from the surface of the ground. If the hydrant needs to be raised or lowered due to
surface changes then ensure the work is performed or scheduled
2. If the hydrant is a traffic model, check the breakaway device for any damage.
3. Remove one outlet-nozzle cap and use a listening device to check for main valve leaks.
4. Check for the presence of water or ice in the hydrant barrel by use of a plumb-bob or other suitable means.
5. Attach a section of fire hose or other detector to protect the street, traffic, and private property from water expelled at
high velocity.
6. Open the hydrant and flush to remove foreign material from the interior and lead.
7. Close the hydrant
a. Remove the deflector and check to operation of the drain valve by placing the palm of one hand over the outlet nozzle.
b. Drainage should be sufficiently rapid to create noticeable suction.
c. For no-drain hydrants, pump the water from the barrel.
8. Using a listening device, check the main valve for leakage.
9. Replace the outlet-nozzle cap. Leave it loose enough to allow air to escape.
10. Open the hydrant only a few turns. Allow air to vent from the outlet-nozzle cap.
11. Tighten the outlet-nozzle cap.
12. Check hydrant lubrication.
a. Open hydrant fully, check for ease of operation.
b. Check for hard-water buildup on the threads or stem threads.
c. Check for stuck packing and bent stems.
13. With the hydrant fully open, check for leakage at flanges, around outlet nozzles, at packing or seals, and around the
operating stem. Repair as needed.
14. Partially close the hydrant so the drains open and water flows through under pressure for approximately 10 seconds,
flushing the drain outlets.
15. Close the hydrant completely. Back off the operating nut enough to take pressure off of the thrust bearing or packing.
16. Remove all outlet-nozzle caps, clean the threads, check the condition of the gaskets, and lubricate the threads. Check
the ease of operation of each cap.
17. Check outlet-nozzle cap chains for free action on each cap. If the chains bind, open the loop around the cap until they
move freely. This will keep the chains from kinking when the cap is removed during an emergency.
18. Replace the caps. Tighten them, and then back off slightly so they will not be excessively tight. Leave them tight enough
to prevent their removal by hand.
19. Check the lubrication of operating-nut threads. Lubricate per the manufacturer's recommendations.
20. Locate and exercise the auxiliary valve. Leave it in the open position.
21. If the hydrant is inoperable, bag it and notify the local 911 Call Center. Schedule the hydrant for prompt repair.

## Flow Testing Procedure
HYDRANT FLOW-TESTING PROCEDURE
1. Determine location and select the flow hydrant(s) for testing. Make notifications as required by these rules.
2. Determine number of flow hydrants:
a. This will depend on the flows required, and/or the strength and capacity of the local distribution system.
b. The number of flow hydrants should be sufficient to achieve a drop in res idual pressure, measured at the residual
hydrant, of at least ten percent (10%) of the static pressure.
c. Where the system pressure and flows may increase due to pump operation during testing, an artificial drop in the static
pressure of ten percent (10%) may be necessary for theoretical supply curve calculations.
3. For multiple-hydrant tests:
a. Designate one hydrant as the residual hydrant:
b. This is where the static pressure will be observed during the static conditions (all other flow hydrants closed) and the residual
conditions (all other test hydrants flowing.)
c. The reidual hydrant should be located such that it is positioned between the flow hydrant(s) and that portion of the distribution
system which supplies fire flows to the immediate area.
4. For single-hydrant tests:
4. For single-hydrant tests:
a. The same hydrant serves as both residual and flow hydrant.
b. Static and residual pressures are measured at one of the 2 1/2” nozzles on the hydrant.
c. A separate 2 1/2” nozzle on the same hydrant should be used for flow measurement.
5. Flow-test procedure:
a. Slowly open each hydrant or hydrants used in the test and flush them individually to remove debris or sediment that may
damage the pressure gauge or flow instruments.
b. Attach a pressure gauge to one of the 2.5-inch outlets on the residual hydrant.
c. Open the cock on the gauge piping.
d. Slowly open the residual hydrant to the full-open position.
e. Once all air is vented from the barrel, close the vent cock on the gauge piping.
f. Record the static pressure reading when the pressure gauge needle is stabilized.
g. For each flow hydrant to be used-measure and record the identification of the outlet nozzle from which the flow is measured.
The identification measurement is taken to the nearest 1/16 inch. Note the type of outlet (e.g. smooth-and-rounded,
square-and-sharp, sharp-and-pro,jecting, etc.) for calculation purposes.
h. Install one pitot tube with a pressure gauge to each flow hydrant. Alternative flow measurement methods, other than pitot tubes,
may be used provided that they give flow measurement results equal in accuracy to the pitot tube method.
i. Slowly open the flow hydrant. If multiple flow hydrants are being used, slowly open each flow hydrant one at a time. While
opening flow hydrant(s) always observe the residual pressure drop. Under no circumstances should the residual pressure be
allowed to fall below 20 psi.
j. When the flow hydrant(s) are flowing, allow enough flow to remove debris and sediment.
k. Record the pitot pressure of each flow hydrant(s) while simultaneously recording the pressure at the residual hydrant,
l. To ensure accurate results, the pressure drop between the static and residual pressures should be at least ten percent (10%) of
the static pressure.
m. After recording all readings, close each flow hydrant slowly, one at a time.
6. Determine the flow rate.
The formula to calculate the flow rate Q (gpm) is as follows:

## Testing Report
WVRWA Hydrant Testing
System Name:
System Address:
Date Inspected (Red Needs Inspected) | Date Tested (Red Needs Tested) | Hydrant | Manufacturer Information |  |  | Hydrant Location |  | Pipe Size | Static PSI | Residual PSI | Flow (GPM) | Hydrant | Notes
|  | ID# (Corresponds with Picture) | Brand | Size | Date | Latitude | Longitude |  |  |  |  | Classification | Maintenance and Repair Information (Write down any work that needs done or work that has been done)