## TDH
Total Dynamic Head Calculator
Project Name:
Date:
Created By:
Design Criteria
| Column Pipe Size (in) | 1.25
| Target Flow Rate (gpm) | 4
| Column Pipe Length (ft) | 0
| Operating Pressure (psi) | 0
| Pumping/Drawdown Level (ft) | 0
| PVC Pipeline Diameter (in) | 1.25
| Pipeline Length (ft) | 0
| Surface Elevation Change (ft) | 0
Total Dynamic Head Calculations
| Total Feet of Vertical Lift | 0
| Column Pipe Friction Loss (ft) | 0
| Pressure in Feet of Head | 0
| Pipeline Friction Loss (ft) | 0
| TDH (ft) | 0
Instructions for using this worksheet:
All items in GREEN and BLUE must be filled in by the user.
Select your Column Pipe Size, Target Flow Rate, Operating Pressure, and PVC Pipeline Size from the drop down list in the associated GREEN cells below.
Manually input your Column Pipe Length, Pipeline Length, Pumping Water Level, and Surface Elevation Change in the associated BLUE cells below.
Notes About This Worksheet:
Column pipe friction loss is based on steel pipe.
Pumping/Drawdown Level refers to water level below ground while pumping at desired flow rate, no the static water level.
PVC pipeline size refers to any above ground plumbing or underground PVC pipeline that the pump must push water through.
Surface elevation change is the total positive elevation change. Example: 20-feet of uphill increase followed by 10-feet of downhill decrease results in 10-feet of total positive elevation change.
Worksheet does not account for check valves, fittings, flowmeters, etc. If needed add equivalent length of pipe to the column pipe or PVC pipeline length.

## Flow Rates - Steel (hidden)
Typical flow rates in gallons per minute per available steel column pipe diameters.
1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 8
4 | 4 | 10 | 20 | 30 | 60 | 100 | 200 | 400
6 | 6 | 12 | 25 | 35 | 80 | 120 | 250 | 450
8 | 8 | 14 | 30 | 40 | 100 | 160 | 300 | 500
10 | 10 | 16 | 35 | 45 | 120 | 200 | 350 | 550
12 | 12 | 18 | 40 | 50 | 140 | 250 | 400 | 600
14 | 14 | 20 | 45 | 60 | 160 | 300 | 450 | 650
16 | 16 | 25 | 50 | 70 | 180 | 350 | 500 | 700
18 | 18 | 30 | 55 | 80 | 200 | 400 | 550 | 750
20 | 20 | 35 | 60 | 90 | 220 | 450 | 600 | 800
25 | 25 | 40 | 65 | 100 | 240 | 500 | 650 | 900
30 | 30 | 45 | 70 | 120 | 260 | 550 | 700 | 1000
35 | 35 | 50 | 75 | 140 | 280 | 600 | 750 | 1100
40 | 40 | 55 | 80 | 160 | 300 | 650 | 800 | 1200
45 | 45 | 60 | 85 | 180 | 320 | 700 | 850 | 1300
50 | 50 | 65 | 90 | 200 | 340 | 750 | 900 | 1400
| 55 | 70 | 95 | 220 | 360 | 800 | 950 | 1500
| 60 |  | 100 | 240 | 380 | 850 | 1000 | 1600
|  |  | 110 | 260 | 400 | 900 | 1100 | 1800
|  |  | 120 | 280 | 420 | 950 | 1200 | 2000
[5 empty] | 460 | 1000 | 1300 | 2200
[7 empty] | 1400 | 2400

## Friction Loss Chart - Steel (hidden)
Column pipe friction loss in feet of head per 100ft of pipe.
| 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 8
GPM | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft
4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3.1 | 1.5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4.3 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
14 | 5.7 | 2.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
16 | 7.3 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
18 | 9.1 | 4.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0
20 | 11.1 | 5.2 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0
25 | 16.8 | 8.5 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0
30 | 23.5 | 11.1 | 3.3 | 1.4 | 0.48 | 0 | 0 | 0 | 0
35 | 31.2 | 15.5 | 4.4 | 1.8 | 0.64 | 0 | 0 | 0 | 0
40 | 40 | 18.9 | 5.6 | 2.4 | 0.82 | 0 | 0 | 0 | 0
45 | 50 | 24.5 | 7 | 2.9 | 1 | 0 | 0 | 0 | 0
50 | 60.4 | 28.5 | 8.5 | 3.6 | 1.2 | 0 | 0 | 0 | 0
55 |  | 34 | 10.1 | 4.2 | 1.4 | 0 | 0 | 0 | 0
60 |  | 40 | 11.9 | 5 | 1.7 | 0.5 | 0 | 0 | 0
65 |  |  | 13.7 | 5.8 | 2 | 0.5 | 0 | 0 | 0
70 |  |  | 15.8 | 6.6 | 2.3 | 0.6 | 0 | 0 | 0
75 |  |  |  | 7.6 | 2.65 | 0.7 | 0 | 0 | 0
80 |  |  |  | 8.5 | 3 | 0.8 | 0 | 0 | 0
85 |  |  |  | 9.5 | 3.35 | 0.9 | 0 | 0 | 0
90 |  |  |  | 10.6 | 3.7 | 1 | 0 | 0 | 0
95 |  |  |  | 11.7 | 4.1 | 1.1 | 0 | 0 | 0
100 |  |  |  | 12.8 | 4.5 | 1.2 | 0.4 | 0 | 0
110 |  |  |  | 15.3 | 5.4 | 1.45 | 0.5 | 0 | 0
120 |  |  |  | 18 | 6.3 | 1.7 | 0.6 | 0 | 0
140 |  |  |  |  | 8.3 | 2.2 | 0.8 | 0 | 0
160 |  |  |  |  | 10.7 | 2.8 | 1 | 0 | 0
180 |  |  |  |  | 13.2 | 3.5 | 1.2 | 0 | 0
200 |  |  |  |  | 16.1 | 4.3 | 1.4 | 0.6 | 0
220 |  |  |  |  | 19.2 | 5.1 | 1.8 | 0.75 | 0
240 |  |  |  |  | 22.6 | 6 | 2.2 | 0.9 | 0
260 |  |  |  |  | 26.2 | 7 | 2.4 | 1 | 0
280 |  |  |  |  | 30 | 8 | 2.7 | 1.1 | 0
300 | [5 empty] | 9.1 | 3 | 1.2 | 0
320 | [5 empty] | 10.2 | 3.5 | 1.4 | 0
340 | [5 empty] | 11.5 | 4 | 1.6 | 0
360 | [5 empty] | 12.7 | 4.4 | 1.75 | 0
380 | [5 empty] | 14.1 | 4.8 | 1.9 | 0
400 | [5 empty] | 15.5 | 5.2 | 2.11 | 0.69
420 | [5 empty] | 16.9 | 5.8 | 2.36 | 0.78
460 | [5 empty] | 20 | 6.4 | 2.62 | 0.86
500 | [6 empty] | 7.8 | 3.19 | 1.05
550 | [6 empty] | 9.3 | 3.8 | 1.25
600 | [6 empty] | 10.9 | 4.46 | 1.46
650 | [6 empty] | 12.6 | 5.17 | 1.7
700 | [6 empty] | 14.5 | 5.93 | 1.95
750 | [6 empty] | 16.5 | 6.74 | 2.21
800 | [6 empty] | 18.6 | 7.6 | 2.49
850 | [6 empty] | 20.8 | 8.5 | 2.7
900 | [6 empty] | 23.1 | 9.44 | 3.1
950 | [6 empty] | 25.5 | 10.2 | 3.43
1000 | [6 empty] | 28.1 | 11.5 | 3.77
1100 | [7 empty] | 13.7 | 4.49
1200 | [7 empty] | 16.1 | 5.28
1300 | [7 empty] | 18.6 | 6.12
1400 | [7 empty] | 21.4 | 7.02
1500 | [8 empty] | 7.98
1600 | [8 empty] | 8.99
1700 | [8 empty] | 10
1800 | [8 empty] | 11.2
1900 | [8 empty] | 12.4
2000 | [8 empty] | 13.6
2100 | [8 empty] | 15.1
2200 | [8 empty] | 16.6
2300 | [8 empty] | 17.8
2400 | [8 empty] | 19

## Friction Loss Chart - PVC (hidden)
Schedule 40 PVC pipe friction loss in feet of head per 100ft of pipe.
| 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 8
GPM | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft | Head Loss Per 100ft
4 | 0.27 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0.57 | 0.26 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0.95 | 0.45 | 0.16 | 0.5 | 0 | 0 | 0 | 0 | 0
10 | 1.44 | 0.67 | 0.24 | 0.8 | 0.03 | 0 | 0 | 0 | 0
12 | 2.02 | 0.94 | 0.37 | 0.11 | 0.05 | 0 | 0 | 0 | 0
14 | 3.05 | 1.41 | 0.51 | 0.17 | 0.07 | 0 | 0 | 0 | 0
16 | 3.66 | 1.7 | 0.6 | 0.2 | 0.8 | 0 | 0 | 0 | 0
18 | 4.28 | 1.99 | 0.7 | 0.24 | 0.1 | 0 | 0 | 0 | 0
20 | 5.21 | 2.44 | 0.86 | 0.29 | 0.12 | 0.03 | 0 | 0 | 0
25 | 7.8 | 3.43 | 1.28 | 0.43 | 0.18 | 0.04 | 0 | 0 | 0
30 | 10.8 | 5.17 | 1.8 | 0.61 | 0.25 | 0.06 | 0.02 | 0 | 0
35 | 14.7 | 6.91 | 2.4 | 0.81 | 0.33 | 0.08 | 0.03 | 0 | 0
40 | 18.8 | 8.83 | 3.1 | 1.03 | 0.43 | 0.1 | 0.04 | 0 | 0
45 | 23.5 | 10.9 | 3.85 | 1.32 | 0.54 | 0.13 | 0.04 | 0 | 0
50 | 28.2 | 13.3 | 4.65 | 1.56 | 0.65 | 0.16 | 0.05 | 0.02 | 0
55 |  | 16 | 5.55 | 1.88 | 0.74 | 0.19 | 0.06 | 0.02 | 0
60 |  | 18.6 | 6.53 | 2.19 | 0.9 | 0.22 | 0.07 | 0.03 | 0
65 |  |  | 7.56 | 2.53 | 1.02 | 0.25 | 0.09 | 0.04 | 0
70 |  |  | 8.64 | 2.91 | 1.21 | 0.3 | 0.1 | 0.04 | 0
75 |  |  |  | 3.33 | 1.41 | 0.34 | 0.11 | 0.05 | 0
80 |  |  |  | 3.71 | 1.54 | 0.38 | 0.13 | 0.05 | 0
85 |  |  |  | 3.81 | 1.66 | 0.42 | 0.15 | 0.06 | 0
90 |  |  |  | 4.61 | 1.92 | 0.47 | 0.16 | 0.07 | 0
95 |  |  |  | 5.07 | 2.04 | 0.53 | 0.18 | 0.07 | 0
100 |  |  |  | 5.64 | 2.33 | 0.57 | 0.19 | 0.08 | 0
110 |  |  |  | 6.81 | 2.82 | 0.69 | 0.23 | 0.1 | 0
120 |  |  |  | 7.89 | 3.29 | 0.8 | 0.27 | 0.11 | 0
140 |  |  |  |  | 4.32 | 1.07 | 0.36 | 0.15 | 0.04
160 |  |  |  |  | 5.54 | 1.37 | 0.46 | 0.19 | 0.05
180 |  |  |  |  | 6.58 | 1.7 | 0.57 | 0.24 | 0.06
200 |  |  |  |  | 8.36 | 2.06 | 0.7 | 0.29 | 0.07
220 |  |  |  |  | 10 | 2.44 | 0.83 | 0.34 | 0.08
240 |  |  |  |  | 11.8 | 2.91 | 0.98 | 0.41 | 0.1
260 |  |  |  |  | 13.7 | 3.28 | 1.13 | 0.47 | 0.12
280 |  |  |  |  | 15.7 | 3.85 | 1.3 | 0.54 | 0.13
300 |  |  |  |  | 17.9 | 4.37 | 1.48 | 0.62 | 0.15
320 | [5 empty] | 4.93 | 1.66 | 0.69 | 0.17
340 | [5 empty] | 5.5 | 1.87 | 0.76 | 0.19
360 | [5 empty] | 6.15 | 2.07 | 0.86 | 0.21
380 | [5 empty] | 6.58 | 2.28 | 0.94 | 0.24
400 | [5 empty] | 7.52 | 2.5 | 1.03 | 0.25
420 | [5 empty] | 8.42 | 2.8 | 1.16 | 0.28
450 | [5 empty] | 9.31 | 3.1 | 1.29 | 0.32
500 | [6 empty] | 3.8 | 1.36 | 0.39
550 | [6 empty] | 4.5 | 1.86 | 0.46
600 | [6 empty] | 5.3 | 2.19 | 0.54
650 | [6 empty] | 6.2 | 2.53 | 0.63
700 | [6 empty] | 7.1 | 2.92 | 0.72
750 | [6 empty] | 8.1 | 3.35 | 0.82
800 | [6 empty] | 9.1 | 3.74 | 0.89
850 | [6 empty] | 10.2 | 4.21 | 1.03
900 | [6 empty] | 11.3 | 4.75 | 1.16
950 | [6 empty] | 12.5 | 5.26 | 1.35
1000 | [6 empty] | 13.7 | 5.66 | 1.4
1100 | [7 empty] | 6.84 | 1.65
1200 | [7 empty] | 8.04 | 1.96
1300 | [7 empty] | 8.6 | 2.28
1400 | [7 empty] | 10.6 | 2.59
1500 | [8 empty] | 2.93
1600 | [8 empty] | 3.29
1700 | [8 empty] | 3.66
1800 | [8 empty] | 4.13
1900 | [8 empty] | 4.53
2000 | [8 empty] | 5.03
2100 | [8 empty] | 5.47
2200 | [8 empty] | 6
2300 | [8 empty] | 6.35
2400 | [8 empty] | 6.7

## Operating Pressure (hidden)
Pressure | Feet of Head
0 | 0
1 | 2.31
2 | 4.62
3 | 6.93
4 | 9.24
5 | 11.55
6 | 13.86
7 | 16.17
8 | 18.48
9 | 20.79
10 | 23.1
11 | 25.41
12 | 27.72
13 | 30.03
14 | 32.34
15 | 34.65
16 | 36.96
17 | 39.27
18 | 41.58
19 | 43.89
20 | 46.2
21 | 48.51
22 | 50.82
23 | 53.13
24 | 55.44
25 | 57.75
26 | 60.06
27 | 62.37
28 | 64.68
29 | 66.99
30 | 69.3
31 | 71.61
32 | 73.92
33 | 76.23
34 | 78.54
35 | 80.85
36 | 83.16
37 | 85.47
38 | 87.78
39 | 90.09
40 | 92.4
41 | 94.71
42 | 97.02
43 | 99.33
44 | 101.64
45 | 103.95
46 | 106.26
47 | 108.57
48 | 110.88
49 | 113.19
50 | 115.5
51 | 117.81
52 | 120.12
53 | 122.43
54 | 124.74
55 | 127.05
56 | 129.36
57 | 131.67
58 | 133.98
59 | 136.29
60 | 138.6
61 | 140.91
62 | 143.22
63 | 145.53
64 | 147.84
65 | 150.15
66 | 152.46
67 | 154.77
68 | 157.08
69 | 159.39
70 | 161.7
71 | 164.01
72 | 166.32
73 | 168.63
74 | 170.94
75 | 173.25
76 | 175.56
77 | 177.87
78 | 180.18
79 | 182.49
80 | 184.8
81 | 187.11
82 | 189.42
83 | 191.73
84 | 194.04
85 | 196.35
86 | 198.66
87 | 200.97
88 | 203.28
89 | 205.59
90 | 207.9
91 | 210.21
92 | 212.52
93 | 214.83
94 | 217.14
95 | 219.45
96 | 221.76
97 | 224.07
98 | 226.38
99 | 228.69
100 | 231