## Sheet1
Turbulent Flow Calculations for Water Cooling
To calculate the GPM you need for Turbulent Flow fill in the yellow cells
Line diameter in inches (see table below) |  |  | 3/8 Inch | 0.563
Temperature of water in oF |  |  | 60 |  | Kinematic Viscosity of Water
Kinematic Viscosity - (see table at right) |  |  | 1.12 |  | oF | Visc. (centistokes)
GPM needed for turbulent flow |  |  |  |  | 32 | 1.79
Measured Flow in GPM |  |  | 1.2 |  | 40 | 1.54
Your Reynolds Number |  |  | 6013.7021 |  | 50 | 1.31
You do Not have turbulent flow! |  |  |  |  | 60 | 1.12
[5 empty] | 70 | 0.98
| Find line diameter here: |  |  |  | 80 | 0.86
| Pipe Size | Diameter inches |  |  | 90 | 0.76
| 1/8 Inch | 0.312 |  |  | 100 | 0.69
| 1/4 Inch | 0.438 |  |  | 120 | 0.56
| 3/8 Inch | 0.563 |  |  | 140 | 0.47
| 1/2 Inch | 0.688 |  |  | 160 | 0.4
| 3/4 Inch | 0.89 |  |  | 180 | 0.35
| 1.00 Inch | 1.125 |  |  | 200 | 0.31
| 1.25 Inch | 1.476 |  |  | 212 | 0.28
| 1.50 Inch | 1.713
| 2.00 Inch | 2.188
Do not forget the maximum change in temperature from inlet to outlet is 4 oF or 2 oC