# NEC Article 100 & 110 – Multiple-Choice Questions

## Question 1

Why is it important to use NEC “code language” instead of industry field slang when applying Code rules?

A. 
B. 
C. 
D.

## Question 2

What is the primary purpose of NEC Article 100?

A. To define all electrical terms used in the industry
B. To list commonly used technical terms
C. To provide only definitions essential to applying the NEC
D. To explain how the NEC should be enforced

## Question 3

Which condition would cause equipment to NOT be considered “readily accessible” under Article 100?

A. Equipment located behind a locked door
B. Equipment that requires a key to access
C. Equipment requiring the use of a portable ladder
D. Equipment installed in a mechanical room

## Question 4

What is the purpose of a grounding electrode bonding jumper?

A. To bond the neutral to the enclosure
B. To connect equipment grounding conductors together
C. To interconnect two or more grounding electrodes
D. To connect the grounding electrode conductor to earth

## Question 5

Why was the definition of an equipment bonding jumper revised?

A. To distinguish it from a grounding electrode conductor
B. To clarify it is part of the effective ground-fault current path
C. To eliminate confusion with supply-side bonding jumpers
D. To limit its use to service equipment only

## Question 6

What is the function of the main bonding jumper?

A. It connects grounding electrodes to the grounding electrode conductor
B. It bonds metal raceways together
C. It connects the grounded (neutral) conductor to the equipment grounding conductor at service equipment
D. It isolates neutrals from ground in subpanels

## Question 7

Which of the following qualifies as a limited-energy cable under Article 100?

A. Service-entrance cable
B. Type NM cable
C. Class 2 and power-limited fire alarm circuits
D. Medium-voltage feeder cable

## Question 8

What does NEC 110.3(B) require for listed or labeled equipment?

A. Manufacturer instructions may replace NEC rules
B. Equipment must be installed per manufacturer instructions that do not conflict with the NEC
C. Instructions are optional if the installer is qualified
D. Instructions apply only to residential installations

## Question 9

Which information is required on an arc-flash hazard label for non-dwelling units per NEC 110.16?

A. Working distance and enclosure size
B. Available fault current and breaker size
C. Nominal voltage, arc-flash boundary, incident energy or PPE, and assessment date
D. PPE category only

## Question 10

Why does NEC 110.26 prohibit equipment doors from restricting egress when opened 90 degrees?

A. To improve equipment aesthetics
B. To allow better airflow
C. To prevent worker entrapment during energized work or arc-flash events
D. To simplify inspections

Congratulations!  Try Again

# Answer Key (Instructor Use Only)

- B

- C

- C

- C

- B

- C

- C

- B

- C

- C