## Sheet1
v2 adelade corrected 16.2.17
[6 empty] | START OF SPREADSHEET (approx. 250rows incl.) | [14 empty] | NOTHING TO THE RIGHT OF RED COLUMN
Disclaimer & etc: This spreadsheet, and information within, was produced by Spry Associates Pty Ltd.
This is a Private and confidential document owned by Spry Associates Pty Ltd.
All unauthorised use is prohibited
All I.P. Rights are retained by Spry Associates Pty Ltd.
No guaranties of accuracy or completeness are given. Users use it at their risk entirely.
Users/Readers are advised to make their own calculations and assessments
[12 empty] | AIRAH |  | AIRAH | AIRAH | AIRAH
[8 empty] | edition 2 |  | edition 1 |  | design aid |  | design aid | design aid | design aid
[8 empty] | of AIRAH |  | of AIRAH |  | No: DA9 |  | No: DA9 | No: DA9 | No: DA9
| UNSORTED, Outdoor design, conditions | [6 empty] | handbook |  | handbook |  | of 1997 |  | of 1997 | of 1997 | of 1997
| i.e. Assumptions | [6 empty] | winter |  | winter |  | winter |  | summer | summer | summer
[8 empty] | design |  | design |  | design |  | design | design | design
| NUMBER | SITE | [5 empty] | D.B. |  | D.B. |  | D.B. |  | D.B. | W.B. | G/kG moisture
| 1 | Adelaide | [5 empty] | 4.9 |  | 6.5 |  | 6.4 |  | 34.8 | 21.3 | 10.4
| 2 | Alice Springs | [5 empty] | 1.1 |  | 3.5 |  | 1.1 |  | 40.1 | 22.8 | 10.5
| 3 | Brisbane | [5 empty] | 6.3 |  | 10.5 |  | 9.3 |  | 31.9 | 24.9 | 17
| 4 | Canberra | [5 empty] | 3.1 |  | 0.5 |  | -2.2 |  | 34.3 | 19.6 | 8.3 | note 1
| 5 | Cloncurry | [7 empty] | 10 |  | 8.5 |  | 40.8 | 25.7 | 14.7
| 6 | Darwin | [5 empty] | 18.1 |  | 18.5 |  | 18.1 |  | 34.4 | 27.7 | 20.6
| 7 | Hobart | [5 empty] | 1.5 |  | 3 |  | 1.9 |  | 27 | 18 | 9.25
| 8 | Melbourne | [5 empty] | 2.4 |  | 4.5 |  | 3.5 |  | 34.3 | 20.5 | 15.3
| 9 | Mildura | (All values from AIRAH HB ed 2) |  |  |  |  | 0.8 |  | 0.8 |  | 0.8 |  | 39.5 | 19.7 | 6.2 | (All values from AIRAH HB ed 2)
| 10 | Perth | [5 empty] | 7.4 |  | 9 |  | 7.4 |  | 36.6 | 22.4 | 11.3
| 11 | Port Hedland | [5 empty] | 14.4 |  | 15 |  | 11.1 |  | 39.5 | 28 | 19.3
| 12 | Sydney | [5 empty] | 7.8 |  | 7 |  | 7.2 |  | 31.1 | 22.7 | 14
| 13 | Townsville | [5 empty] | 13.1 |  | 13 |  | 13.1 |  | 32.8 | 26.7 | 19.6
| 14 | Wagga | [5 empty] | -0.8 |  | 1.5 |  | -0.8 |  | 37.1 | 21.1 | 9.2 | note 1
Note:
Mildura design conditions are not in the DA9 reference so the AIRAH handbook values are used
weather/economic calculations
| UNSORTED | [14 empty] | Savings, cooling
[6 empty] | RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW
[6 empty] | $$ |  | $$ |  | $$ |  |  | kW | kW |  | $
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318
Notes:
Plant peak capacities are based on 24/50% RH indoor summer design (AIRAH DA9 recommendation),18C winter indoor design
Energy use calculations are based on 23C/50% summer indoors and 18C winter indoors, no humidification
Cooling @ $0.30/kWH electrical supply, Heating @ $0.10 /kWH gas supply
Cooling COP = 3.0; gas fired heating plant overall efficiency of 76%
Extra heating plant will likely dominate marginal costs in Hobart; so, plant 'savings' (last column) are likely underestimated
Weather frequency data from C'wlth. Dept. Works (BOM data, processed by CSIRO), charts reproduced by AIRAH
Sites 4, 9 and 14 have summer design absolute humidities lower than indoor design so they are adjusted to give zero latent load -
- otherwise negative load would result and humidification be indicated and this is not within the scopes of assumptions about -
- Australian practice i.e. no summer humidification to produce a RH goal
Day plant operation is 6am to 6pm
Night plant operation is 6pm to 6am
Darwin Commercial electricity price from 1 July 2016 is $0.2972/kWH + $0.7862/day (other tariff available)
ACT Business electricity price from 1 July 2016 is $0.26807/kWH + $1.166/day (over 330 kWH/day)
ACT Business gas price from 1 July 2016 is $0.02398 $/mJ ($0.086328/kWH) + $1.51129/day (83 to 3123mJ/day)
Escalating price environment, forward economics based on Electricity @ $0.30/kWH & Gas @ $0.10/kWH
HOW TO USE THESE TABLES - AN EXAMPLE
Look at the table above, at City number 6 i.e. Darwin; Darwin is where, of the listed 14 cities, GPAC use is most advantageous
If a GPAC unit is used to replace a 600 l/s component of a buildings outdoor air intake, then, given the stated parameters
- the annual cost of operating the airconditioning during the daytime (6am-6pm) will be decreased by $7,125
- the annual cost of operating the airconditioning during the nighttime (6pm-6am) will be decreased by $6,176
- the annual cost of operating the airconditioning during for 24 hr/day will be decreased by $13,301
- the cost of construction of the airconditioning will be reduced by $33,394
however, the cost of supply and installation etc. of the GPAC must be taken into account
| weather/economic calculations | [14 empty] | Savings, cooling
| SORTED BY PEAK HEATING |  |  |  |  | RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW
[6 empty] | $$ |  | $$ |  | $$ |  |  | kW | kW |  | $
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832
| weather/economic calculations | [14 empty] | Savings, cooling
| SORTED BY PEAK COOLING |  |  |  |  | RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW
[6 empty] | $$ |  | $$ |  | $$ |  |  | kW | kW |  | $
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992
weather/economic calculations
| SORTED BY DAY ENERGY USE |  |  |  |  | RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394
| weather/economic calculations | [14 empty] | Savings, cooling
| SORTED BY NIGHT ENERGY USE |  |  |  |  | RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394
| weather/economic calculations | [14 empty] | Savings, cooling
| SORTED BY ALL ENERGY USE |  |  |  |  | $ RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394
CAPITAL COST ECONOMICS COOLING - EXAMPLES (APPROXIMATIONS)
| AUDITORIUM IN SYDNEY | [10 empty] | non GPAC OA load = |  | 203.4 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 303.4 | watts
| 22C db / 50% RH indoors |  |  | 11.75 g/kg | [7 empty] | GPAC use reduces load by |  | 44.6935 | %
| delta C = | 9.1 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 5.4 | [10 empty] | say | 35 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 54.6 | watts | saving
| latent = | 81 | watts | saving
| total = | 135.6 | watts | saving
| AUDITORIUM IN DARWIN | [10 empty] | non GPAC OA load = |  | 381.6 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 34.4C db ourdoors, 23.6C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 481.6 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 52.8239 | %
| delta C = | 12.4 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 12 | [10 empty] | say | 40 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 74.4 | watts | saving
| latent = | 180 | watts | saving
| total = | 254.4 | watts | saving
AUDITORIUM IN ADELAIDE
[12 empty] | non GPAC OA load = |  | 155.7 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 255.7 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 40.5944 | %
| delta C = | 12.8 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 1.8 | [10 empty] | say | 30 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 76.8 | watts | saving
| latent = | 27 | watts | saving
| total = | 103.8 | watts | saving
AUDITORIUM IN ALICE SPRINGS
[12 empty] | non GPAC OA load = |  | 203.85 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 303.85 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 44.726 | %
| delta C = | 17.9 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 1.9 | [10 empty] | say | 35 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 107.4 | watts | saving
| latent = | 28.5 | watts | saving
| total = | 135.9 | watts | saving
AUDITORIUM IN HOBART
[12 empty] | non GPAC OA load = |  | 59.625 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 159.625 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 24.9021 | %
| delta C = | 5 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 0.65 | [10 empty] | say | 15 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 30 | watts | saving
| latent = | 9.75 | watts | saving
| total = | 39.75 | watts | saving
AUDITORIUM IN CANBERRA
[12 empty] | non GPAC OA load = |  | 110.7 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 210.7 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 35.0261 | %
| delta C = | 12.3 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 0 | [10 empty] | say | 25 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 73.8 | watts | saving
| latent = | 0 | watts | saving
| total = | 73.8 | watts | saving
AUDITORIUM IN CLONCURRY
[12 empty] | non GPAC OA load = |  | 292.05 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 392.05 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 49.662 | %
| delta C = | 17.2 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 6.1 | [10 empty] | say | 40 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 103.2 | watts | saving
| latent = | 91.5 | watts | saving
| total = | 194.7 | watts | saving
AUDITORIUM IN WAGGA
[12 empty] | non GPAC OA load = |  | 149.4 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 249.4 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 39.9358 | %
| delta C = | 15.1 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 0.6 | [10 empty] | say | 30 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 90.6 | watts | saving
| latent = | 9 | watts | saving
| total = | 99.6 | watts | saving
AUDITORIUM IN TOWNSVILLE
[12 empty] | non GPAC OA load = |  | 344.7 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 444.7 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 51.6753 | %
| delta C = | 10.8 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 11 | [10 empty] | say | 40 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 64.8 | watts | saving
| latent = | 165 | watts | saving
| total = | 229.8 | watts | saving
AUDITORIUM IN PORT HEDLAND
[12 empty] | non GPAC OA load = |  | 398.25 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 498.25 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 53.2865 | %
| delta C = | 17.5 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 10.7 | [10 empty] | say | 40 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 105 | watts | saving
| latent = | 160.5 | watts | saving
| total = | 265.5 | watts | saving
AUDITORIUM IN BRISBANE
[12 empty] | non GPAC OA load = |  | 278.1 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 378.1 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 49.0346 | %
| delta C = | 9.9 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 8.4 | [10 empty] | say | 40 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 59.4 | watts | saving
| latent = | 126 | watts | saving
| total = | 185.4 | watts | saving
AUDITORIUM IN MELBOURNE
[12 empty] | non GPAC OA load = |  | 261.45 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 361.45 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 48.2224 | %
| delta C = | 12.3 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 6.7 | [10 empty] | say | 40 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 73.8 | watts | saving
| latent = | 100.5 | watts | saving
| total = | 174.3 | watts | saving
AUDITORIUM IN MILDURA
[12 empty] | non GPAC OA load = |  | 157.5 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 257.5 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 40.7767 | %
| delta C = | 17.5 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 0 | [10 empty] | say | 30 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 105 | watts | saving
| latent = | 0 | watts | saving
| total = | 105 | watts | saving
AUDITORIUM IN PERTH
[12 empty] | non GPAC OA load = |  | 192.15 | watts
| almost all load is people, calc for 1 person | [10 empty] | pop load , airah 80+20 |  | 100 | watts
| 31.1C db ourdoors, 19.8C wb outdoors (AIRAH design conditions) | [10 empty] | total |  | 292.15 | watts
| 22C db / 50% RH indoors | [10 empty] | GPAC use reduces load by |  | 43.8473 | %
| delta C = | 14.6 | [9 empty] | if building heat contribution negligable
| delta g/kG= | 2.7 | [10 empty] | say | 30 | %
| l/s = | 5 | saving using GPAC | [9 empty] | some allowance for building load
| sensible = | 87.6 | watts | saving
| latent = | 40.5 | watts | saving
| total = | 128.1 | watts | saving
% OF AIRCONDITIONING LOAD IN OFFICE
| 600 l/s GPAC unit |  | normal heat load (AIRAH) 100 w/sq. m.
120 people
1500 sq. m.
12.5 Sq. M. /person
power use (AIRAH) 30-60 kWH/annum/sq.m, so
| sydney | 30
| darwin | 60 | [12 empty] | 208333.3333
| $/kWH | 0.3 | both
Sydney
| day use av saving $ PA, see above = |  |  | 1227 |  |  |  | $/annum = |  |  |  | 627 | saving
| recharge $ PA |  |  | 600
| nett saving $ |  |  | 627
| annual power = | [6 empty] | $/annum = |  |  |  | 13500 | total
[8 empty] | GPAC use reduces power use by |  |  |  |  | 4.6444 | %
[8 empty] | see assumptions |  |  |  | say | 4.5 | %
Darwin
| day use av saving $ PA, see above = |  |  | 7125 |  |  |  | $/annum = |  |  |  | 6525 | saving
| recharge $ PA |  |  | 600
| nett saving $ |  |  | 6525
| annual power = | [6 empty] | $/annum = |  |  |  | 27000 | total
[8 empty] | GPAC use reduces power use by |  |  |  |  | 24.1667
[8 empty] | see assumptions |  |  |  | say | 24 | %
OFFICE BUILDING (100 w/m2) % capacity reduction from GPAC use - cooling basis
| weather/economic calculations | [15 empty] | USUAL | USUAL | % plant
| SORTED BY DAY ENERGY USE |  |  |  |  | RUNNING COST SAVING - 600 l/s | [6 empty] | Peak | Peak |  | plant capacity | 1500sq m | 150 kW@ | size
[6 empty] | Day |  | Night |  | 24 Hr |  |  | Cool | Heat |  | not needed | @ 100w/m2 | $1200/kW | reduction
| NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  |  | Capacity | Capacity |  | @$1200/kW | kW
| 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707 | 150 | 180000 | 6.5039
| 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206 | 150 | 180000 | 8.4478
| 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859 | 150 | 180000 | 12.1439
| 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392 | 150 | 180000 | 7.44
| 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286 | 150 | 180000 | 9.0478
| 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592 | 150 | 180000 | 1.44
| 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458 | 150 | 180000 | 13.0322
| 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832 | 150 | 180000 | 8.24
| 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286 | 150 | 180000 | 9.0478
| 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318 | 150 | 180000 | 6.2878
| 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179 | 150 | 180000 | 14.5439
| 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992 | 150 | 180000 | 19.44
| 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851 | 150 | 180000 | 16.5839
| 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394 | 150 | 180000 | 18.5522
| population | occupancy type |  |  |  | area served
| load, number |  |  |  |  | sq. m.
| 120 | bar, theatre, auditorium, conference |  |  |  | 120
| 120 | library,mall,arcade,exercise room |  |  |  | 810
| 120 | office,bedroom,workroom |  |  |  | 1500
auditorium, bar etc 120 sq m
|  | BASE | ADJUSTED | BASE |  | ADJUSTED |  |  |  | MID DENSITY
|  | office | office, workroom | auditorium |  | auditorium |  |  |  | mall, library
workroom
bedroom
|  | % plant | % plant | % plant |  | % plant |  |  |  | % plant
| Adelaide | 6.5039 | 6 | 40 |  | 30 |  |  |  | 18
| Perth | 8.4478 | 8 | 44 |  | 35 |  |  |  | 21.5
| Melbourne | 12.1439 | 12 | 48 |  | 40 |  |  |  | 26
| Mildura | 7.44 | 7 | 41 |  | 30 |  |  |  | 18.5
| Sydney | 9.0478 | 9 | 45 |  | 35 |  |  |  | 22
| Hobart | 1.44 | 2 | 25 |  | 20 |  |  |  | 11
| Brisbane | 13.0322 | 13 | 49 |  | 40 |  |  |  | 26.5
| Canberra | 8.24 | 8 | 35 |  | 25 |  |  |  | 16.5
| Alice Springs | 9.0478 | 9 | 45 |  | 35 |  |  |  | 22
| Wagga | 6.2878 | 6 | 40 |  | 30 |  |  |  | 18
| Cloncurry | 14.5439 | 14 | 50 |  | 40 |  |  |  | 27
| Port Hedland | 19.44 | 19 | 53 |  | 45 |  |  |  | 32
| Townsville | 16.5839 | 17 | 52 |  | 45 |  |  |  | 31
| Darwin | 18.5522 | 18 | 53 |  | 45 |  |  |  | 31.5
END OF SPREADSHEET
Summary Scenarios
[6 empty] | RUNNING COST SAVING - 600 l/s | [6 empty] | PLANT COST SAVING - 600 l/s
| NUMBER | SITE | Scenario |  |  | Run cost saving day AUD | Run cost saving day % | Run cost saving night AUD | Run cost saving night % | Run cost saving 24hr AUD | Run cost saving 24hr % |  | Peak cool capacity (kW) | Peak heat capacity (kW) |  | Plant capacity not needed @$1200/kW AUD | 1500 sqm @ 100w/m2 (kW) | 150kW@$1200/kW (AUD) | Plant size reduction %
| 1 | Adelaide | Low-Office |  |  | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707 | 150 | 180000 | 6
| 1 | Adelaide | Mid-Mall/libray | [15 empty] | 18
| 1 | Adelaide | High-Auditorium | [15 empty] | 30
| 10 | Perth | Low-Office |  |  | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206 | 150 | 180000 | 8
| 10 | Perth | Mid-Mall/libray | [15 empty] | 21.5
| 10 | Perth | High-Auditorium | [15 empty] | 35
| 8 | Melbourne | Low-Office |  |  | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859 | 150 | 180000 | 12
| 8 | Melbourne | Mid-Mall/libray | [15 empty] | 26
| 8 | Melbourne | High-Auditorium | [15 empty] | 40
| 9 | Mildura | Low-Office |  |  | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392 | 150 | 180000 | 7
| 9 | Mildura | Mid-Mall/libray | [15 empty] | 18.5
| 9 | Mildura | High-Auditorium | [15 empty] | 30
| 12 | Sydney | Low-Office |  |  | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286 | 150 | 180000 | 9
| 12 | Sydney | Mid-Mall/libray | [15 empty] | 22
| 12 | Sydney | High-Auditorium | [15 empty] | 35
| 7 | Hobart | Low-Office |  |  | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592 | 150 | 180000 | 2
| 7 | Hobart | Mid-Mall/libray | [15 empty] | 11
| 7 | Hobart | High-Auditorium | [15 empty] | 20
| 3 | Brisbane | Low-Office |  |  | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458 | 150 | 180000 | 13
| 3 | Brisbane | Mid-Mall/libray | [15 empty] | 26.5
| 3 | Brisbane | High-Auditorium | [15 empty] | 40
| 4 | Canberra | Low-Office |  |  | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832 | 150 | 180000 | 8
| 4 | Canberra | Mid-Mall/libray | [15 empty] | 16.5
| 4 | Canberra | High-Auditorium | [15 empty] | 25
| 2 | Alice Springs | Low-Office |  |  | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286 | 150 | 180000 | 9
| 2 | Alice Springs | Mid-Mall/libray | [15 empty] | 22
| 2 | Alice Springs | High-Auditorium | [15 empty] | 35
| 14 | Wagga | Low-Office |  |  | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318 | 150 | 180000 | 6
| 14 | Wagga | Mid-Mall/libray | [15 empty] | 18
| 14 | Wagga | High-Auditorium | [15 empty] | 30
| 5 | Cloncurry | Low-Office |  |  | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179 | 150 | 180000 | 14
| 5 | Cloncurry | Mid-Mall/libray | [15 empty] | 27
| 5 | Cloncurry | High-Auditorium | [15 empty] | 40
| 11 | Port Hedland | Low-Office |  |  | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992 | 150 | 180000 | 19
| 11 | Port Hedland | Mid-Mall/libray | [15 empty] | 32
| 11 | Port Hedland | High-Auditorium | [15 empty] | 40
| 13 | Townsville | Low-Office |  |  | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851 | 150 | 180000 | 45
| 13 | Townsville | Mid-Mall/libray | [15 empty] | 31
| 13 | Townsville | High-Auditorium | [15 empty] | 45
| 6 | Darwin | Low-Office |  |  | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394 | 150 | 180000 | 18
| 6 | Darwin | Mid-Mall/libray | [15 empty] | 31.5
| 6 | Darwin | High-Auditorium | [15 empty] | 45
[6 empty] | RUNNING COST SAVING - 600 l/s, 120 persons | [6 empty] | PLANT COST SAVING - 600 l/s, 120 persons
| NUMBER | SITE | Scenario | 120 area sq.m. | sq. m. /person | Run cost saving day AUD | Run cost saving day % | Run cost saving night AUD | Run cost saving night % | Run cost saving 24hr AUD | Run cost saving 24hr % |  | Peak cool capacity not needed (kW) | Peak heat capacity not needed (kW) |  | Plant capacity not needed @$1200/kW AUD | total plant kW, before GPAC | plant $ @ 1200/kW | Plant size reduction %
| 1 | Adelaide | Low-Office | 1500 | 12.5 | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707 | 150 | 180000 | 6
| 1 | Adelaide | Mid-Mall/libray | 810 | 6.75 | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707 | 50 | 60000 | 18
| 1 | Adelaide | High-Auditorium | 120 | 1 | 668 |  | 1206 |  | 1874 |  |  | 9.76 | 8.35 |  | 11707 | 36 | 36000 | 30
| 10 | Perth | Low-Office | 1500 | 12.5 | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206 | 150 | 180000 | 8
| 10 | Perth | Mid-Mall/libray | 810 | 6.75 | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206 | 56 | 67200 | 21.5
| 10 | Perth | High-Auditorium | 120 | 1 | 657 |  | 871 |  | 1528 |  |  | 12.67 | 7.63 |  | 15206 | 34 | 40800 | 35
| 8 | Melbourne | Low-Office | 1500 | 12.5 | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859 | 150 | 180000 | 12
| 8 | Melbourne | Mid-Mall/libray | 810 | 6.75 | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859 | 69 | 82800 | 26
| 8 | Melbourne | High-Auditorium | 120 | 1 | 910 |  | 1726 |  | 2636 |  |  | 18.22 | 10.44 |  | 21859 | 45 | 54000 | 40
| 9 | Mildura | Low-Office | 1500 | 12.5 | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392 | 150 | 180000 | 7
| 9 | Mildura | Mid-Mall/libray | 810 | 6.75 | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392 | 57 | 68400 | 18.5
| 9 | Mildura | High-Auditorium | 120 | 1 | 1081 |  | 1751 |  | 2832 |  |  | 11.16 | 12.38 |  | 13392 | 35 | 42000 | 30
| 12 | Sydney | Low-Office | 1500 | 12.5 | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286 | 150 | 180000 | 9
| 12 | Sydney | Mid-Mall/libray | 810 | 6.75 | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286 | 61 | 73200 | 22
| 12 | Sydney | High-Auditorium | 120 | 1 | 1227 |  | 2831 |  | 4058 |  |  | 13.57 | 7.77 |  | 16286 | 39 | 46800 | 35
| 7 | Hobart | Low-Office | 1500 | 12.5 | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592 | 150 | 180000 | 2
| 7 | Hobart | Mid-Mall/libray | 810 | 6.75 | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592 | 27 | 32400 | 11
| 7 | Hobart | High-Auditorium | 120 | 1 | 1352 |  | 2389 |  | 3741 |  |  | 2.16 | 11.59 |  | 2592 | 15 | 18000 | 20
| 3 | Brisbane | Low-Office | 1500 | 12.5 | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458 | 150 | 180000 | 13
| 3 | Brisbane | Mid-Mall/libray | 810 | 6.75 | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458 | 74 | 88800 | 26.5
| 3 | Brisbane | High-Auditorium | 120 | 1 | 1381 |  | 593 |  | 1974 |  |  | 19.55 | 6.26 |  | 23458 | 48.75 | 58500 | 40
| 4 | Canberra | Low-Office | 1500 | 12.5 | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832 | 150 | 180000 | 8
| 4 | Canberra | Mid-Mall/libray | 810 | 6.75 | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832 | 73 | 87600 | 16.5
| 4 | Canberra | High-Auditorium | 120 | 1 | 1398 |  | 2873 |  | 4271 |  |  | 12.36 | 24.24 |  | 14832 | 48 | 57600 | 25
| 2 | Alice Springs | Low-Office | 1500 | 12.5 | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286 | 150 | 180000 | 9
| 2 | Alice Springs | Mid-Mall/libray | 810 | 6.75 | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286 | 61 | 73200 | 22
| 2 | Alice Springs | High-Auditorium | 120 | 1 | 1628 |  | 1532 |  | 3160 |  |  | 13.57 | 12.17 |  | 16286 | 39 | 46800 | 35
| 14 | Wagga | Low-Office | 1500 | 12.5 | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318 | 150 | 180000 | 6
| 14 | Wagga | Mid-Mall/libray | 810 | 6.75 | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318 | 50 | 60000 | 18
| 14 | Wagga | High-Auditorium | 120 | 1 | 2806 |  | 2049 |  | 4855 |  |  | 9.43 | 13.54 |  | 11318 | 30 | 36000 | 30
| 5 | Cloncurry | Low-Office | 1500 | 12.5 | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179 | 150 | 180000 | 14
| 5 | Cloncurry | Mid-Mall/libray | 810 | 6.75 | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179 | 78 | 93600 | 27
| 5 | Cloncurry | High-Auditorium | 120 | 1 | 2946 |  | 1829 |  | 4775 |  |  | 21.82 | 6.84 |  | 26179 | 52.5 | 63000 | 40
| 11 | Port Hedland | Low-Office | 1500 | 12.5 | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992 | 150 | 180000 | 19
| 11 | Port Hedland | Mid-Mall/libray | 810 | 6.75 | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992 | 89 | 106800 | 32
| 11 | Port Hedland | High-Auditorium | 120 | 1 | 4304 |  | 2981 |  | 7285 |  |  | 29.16 | 4.97 |  | 34992 | 71 | 85200 | 40
| 13 | Townsville | Low-Office | 1500 | 12.5 | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851 | 150 | 180000 | 45
| 13 | Townsville | Mid-Mall/libray | 810 | 6.75 | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851 | 218 | 261600 | 31
| 13 | Townsville | High-Auditorium | 120 | 1 | 4382 |  | 2704 |  | 7086 |  |  | 24.88 | 3.53 |  | 29851 | 150 | 180000 | 45
| 6 | Darwin | Low-Office | 1500 | 12.5 | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394 | 150 | 180000 | 18
| 6 | Darwin | Mid-Mall/libray | 810 | 6.75 | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394 | 86 | 103200 | 31.5
| 6 | Darwin | High-Auditorium | 120 | 1 | 7125 |  | 6176 |  | 13301 |  |  | 27.83 | 0.07 |  | 33394 | 60 | 72000 | 45
|  | weather/economic calculations |  | day/night ratios | [15 empty] | schools | stand alone | retail - | hospitals | schools | schools | universities | VET | public | law courts
|  | SORTED BY DAY ENERGY USE |  |  |  |  | RUNNING COST SAVING - 600 l/s | [13 empty] | offices | shopping |  |  |  |  | buildings | buildings
[7 empty] | Day |  | Night |  | 24 Hr |  | ratio | ratio | [7 empty] | centres
|  | NUMBER | SITE |  |  |  | Annual |  | Annual |  | Annual |  | day to total | night to total
|  | 1 | Adelaide |  |  |  | 668 |  | 1206 |  | 1874 |  | 0.35646 | 0.64354
|  | 10 | Perth |  |  |  | 657 |  | 871 |  | 1528 |  | 0.42997 | 0.57003
|  | 8 | Melbourne |  |  |  | 910 |  | 1726 |  | 2636 |  | 0.34522 | 0.65478
|  | 9 | Mildura |  |  |  | 1081 |  | 1751 |  | 2832 |  | 0.38171 | 0.61829
|  | 12 | Sydney |  |  |  | 1227 |  | 2831 |  | 4058 |  | 0.30237 | 0.69763
|  | 7 | Hobart |  |  |  | 1352 |  | 2389 |  | 3741 |  | 0.3614 | 0.6386
|  | 3 | Brisbane |  |  |  | 1381 |  | 593 |  | 1974 |  | 0.69959 | 0.30041
|  | 4 | Canberra |  |  |  | 1398 |  | 2873 |  | 4271 |  | 0.32732 | 0.67268
|  | 2 | Alice Springs |  |  |  | 1628 |  | 1532 |  | 3160 |  | 0.51519 | 0.48481
|  | 14 | Wagga |  |  |  | 2806 |  | 2049 |  | 4855 |  | 0.57796 | 0.42204
|  | 5 | Cloncurry |  |  |  | 2946 |  | 1829 |  | 4775 |  | 0.61696 | 0.38304
|  | 11 | Port Hedland |  |  |  | 4304 |  | 2981 |  | 7285 |  | 0.5908 | 0.4092
|  | 13 | Townsville |  |  |  | 4382 |  | 2704 |  | 7086 |  | 0.6184 | 0.3816
|  | 6 | Darwin |  |  |  | 7125 |  | 6176 |  | 13301 |  | 0.53567 | 0.46433
1500 m2 area: Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and assumption that HVAC uses 40% of building energy
[11 empty] | AS % of all use | [7 empty] | AS % 0f HVAC use
[10 empty] | ADELAIDE | ADELAIDE |  | ADELAIDE | ADELAIDE |  | ADELAIDE | ADELAIDE |  | ADELAIDE |  | ADELAIDE | ADELAIDE
|  | All | 1 kWH=3.6mJ | All | All | ALL | HVAC cost | HVAC |  | GPAC use | GPAC use |  | GPAC use | GPAC use |  | GPAC use | GPAC use |  | GPAC use |  | GPAC use | GPAC use
[10 empty] | day saving | day saving |  | night saving | night saving |  | 24 hr saving | 24 hr saving |  | day saving |  | night saving | 24 hr saving
Units: MJ/ m2.a | in 2020 | kWH/m2.a. | area m2 | kWH/a | cost $/kWH | cost $/a. | fraction | cost $/a. |  | $/a. | % |  | $/a. | % |  | $/a. | % |  | % |  | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 668 | 1.6038 |  | 1206 | 2.8956 |  | 1874 | 4.4994 |  | 4.0096 |  | 7.2389 | 11.2485
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 668 | 0.80872 |  | 1206 | 1.46 |  | 1874 | 2.2688 |  | 2.0218 |  | 3.6501 | 5.6719
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 668 | 1.2486 |  | 1206 | 2.2542 |  | 1874 | 3.5028 |  | 3.1215 |  | 5.6355 | 8.757
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 668 | 0.59378 |  | 1206 | 1.072 |  | 1874 | 1.6658 |  | 1.4844 |  | 2.68 | 4.1644
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 668 | 1.1957 |  | 1206 | 2.1587 |  | 1874 | 3.3544 |  | 2.9893 |  | 5.3968 | 8.386
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 668 | 10.4921 |  | 1206 | 18.9424 |  | 1874 | 29.4346 |  | 26.2304 |  | 47.356 | 73.5864
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 668 | 7.3005 |  | 1206 | 13.1803 |  | 1874 | 20.4809 |  | 18.2514 |  | 32.9508 | 51.2022
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 668 | 2.7689 |  | 1206 | 4.999 |  | 1874 | 7.7679 |  | 6.9223 |  | 12.4974 | 19.4197
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 668 | 3.4792 |  | 1206 | 6.2812 |  | 1874 | 9.7604 |  | 8.6979 |  | 15.7031 | 24.401
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 668 | 3.1215 |  | 1206 | 5.6355 |  | 1874 | 8.757 |  | 7.8037 |  | 14.0888 | 21.8925
Note on A34: p:

## adelaide
ADELAIDE GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 668 | 0.64154 | 1206 | 1.1582 | 1874 | 1.7998 | 1.6038 | 2.8956 | 4.4994 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 668 | 0.32349 | 1206 | 0.58402 | 1874 | 0.90751 | 0.80872 | 1.46 | 2.2688 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 668 | 0.49944 | 1206 | 0.90168 | 1874 | 1.4011 | 1.2486 | 2.2542 | 3.5028 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 668 | 0.23751 | 1206 | 0.4288 | 1874 | 0.66631 | 0.59378 | 1.072 | 1.6658 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 668 | 0.47828 | 1206 | 0.86348 | 1874 | 1.3418 | 1.1957 | 2.1587 | 3.3544 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 668 | 4.1969 | 1206 | 7.577 | 1874 | 11.7738 | 10.4921 | 18.9424 | 29.4346 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 668 | 2.9202 | 1206 | 5.2721 | 1874 | 8.1923 | 7.3005 | 13.1803 | 20.4809 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 668 | 1.1076 | 1206 | 1.9996 | 1874 | 3.1072 | 2.7689 | 4.999 | 7.7679 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 668 | 1.3917 | 1206 | 2.5125 | 1874 | 3.9042 | 3.4792 | 6.2812 | 9.7604 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 668 | 1.2486 | 1206 | 2.2542 | 1874 | 3.5028 | 3.1215 | 5.6355 | 8.757 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## perth
PERTH GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | PERTH | PERTH | PERTH | PERTH | PERTH | PERTH | PERTH | PERTH | PERTH
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 657 | 0.63097 | 871 | 0.83649 | 1528 | 1.4675 | 1.5774 | 2.0912 | 3.6687 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 657 | 0.31816 | 871 | 0.42179 | 1874 | 0.90751 | 0.7954 | 1.0545 | 2.2688 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 657 | 0.49121 | 871 | 0.65121 | 1874 | 1.4011 | 1.228 | 1.628 | 3.5028 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 657 | 0.2336 | 871 | 0.30969 | 1874 | 0.66631 | 0.584 | 0.77422 | 1.6658 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 657 | 0.47041 | 871 | 0.62363 | 1874 | 1.3418 | 1.176 | 1.5591 | 3.3544 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 657 | 4.1277 | 871 | 5.4723 | 1874 | 11.7738 | 10.3194 | 13.6806 | 29.4346 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 657 | 2.8721 | 871 | 3.8077 | 1874 | 8.1923 | 7.1803 | 9.5191 | 20.4809 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 657 | 1.0893 | 871 | 1.4441 | 1874 | 3.1072 | 2.7233 | 3.6104 | 7.7679 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 657 | 1.3687 | 871 | 1.8146 | 1874 | 3.9042 | 3.4219 | 4.5365 | 9.7604 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 657 | 1.228 | 871 | 1.628 | 1874 | 3.5028 | 3.0701 | 4.0701 | 8.757 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## melbourne
MELBOURNE GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 910 | 0.87395 | 1726 | 1.6576 | 2636 | 2.5316 | 2.1849 | 4.1441 | 6.3289 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 910 | 0.44068 | 1726 | 0.83584 | 2636 | 1.2765 | 1.1017 | 2.0896 | 3.1913 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 910 | 0.68037 | 1726 | 1.2905 | 2636 | 1.9708 | 1.7009 | 3.2262 | 4.9271 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 910 | 0.32356 | 1726 | 0.61369 | 2636 | 0.93724 | 0.80889 | 1.5342 | 2.3431 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 910 | 0.65155 | 1726 | 1.2358 | 2636 | 1.8874 | 1.6289 | 3.0895 | 4.7184 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 910 | 5.7173 | 1726 | 10.844 | 2636 | 16.5613 | 14.2932 | 27.1099 | 41.4031 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 910 | 3.9781 | 1726 | 7.5454 | 2636 | 11.5235 | 9.9454 | 18.8634 | 28.8087 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 910 | 1.5088 | 1726 | 2.8618 | 2636 | 4.3706 | 3.772 | 7.1544 | 10.9264 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 910 | 1.8958 | 1726 | 3.5958 | 2636 | 5.4917 | 4.7396 | 8.9896 | 13.7292 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 910 | 1.7009 | 1726 | 3.2262 | 2636 | 4.9271 | 4.2523 | 8.0654 | 12.3178 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## mildura
MILDURA GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1081 | 1.0382 | 1751 | 1.6816 | 2832 | 2.7198 | 2.5954 | 4.2041 | 6.7995 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1081 | 0.52349 | 1751 | 0.84794 | 2832 | 1.3714 | 1.3087 | 2.1199 | 3.4286 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1081 | 0.80822 | 1751 | 1.3092 | 2832 | 2.1174 | 2.0206 | 3.2729 | 5.2935 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1081 | 0.38436 | 1751 | 0.62258 | 2832 | 1.0069 | 0.96089 | 1.5564 | 2.5173 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1081 | 0.77399 | 1751 | 1.2537 | 2832 | 2.0277 | 1.935 | 3.1342 | 5.0692 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1081 | 6.7916 | 1751 | 11.001 | 2832 | 17.7927 | 16.9791 | 27.5026 | 44.4817 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1081 | 4.7257 | 1751 | 7.6546 | 2832 | 12.3803 | 11.8142 | 19.1366 | 30.9508 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1081 | 1.7923 | 1751 | 2.9032 | 2832 | 4.6955 | 4.4808 | 7.258 | 11.7389 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1081 | 2.2521 | 1751 | 3.6479 | 2832 | 5.9 | 5.6302 | 9.1198 | 14.75 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1081 | 2.0206 | 1751 | 3.2729 | 2832 | 5.2935 | 5.0514 | 8.1822 | 13.2336 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## sydney
SYDNEY GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1227 | 1.1784 | 2831 | 2.7188 | 4058 | 3.8972 | 2.946 | 6.7971 | 9.7431 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1227 | 0.59419 | 2831 | 1.3709 | 4058 | 1.9651 | 1.4855 | 3.4274 | 4.9128 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1227 | 0.91738 | 2831 | 2.1166 | 4058 | 3.034 | 2.2935 | 5.2916 | 7.585 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1227 | 0.43627 | 2831 | 1.0066 | 4058 | 1.4428 | 1.0907 | 2.5164 | 3.6071 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1227 | 0.87852 | 2831 | 2.027 | 4058 | 2.9055 | 2.1963 | 5.0674 | 7.2637 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1227 | 7.7089 | 2831 | 17.7864 | 4058 | 25.4953 | 19.2723 | 44.466 | 63.7382 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1227 | 5.3639 | 2831 | 12.376 | 4058 | 17.7399 | 13.4098 | 30.9399 | 44.3497 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1227 | 2.0344 | 2831 | 4.6939 | 4058 | 6.7283 | 5.086 | 11.7347 | 16.8207 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1227 | 2.5562 | 2831 | 5.8979 | 4058 | 8.4542 | 6.3906 | 14.7448 | 21.1354 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1227 | 2.2935 | 2831 | 5.2916 | 4058 | 7.585 | 5.7336 | 13.229 | 18.9626 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## hobart
SYDNEY GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | HOBART | HOBART | HOBART | HOBART | HOBART | HOBART | HOBART | HOBART | HOBART
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1352 | 1.2984 | 2389 | 2.2944 | 2389 | 2.2944 | 3.2461 | 5.7359 | 5.7359 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1352 | 0.65472 | 2389 | 1.1569 | 2389 | 1.1569 | 1.6368 | 2.8923 | 2.8923 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1352 | 1.0108 | 2389 | 1.7862 | 2389 | 1.7862 | 2.5271 | 4.4654 | 4.4654 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1352 | 0.48071 | 2389 | 0.84942 | 2389 | 0.84942 | 1.2018 | 2.1236 | 2.1236 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1352 | 0.96802 | 2389 | 1.7105 | 2389 | 1.7105 | 2.42 | 4.2763 | 4.2763 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1352 | 8.4942 | 2389 | 15.0094 | 2389 | 15.0094 | 21.2356 | 37.5236 | 37.5236 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1352 | 5.9104 | 2389 | 10.4437 | 2389 | 10.4437 | 14.776 | 26.1093 | 26.1093 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1352 | 2.2417 | 2389 | 3.961 | 2389 | 3.961 | 5.6041 | 9.9026 | 9.9026 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1352 | 2.8167 | 2389 | 4.9771 | 2389 | 4.9771 | 7.0417 | 12.4427 | 12.4427 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1352 | 2.5271 | 2389 | 4.4654 | 2389 | 4.4654 | 6.3178 | 11.1636 | 11.1636 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## brisbane
BRISMANE GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1381 | 1.3263 | 593 | 0.56951 | 1974 | 1.8958 | 3.3157 | 1.4238 | 4.7395 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1381 | 0.66877 | 593 | 0.28717 | 1974 | 0.95593 | 1.6719 | 0.71792 | 2.3898 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1381 | 1.0325 | 593 | 0.44336 | 1974 | 1.4759 | 2.5813 | 1.1084 | 3.6897 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1381 | 0.49102 | 593 | 0.21084 | 1974 | 0.70187 | 1.2276 | 0.52711 | 1.7547 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1381 | 0.98878 | 593 | 0.42458 | 1974 | 1.4134 | 2.472 | 1.0615 | 3.5334 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1381 | 8.6764 | 593 | 3.7257 | 1974 | 12.4021 | 21.6911 | 9.3141 | 31.0052 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1381 | 6.0372 | 593 | 2.5923 | 1974 | 8.6295 | 15.0929 | 6.4809 | 21.5738 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1381 | 2.2897 | 593 | 0.98321 | 1974 | 3.273 | 5.7244 | 2.458 | 8.1824 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1381 | 2.8771 | 593 | 1.2354 | 1974 | 4.1125 | 7.1927 | 3.0885 | 10.2812 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1381 | 2.5813 | 593 | 1.1084 | 1974 | 3.6897 | 6.4533 | 2.771 | 9.2243 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## ALL CITIES
BIOAIR [GPAC] Savings & Benefit Matrix
GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd estmates using weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
ADELAIDE | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE | ADELAIDE |  | ADELAIDE | ADELAIDE | ADELAIDE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 668 | 0.64154 | 1206 | 1.1582 | 1874 | 1.7998 |  | 1.6038 | 2.8956 | 4.4994 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 668 | 0.32349 | 1206 | 0.58402 | 1874 | 0.90751 |  | 0.80872 | 1.46 | 2.2688 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 668 | 0.49944 | 1206 | 0.90168 | 1874 | 1.4011 |  | 1.2486 | 2.2542 | 3.5028 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 668 | 0.23751 | 1206 | 0.4288 | 1874 | 0.66631 |  | 0.59378 | 1.072 | 1.6658 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 668 | 0.47828 | 1206 | 0.86348 | 1874 | 1.3418 |  | 1.1957 | 2.1587 | 3.3544 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 668 | 4.1969 | 1206 | 7.577 | 1874 | 11.7738 |  | 10.4921 | 18.9424 | 29.4346 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 668 | 2.9202 | 1206 | 5.2721 | 1874 | 8.1923 |  | 7.3005 | 13.1803 | 20.4809 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 668 | 1.1076 | 1206 | 1.9996 | 1874 | 3.1072 |  | 2.7689 | 4.999 | 7.7679 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 668 | 1.3917 | 1206 | 2.5125 | 1874 | 3.9042 |  | 3.4792 | 6.2812 | 9.7604 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 668 | 1.2486 | 1206 | 2.2542 | 1874 | 3.5028 |  | 3.1215 | 5.6355 | 8.757 | Law Courts
PERTH | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | PERTH | PERTH | PERTH | PERTH | PERTH | PERTH |  | PERTH | PERTH | PERTH
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 657 | 0.63097 | 871 | 0.83649 | 1528 | 1.4675 |  | 1.5774 | 2.0912 | 3.6687 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 657 | 0.31816 | 871 | 0.42179 | 1874 | 0.90751 |  | 0.7954 | 1.0545 | 2.2688 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 657 | 0.49121 | 871 | 0.65121 | 1874 | 1.4011 |  | 1.228 | 1.628 | 3.5028 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 657 | 0.2336 | 871 | 0.30969 | 1874 | 0.66631 |  | 0.584 | 0.77422 | 1.6658 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 657 | 0.47041 | 871 | 0.62363 | 1874 | 1.3418 |  | 1.176 | 1.5591 | 3.3544 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 657 | 4.1277 | 871 | 5.4723 | 1874 | 11.7738 |  | 10.3194 | 13.6806 | 29.4346 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 657 | 2.8721 | 871 | 3.8077 | 1874 | 8.1923 |  | 7.1803 | 9.5191 | 20.4809 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 657 | 1.0893 | 871 | 1.4441 | 1874 | 3.1072 |  | 2.7233 | 3.6104 | 7.7679 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 657 | 1.3687 | 871 | 1.8146 | 1874 | 3.9042 |  | 3.4219 | 4.5365 | 9.7604 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 657 | 1.228 | 871 | 1.628 | 1874 | 3.5028 |  | 3.0701 | 4.0701 | 8.757 | Law Courts
MELBOURNE | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE | MELBOURNE |  | MELBOURNE | MELBOURNE | MELBOURNE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 910 | 0.87395 | 1726 | 1.6576 | 2636 | 2.5316 |  | 2.1849 | 4.1441 | 6.3289 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 910 | 0.44068 | 1726 | 0.83584 | 2636 | 1.2765 |  | 1.1017 | 2.0896 | 3.1913 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 910 | 0.68037 | 1726 | 1.2905 | 2636 | 1.9708 |  | 1.7009 | 3.2262 | 4.9271 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 910 | 0.32356 | 1726 | 0.61369 | 2636 | 0.93724 |  | 0.80889 | 1.5342 | 2.3431 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 910 | 0.65155 | 1726 | 1.2358 | 2636 | 1.8874 |  | 1.6289 | 3.0895 | 4.7184 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 910 | 5.7173 | 1726 | 10.844 | 2636 | 16.5613 |  | 14.2932 | 27.1099 | 41.4031 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 910 | 3.9781 | 1726 | 7.5454 | 2636 | 11.5235 |  | 9.9454 | 18.8634 | 28.8087 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 910 | 1.5088 | 1726 | 2.8618 | 2636 | 4.3706 |  | 3.772 | 7.1544 | 10.9264 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 910 | 1.8958 | 1726 | 3.5958 | 2636 | 5.4917 |  | 4.7396 | 8.9896 | 13.7292 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 910 | 1.7009 | 1726 | 3.2262 | 2636 | 4.9271 |  | 4.2523 | 8.0654 | 12.3178 | Law Courts
MILDURA | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA | MILDURA |  | MILDURA | MILDURA | MILDURA
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1081 | 1.0382 | 1751 | 1.6816 | 2832 | 2.7198 |  | 2.5954 | 4.2041 | 6.7995 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1081 | 0.52349 | 1751 | 0.84794 | 2832 | 1.3714 |  | 1.3087 | 2.1199 | 3.4286 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1081 | 0.80822 | 1751 | 1.3092 | 2832 | 2.1174 |  | 2.0206 | 3.2729 | 5.2935 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1081 | 0.38436 | 1751 | 0.62258 | 2832 | 1.0069 |  | 0.96089 | 1.5564 | 2.5173 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1081 | 0.77399 | 1751 | 1.2537 | 2832 | 2.0277 |  | 1.935 | 3.1342 | 5.0692 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1081 | 6.7916 | 1751 | 11.001 | 2832 | 17.7927 |  | 16.9791 | 27.5026 | 44.4817 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1081 | 4.7257 | 1751 | 7.6546 | 2832 | 12.3803 |  | 11.8142 | 19.1366 | 30.9508 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1081 | 1.7923 | 1751 | 2.9032 | 2832 | 4.6955 |  | 4.4808 | 7.258 | 11.7389 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1081 | 2.2521 | 1751 | 3.6479 | 2832 | 5.9 |  | 5.6302 | 9.1198 | 14.75 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1081 | 2.0206 | 1751 | 3.2729 | 2832 | 5.2935 |  | 5.0514 | 8.1822 | 13.2336 | Law Courts
SYDNEY | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY | SYDNEY |  | SYDNEY | SYDNEY | SYDNEY
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1227 | 1.1784 | 2831 | 2.7188 | 4058 | 3.8972 |  | 2.946 | 6.7971 | 9.7431 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1227 | 0.59419 | 2831 | 1.3709 | 4058 | 1.9651 |  | 1.4855 | 3.4274 | 4.9128 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1227 | 0.91738 | 2831 | 2.1166 | 4058 | 3.034 |  | 2.2935 | 5.2916 | 7.585 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1227 | 0.43627 | 2831 | 1.0066 | 4058 | 1.4428 |  | 1.0907 | 2.5164 | 3.6071 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1227 | 0.87852 | 2831 | 2.027 | 4058 | 2.9055 |  | 2.1963 | 5.0674 | 7.2637 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1227 | 7.7089 | 2831 | 17.7864 | 4058 | 25.4953 |  | 19.2723 | 44.466 | 63.7382 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1227 | 5.3639 | 2831 | 12.376 | 4058 | 17.7399 |  | 13.4098 | 30.9399 | 44.3497 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1227 | 2.0344 | 2831 | 4.6939 | 4058 | 6.7283 |  | 5.086 | 11.7347 | 16.8207 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1227 | 2.5562 | 2831 | 5.8979 | 4058 | 8.4542 |  | 6.3906 | 14.7448 | 21.1354 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1227 | 2.2935 | 2831 | 5.2916 | 4058 | 7.585 |  | 5.7336 | 13.229 | 18.9626 | Law Courts
HOBART | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | HOBART | HOBART | HOBART | HOBART | HOBART | HOBART |  | HOBART | HOBART | HOBART
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1352 | 1.2984 | 2389 | 2.2944 | 2389 | 2.2944 |  | 3.2461 | 5.7359 | 5.7359 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1352 | 0.65472 | 2389 | 1.1569 | 2389 | 1.1569 |  | 1.6368 | 2.8923 | 2.8923 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1352 | 1.0108 | 2389 | 1.7862 | 2389 | 1.7862 |  | 2.5271 | 4.4654 | 4.4654 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1352 | 0.48071 | 2389 | 0.84942 | 2389 | 0.84942 |  | 1.2018 | 2.1236 | 2.1236 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1352 | 0.96802 | 2389 | 1.7105 | 2389 | 1.7105 |  | 2.42 | 4.2763 | 4.2763 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1352 | 8.4942 | 2389 | 15.0094 | 2389 | 15.0094 |  | 21.2356 | 37.5236 | 37.5236 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1352 | 5.9104 | 2389 | 10.4437 | 2389 | 10.4437 |  | 14.776 | 26.1093 | 26.1093 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1352 | 2.2417 | 2389 | 3.961 | 2389 | 3.961 |  | 5.6041 | 9.9026 | 9.9026 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1352 | 2.8167 | 2389 | 4.9771 | 2389 | 4.9771 |  | 7.0417 | 12.4427 | 12.4427 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1352 | 2.5271 | 2389 | 4.4654 | 2389 | 4.4654 |  | 6.3178 | 11.1636 | 11.1636 | Law Courts
BRISBANE | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE | BRISBANE |  | BRISBANE | BRISBANE | BRISBANE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1381 | 1.3263 | 593 | 0.56951 | 1974 | 1.8958 |  | 3.3157 | 1.4238 | 4.7395 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1381 | 0.66877 | 593 | 0.28717 | 1974 | 0.95593 |  | 1.6719 | 0.71792 | 2.3898 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1381 | 1.0325 | 593 | 0.44336 | 1974 | 1.4759 |  | 2.5813 | 1.1084 | 3.6897 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1381 | 0.49102 | 593 | 0.21084 | 1974 | 0.70187 |  | 1.2276 | 0.52711 | 1.7547 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1381 | 0.98878 | 593 | 0.42458 | 1974 | 1.4134 |  | 2.472 | 1.0615 | 3.5334 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1381 | 8.6764 | 593 | 3.7257 | 1974 | 12.4021 |  | 21.6911 | 9.3141 | 31.0052 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1381 | 6.0372 | 593 | 2.5923 | 1974 | 8.6295 |  | 15.0929 | 6.4809 | 21.5738 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1381 | 2.2897 | 593 | 0.98321 | 1974 | 3.273 |  | 5.7244 | 2.458 | 8.1824 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1381 | 2.8771 | 593 | 1.2354 | 1974 | 4.1125 |  | 7.1927 | 3.0885 | 10.2812 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1381 | 2.5813 | 593 | 1.1084 | 1974 | 3.6897 |  | 6.4533 | 2.771 | 9.2243 | Law Courts
CANBERRA | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA |  | CANBERRA | CANBERRA | CANBERRA
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1398 | 1.3426 | 2873 | 2.7592 | 4271 | 4.1018 |  | 3.3565 | 6.898 | 10.2545 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1398 | 0.677 | 2873 | 1.3913 | 4271 | 2.0683 |  | 1.6925 | 3.4782 | 5.1707 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1398 | 1.0452 | 2873 | 2.148 | 4271 | 3.1933 |  | 2.6131 | 5.3701 | 7.9832 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1398 | 0.49707 | 2873 | 1.0215 | 4271 | 1.5186 |  | 1.2427 | 2.5538 | 3.7964 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1398 | 1.001 | 2873 | 2.057 | 4271 | 3.058 |  | 2.5024 | 5.1426 | 7.645 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1398 | 8.7832 | 2873 | 18.0503 | 4271 | 26.8335 |  | 21.9581 | 45.1257 | 67.0838 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1398 | 6.1115 | 2873 | 12.5596 | 4271 | 18.671 |  | 15.2787 | 31.3989 | 46.6776 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1398 | 2.3179 | 2873 | 4.7635 | 4271 | 7.0815 |  | 5.7948 | 11.9088 | 17.7036 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1398 | 2.9125 | 2873 | 5.9854 | 4271 | 8.8979 |  | 7.2812 | 14.9635 | 22.2448 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1398 | 2.6131 | 2873 | 5.3701 | 4271 | 7.9832 |  | 6.5327 | 13.4252 | 19.9579 | Law Courts
ALICE SPRINGS | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS |  | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1628 | 1.5635 | 1532 | 1.4713 | 3160 | 3.0348 |  | 3.9088 | 3.6783 | 7.587 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1628 | 0.78838 | 1532 | 0.74189 | 3160 | 1.5303 |  | 1.9709 | 1.8547 | 3.8257 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1628 | 1.2172 | 1532 | 1.1454 | 3160 | 2.3626 |  | 3.043 | 2.8636 | 5.9065 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1628 | 0.57884 | 1532 | 0.54471 | 3160 | 1.1236 |  | 1.4471 | 1.3618 | 2.8089 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1628 | 1.1656 | 1532 | 1.0969 | 3160 | 2.2625 |  | 2.9141 | 2.7422 | 5.6563 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1628 | 10.2283 | 1532 | 9.6251 | 3160 | 19.8534 |  | 25.5707 | 24.0628 | 49.6335 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1628 | 7.1169 | 1532 | 6.6973 | 3160 | 13.8142 |  | 17.7923 | 16.7432 | 34.5355 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1628 | 2.6993 | 1532 | 2.5401 | 3160 | 5.2394 |  | 6.7482 | 6.3503 | 13.0984 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1628 | 3.3917 | 1532 | 3.1917 | 3160 | 6.5833 |  | 8.4792 | 7.9792 | 16.4583 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1628 | 3.043 | 1532 | 2.8636 | 3160 | 5.9065 |  | 7.6075 | 7.1589 | 14.7664 | Law Courts
WAGGA | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA |  | WAGGA | WAGGA | WAGGA
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 2806 | 2.6948 | 2806 | 2.6948 | 4855 | 4.6627 |  | 6.7371 | 6.7371 | 11.6567 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 2806 | 1.3588 | 2806 | 1.3588 | 3160 | 1.5303 |  | 3.3971 | 3.3971 | 3.8257 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 2806 | 2.0979 | 2806 | 2.0979 | 3160 | 2.3626 |  | 5.2449 | 5.2449 | 5.9065 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 2806 | 0.99769 | 2806 | 0.99769 | 3160 | 1.1236 |  | 2.4942 | 2.4942 | 2.8089 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 2806 | 2.0091 | 2806 | 2.0091 | 3160 | 2.2625 |  | 5.0227 | 5.0227 | 5.6563 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 2806 | 17.6293 | 2806 | 17.6293 | 3160 | 19.8534 |  | 44.0733 | 44.0733 | 49.6335 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 2806 | 12.2667 | 2806 | 12.2667 | 3160 | 13.8142 |  | 30.6667 | 30.6667 | 34.5355 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 2806 | 4.6524 | 2806 | 4.6524 | 3160 | 5.2394 |  | 11.6311 | 11.6311 | 13.0984 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 2806 | 5.8458 | 2806 | 5.8458 | 3160 | 6.5833 |  | 14.6146 | 14.6146 | 16.4583 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 2806 | 5.2449 | 2806 | 5.2449 | 3160 | 5.9065 |  | 13.1121 | 13.1121 | 14.7664 | Law Courts
CLONCURRY | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY |  | CLONCURRY | CLONCURRY | CLONCURRY
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 2946 | 2.8293 | 1829 | 1.7565 | 4775 | 4.5858 |  | 7.0732 | 4.3914 | 11.4646 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 2946 | 1.4266 | 1829 | 0.88571 | 4775 | 2.3123 |  | 3.5666 | 2.2143 | 5.7809 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 2946 | 2.2026 | 1829 | 1.3675 | 4775 | 3.5701 |  | 5.5065 | 3.4187 | 8.9252 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 2946 | 1.0475 | 1829 | 0.65031 | 4775 | 1.6978 |  | 2.6187 | 1.6258 | 4.2444 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 2946 | 2.1093 | 1829 | 1.3095 | 4775 | 3.4189 |  | 5.2733 | 3.2739 | 8.5471 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 2946 | 18.5089 | 1829 | 11.4911 | 4775 | 30 |  | 46.2723 | 28.7277 | 75 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 2946 | 12.8787 | 1829 | 7.9956 | 4775 | 20.8743 |  | 32.1967 | 19.9891 | 52.1858 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 2946 | 4.8846 | 1829 | 3.0325 | 4775 | 7.9171 |  | 12.2114 | 7.5813 | 19.7927 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 2946 | 6.1375 | 1829 | 3.8104 | 4775 | 9.9479 |  | 15.3438 | 9.526 | 24.8698 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 2946 | 5.5065 | 1829 | 3.4187 | 4775 | 8.9252 |  | 13.7664 | 8.5467 | 22.3131 | Law Courts
PORT HEDLAND | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND |  | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 4304 | 4.1335 | 2704 | 2.5969 | 7285 | 6.9964 |  | 10.3337 | 6.4922 | 17.491 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 4304 | 2.0843 | 2704 | 1.3094 | 7285 | 3.5278 |  | 5.2107 | 3.2736 | 8.8196 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 4304 | 3.2179 | 2704 | 2.0217 | 7285 | 5.4467 |  | 8.0449 | 5.0542 | 13.6168 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 4304 | 1.5303 | 2704 | 0.96142 | 7285 | 2.5902 |  | 3.8258 | 2.4036 | 6.4756 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 4304 | 3.0816 | 2704 | 1.936 | 7285 | 5.216 |  | 7.7041 | 4.8401 | 13.04 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 4304 | 27.0408 | 2704 | 16.9885 | 7285 | 45.7696 |  | 67.6021 | 42.4712 | 114.4241 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 4304 | 18.8153 | 2704 | 11.8208 | 7285 | 31.847 |  | 47.0383 | 29.5519 | 79.6175 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 4304 | 7.1362 | 2704 | 4.4833 | 7285 | 12.0788 |  | 17.8404 | 11.2083 | 30.1969 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 4304 | 8.9667 | 2704 | 5.6333 | 7285 | 15.1771 |  | 22.4167 | 14.0833 | 37.9427 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 4304 | 8.0449 | 2704 | 5.0542 | 7285 | 13.6168 |  | 20.1121 | 12.6355 | 34.0421 | Law Courts
TOWNSVILLE | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE |  | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 4382 | 4.2084 | 2704 | 2.5969 | 7086 | 6.8053 |  | 10.521 | 6.4922 | 17.0132 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 4382 | 2.122 | 2704 | 1.3094 | 7086 | 3.4315 |  | 5.3051 | 3.2736 | 8.5787 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 4382 | 3.2763 | 2704 | 2.0217 | 7086 | 5.2979 |  | 8.1907 | 5.0542 | 13.2449 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 4382 | 1.558 | 2704 | 0.96142 | 7086 | 2.5195 |  | 3.8951 | 2.4036 | 6.2987 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 4382 | 3.1375 | 2704 | 1.936 | 7086 | 5.0735 |  | 7.8437 | 4.8401 | 12.6838 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 4382 | 27.5309 | 2704 | 16.9885 | 7086 | 44.5194 |  | 68.8272 | 42.4712 | 111.2984 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 4382 | 19.1563 | 2704 | 11.8208 | 7086 | 30.977 |  | 47.8907 | 29.5519 | 77.4426 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 4382 | 7.2655 | 2704 | 4.4833 | 7086 | 11.7488 |  | 18.1637 | 11.2083 | 29.372 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 4382 | 9.1292 | 2704 | 5.6333 | 7086 | 14.7625 |  | 22.8229 | 14.0833 | 36.9062 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 4382 | 8.1907 | 2704 | 5.0542 | 7086 | 33.1121 |  | 20.4766 | 12.6355 | 82.7804 | Law Courts
DARWIN | [10 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | DARWIN | DARWIN | DARWIN | DARWIN |  | DARWIN | DARWIN |  | DARWIN | DARWIN | DARWIN
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 7125 | 6.8427 | 6176 | 5.9313 | 13301 | 12.7741 |  | 17.1068 | 14.8283 | 31.9352 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 7125 | 3.4504 | 6176 | 2.9908 | 7086 | 3.4315 |  | 8.6259 | 7.477 | 8.5787 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 7125 | 5.3271 | 6176 | 4.6176 | 7086 | 5.2979 |  | 13.3178 | 11.5439 | 13.2449 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 7125 | 2.5333 | 6176 | 2.1959 | 7086 | 2.5195 |  | 6.3333 | 5.4898 | 6.2987 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 7125 | 5.1014 | 6176 | 4.422 | 7086 | 5.0735 |  | 12.7536 | 11.0549 | 12.6838 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 7125 | 44.7644 | 6176 | 38.8021 | 7086 | 44.5194 |  | 111.911 | 97.0052 | 111.2984 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 7125 | 31.1475 | 6176 | 26.9989 | 7086 | 30.977 |  | 77.8689 | 67.4973 | 77.4426 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 7125 | 11.8135 | 6176 | 10.24 | 7086 | 11.7488 |  | 29.5337 | 25.6 | 29.372 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 7125 | 14.8438 | 6176 | 12.8667 | 7086 | 14.7625 |  | 37.1094 | 32.1667 | 36.9062 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 7125 | 13.3178 | 6176 | 11.5439 | 7086 | 13.2449 |  | 33.2944 | 28.8598 | 33.1121 | Law Courts

## canberra
CANBERRA GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day |  | Night |  | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA | CANBERRA
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1398 | 1.3426 | 2873 | 2.7592 | 4271 | 4.1018 | 3.3565 | 6.898 | 10.2545 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1398 | 0.677 | 2873 | 1.3913 | 4271 | 2.0683 | 1.6925 | 3.4782 | 5.1707 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1398 | 1.0452 | 2873 | 2.148 | 4271 | 3.1933 | 2.6131 | 5.3701 | 7.9832 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1398 | 0.49707 | 2873 | 1.0215 | 4271 | 1.5186 | 1.2427 | 2.5538 | 3.7964 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1398 | 1.001 | 2873 | 2.057 | 4271 | 3.058 | 2.5024 | 5.1426 | 7.645 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1398 | 8.7832 | 2873 | 18.0503 | 4271 | 26.8335 | 21.9581 | 45.1257 | 67.0838 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1398 | 6.1115 | 2873 | 12.5596 | 4271 | 18.671 | 15.2787 | 31.3989 | 46.6776 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1398 | 2.3179 | 2873 | 4.7635 | 4271 | 7.0815 | 5.7948 | 11.9088 | 17.7036 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1398 | 2.9125 | 2873 | 5.9854 | 4271 | 8.8979 | 7.2812 | 14.9635 | 22.2448 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1398 | 2.6131 | 2873 | 5.3701 | 4271 | 7.9832 | 6.5327 | 13.4252 | 19.9579 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## alice springs
ALICE SPRINGS GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS | ALICE SPRINGS
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 1628 | 1.5635 | 1532 | 1.4713 | 3160 | 3.0348 | 3.9088 | 3.6783 | 7.587 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 1628 | 0.78838 | 1532 | 0.74189 | 3160 | 1.5303 | 1.9709 | 1.8547 | 3.8257 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 1628 | 1.2172 | 1532 | 1.1454 | 3160 | 2.3626 | 3.043 | 2.8636 | 5.9065 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 1628 | 0.57884 | 1532 | 0.54471 | 3160 | 1.1236 | 1.4471 | 1.3618 | 2.8089 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 1628 | 1.1656 | 1532 | 1.0969 | 3160 | 2.2625 | 2.9141 | 2.7422 | 5.6563 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 1628 | 10.2283 | 1532 | 9.6251 | 3160 | 19.8534 | 25.5707 | 24.0628 | 49.6335 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 1628 | 7.1169 | 1532 | 6.6973 | 3160 | 13.8142 | 17.7923 | 16.7432 | 34.5355 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 1628 | 2.6993 | 1532 | 2.5401 | 3160 | 5.2394 | 6.7482 | 6.3503 | 13.0984 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 1628 | 3.3917 | 1532 | 3.1917 | 3160 | 6.5833 | 8.4792 | 7.9792 | 16.4583 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 1628 | 3.043 | 1532 | 2.8636 | 3160 | 5.9065 | 7.6075 | 7.1589 | 14.7664 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## wagga
WAGGA GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA | WAGGA
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 2806 | 2.6948 | 2806 | 2.6948 | 4855 | 4.6627 | 6.7371 | 6.7371 | 11.6567 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 2806 | 1.3588 | 2806 | 1.3588 | 3160 | 1.5303 | 3.3971 | 3.3971 | 3.8257 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 2806 | 2.0979 | 2806 | 2.0979 | 3160 | 2.3626 | 5.2449 | 5.2449 | 5.9065 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 2806 | 0.99769 | 2806 | 0.99769 | 3160 | 1.1236 | 2.4942 | 2.4942 | 2.8089 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 2806 | 2.0091 | 2806 | 2.0091 | 3160 | 2.2625 | 5.0227 | 5.0227 | 5.6563 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 2806 | 17.6293 | 2806 | 17.6293 | 3160 | 19.8534 | 44.0733 | 44.0733 | 49.6335 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 2806 | 12.2667 | 2806 | 12.2667 | 3160 | 13.8142 | 30.6667 | 30.6667 | 34.5355 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 2806 | 4.6524 | 2806 | 4.6524 | 3160 | 5.2394 | 11.6311 | 11.6311 | 13.0984 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 2806 | 5.8458 | 2806 | 5.8458 | 3160 | 6.5833 | 14.6146 | 14.6146 | 16.4583 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 2806 | 5.2449 | 2806 | 5.2449 | 3160 | 5.9065 | 13.1121 | 13.1121 | 14.7664 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## cloncurry
CLONCURRY GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY | CLONCURRY
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 2946 | 2.8293 | 1829 | 1.7565 | 4775 | 4.5858 | 7.0732 | 4.3914 | 11.4646 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 2946 | 1.4266 | 1829 | 0.88571 | 4775 | 2.3123 | 3.5666 | 2.2143 | 5.7809 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 2946 | 2.2026 | 1829 | 1.3675 | 4775 | 3.5701 | 5.5065 | 3.4187 | 8.9252 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 2946 | 1.0475 | 1829 | 0.65031 | 4775 | 1.6978 | 2.6187 | 1.6258 | 4.2444 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 2946 | 2.1093 | 1829 | 1.3095 | 4775 | 3.4189 | 5.2733 | 3.2739 | 8.5471 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 2946 | 18.5089 | 1829 | 11.4911 | 4775 | 30 | 46.2723 | 28.7277 | 75 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 2946 | 12.8787 | 1829 | 7.9956 | 4775 | 20.8743 | 32.1967 | 19.9891 | 52.1858 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 2946 | 4.8846 | 1829 | 3.0325 | 4775 | 7.9171 | 12.2114 | 7.5813 | 19.7927 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 2946 | 6.1375 | 1829 | 3.8104 | 4775 | 9.9479 | 15.3438 | 9.526 | 24.8698 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 2946 | 5.5065 | 1829 | 3.4187 | 4775 | 8.9252 | 13.7664 | 8.5467 | 22.3131 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## port hedland
PORT HEDLAND GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND | PORT HEDLAND
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 4304 | 4.1335 | 2704 | 2.5969 | 7285 | 6.9964 | 10.3337 | 6.4922 | 17.491 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 4304 | 2.0843 | 2704 | 1.3094 | 7285 | 3.5278 | 5.2107 | 3.2736 | 8.8196 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 4304 | 3.2179 | 2704 | 2.0217 | 7285 | 5.4467 | 8.0449 | 5.0542 | 13.6168 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 4304 | 1.5303 | 2704 | 0.96142 | 7285 | 2.5902 | 3.8258 | 2.4036 | 6.4756 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 4304 | 3.0816 | 2704 | 1.936 | 7285 | 5.216 | 7.7041 | 4.8401 | 13.04 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 4304 | 27.0408 | 2704 | 16.9885 | 7285 | 45.7696 | 67.6021 | 42.4712 | 114.4241 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 4304 | 18.8153 | 2704 | 11.8208 | 7285 | 31.847 | 47.0383 | 29.5519 | 79.6175 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 4304 | 7.1362 | 2704 | 4.4833 | 7285 | 12.0788 | 17.8404 | 11.2083 | 30.1969 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 4304 | 8.9667 | 2704 | 5.6333 | 7285 | 15.1771 | 22.4167 | 14.0833 | 37.9427 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 4304 | 8.0449 | 2704 | 5.0542 | 7285 | 13.6168 | 20.1121 | 12.6355 | 34.0421 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## townsville
TOWNSVILLE GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs |  |  |  |  | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE | TOWNSVILLE
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 4382 | 4.2084 | 2704 | 2.5969 | 7086 | 6.8053 | 10.521 | 6.4922 | 17.0132 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 4382 | 2.122 | 2704 | 1.3094 | 7086 | 3.4315 | 5.3051 | 3.2736 | 8.5787 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 4382 | 3.2763 | 2704 | 2.0217 | 7086 | 5.2979 | 8.1907 | 5.0542 | 13.2449 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 4382 | 1.558 | 2704 | 0.96142 | 7086 | 2.5195 | 3.8951 | 2.4036 | 6.2987 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 4382 | 3.1375 | 2704 | 1.936 | 7086 | 5.0735 | 7.8437 | 4.8401 | 12.6838 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 4382 | 27.5309 | 2704 | 16.9885 | 7086 | 44.5194 | 68.8272 | 42.4712 | 111.2984 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 4382 | 19.1563 | 2704 | 11.8208 | 7086 | 30.977 | 47.8907 | 29.5519 | 77.4426 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 4382 | 7.2655 | 2704 | 4.4833 | 7086 | 11.7488 | 18.1637 | 11.2083 | 29.372 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 4382 | 9.1292 | 2704 | 5.6333 | 7086 | 14.7625 | 22.8229 | 14.0833 | 36.9062 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 4382 | 8.1907 | 2704 | 5.0542 | 7086 | 33.1121 | 20.4766 | 12.6355 | 82.7804 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.

## darwin
DARWIN GPAC SAVINGS AS % OF BUILDING ENERGY USE AND AS % OF HVAC USE
(Spry Associates Pty Ltd calculations from weather frequency psychometric charts)
weather/economic calculations & day/night ratios (sorted by day energy use)
RUNNING COST SAVING - $/600 l/s
|  |  | Day | Night | 24 Hr | ratio | ratio
NUMBER | SITE |  | Annual | Annual | Annual | day to total | night to total
1 | Adelaide |  | 668 | 1206 | 1874 | 0.35646 | 0.64354
10 | Perth |  | 657 | 871 | 1528 | 0.42997 | 0.57003
8 | Melbourne |  | 910 | 1726 | 2636 | 0.34522 | 0.65478
9 | Mildura |  | 1081 | 1751 | 2832 | 0.38171 | 0.61829
12 | Sydney |  | 1227 | 2831 | 4058 | 0.30237 | 0.69763
7 | Hobart |  | 1352 | 2389 | 3741 | 0.3614 | 0.6386
3 | Brisbane |  | 1381 | 593 | 1974 | 0.69959 | 0.30041
4 | Canberra |  | 1398 | 2873 | 4271 | 0.32732 | 0.67268
2 | Alice Springs |  | 1628 | 1532 | 3160 | 0.51519 | 0.48481
14 | Wagga |  | 2806 | 2049 | 4855 | 0.57796 | 0.42204
5 | Cloncurry |  | 2946 | 1829 | 4775 | 0.61696 | 0.38304
11 | Port Hedland |  | 4304 | 2981 | 7285 | 0.5908 | 0.4092
13 | Townsville |  | 4382 | 2704 | 7086 | 0.6184 | 0.3816
6 | Darwin |  | 7125 | 6176 | 13301 | 0.53567 | 0.46433
120 person, 750-1500 m2 area (occupancy dependent): Using 'COAG 2012 baseline energy consumption report, commercial bldgs (available on line)' averages and
Assumptions: HVAC uses 40% of building energy,
note: VET and School calculations unreliable as low energy use indicates little heating and cooling (is this true?)
[11 empty] | GPAC savings as $/a. and as % of all annual energy costs | [5 empty] | GPAC annual savings as % of HVAC annual energy costs
|  | (1 kWH=3.6mJ) | [7 empty] | DARWIN | DARWIN | DARWIN | DARWIN |  | DARWIN | DARWIN |  | DARWIN | DARWIN | DARWIN
COAG bldg. | pro rata | pro rata | whole bldg. | whole bldg. | energy | whole bldg. | HVAC cost | HVAC | COAG bldg. | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use | GPAC use |  | GPAC use | GPAC use | GPAC use | COAG bldg.
classification | energy use | energy use | area | energy use | price | energy cost | fraction of | cost | classification | day saving | day saving | night saving | night saving | 24 hr saving | 24 hr saving |  | day saving | night saving | 24 hr saving | classification
2020 projected | MJ/ m2.a. | kWH/m2.a. | sq. M. | kWH/a. | $/kWH | $/a. | whole cost | $/a. |  | $/a. | % | $/a. | % | $/a. | % |  | % | % | %
Office – Whole Buildings | 833 | 231.3889 | 1500 | 347083.3333 | 0.3 | 104125 | 0.4 | 41650 | Office – Whole Buildings | 7125 | 6.8427 | 6176 | 5.9313 | 13301 | 12.7741 |  | 17.1068 | 14.8283 | 31.9352 | Office – Whole Buildings
Hotels | 1652 | 458.8889 | 1500 | 688333.3333 | 0.3 | 206500 | 0.4 | 82600 | Hotels | 7125 | 3.4504 | 6176 | 2.9908 | 7086 | 3.4315 |  | 8.6259 | 7.477 | 8.5787 | Hotels
Shopping Centres - Base +Tenancy* | 1605 | 445.8333 | 1000 | 445833.3333 | 0.3 | 133750 | 0.4 | 53500 | Shopping Centres - Base +Tenancy* | 7125 | 5.3271 | 6176 | 4.6176 | 7086 | 5.2979 |  | 13.3178 | 11.5439 | 13.2449 | Shopping Centres - Base +Tenancy*
Supermarkets (Whole) * | 3375 | 937.5 | 1000 | 937500 | 0.3 | 281250 | 0.4 | 112500 | Supermarkets (Whole) * | 7125 | 2.5333 | 6176 | 2.1959 | 7086 | 2.5195 |  | 6.3333 | 5.4898 | 6.2987 | Supermarkets (Whole) *
Hospitals | 1676 | 465.5556 | 1000 | 465555.5556 | 0.3 | 139666.6667 | 0.4 | 55866.6667 | Hospitals | 7125 | 5.1014 | 6176 | 4.422 | 7086 | 5.0735 |  | 12.7536 | 11.0549 | 12.6838 | Hospitals
Schools | 191 | 53.0556 | 1000 | 53055.5556 | 0.3 | 15916.6667 | 0.4 | 6366.6667 | Schools | 7125 | 44.7644 | 6176 | 38.8021 | 7086 | 44.5194 |  | 111.911 | 97.0052 | 111.2984 | Schools
VET buildings | 366 | 101.6667 | 750 | 76250 | 0.3 | 22875 | 0.4 | 9150 | VET buildings | 7125 | 31.1475 | 6176 | 26.9989 | 7086 | 30.977 |  | 77.8689 | 67.4973 | 77.4426 | VET buildings
Universities | 965 | 268.0556 | 750 | 201041.6667 | 0.3 | 60312.5 | 0.4 | 24125 | Universities | 7125 | 11.8135 | 6176 | 10.24 | 7086 | 11.7488 |  | 29.5337 | 25.6 | 29.372 | Universities
Museums,galleries, libraries | 768 | 213.3333 | 750 | 160000 | 0.3 | 48000 | 0.4 | 19200 | Museums,galleries, libraries | 7125 | 14.8438 | 6176 | 12.8667 | 7086 | 14.7625 |  | 37.1094 | 32.1667 | 36.9062 | Museums,galleries, libraries
Law Courts | 642 | 178.3333 | 1000 | 178333.3333 | 0.3 | 53500 | 0.4 | 21400 | Law Courts | 7125 | 13.3178 | 6176 | 11.5439 | 7086 | 13.2449 |  | 33.2944 | 28.8598 | 33.1121 | Law Courts
From COAG report: Table 1.3 - Australian Average Energy Intensity Trends by Building Type, 1999 – 2020
Units: MJ/ m2.a | 1999 | 2009 | 2020
Office - Tenancies | 400 | 385 | 368
Office - Base Buildings | 594 | 532 | 465
Office – Whole Buildings | 994 | 917 | 833
Hotels | 1209 | 1420 | 1652
Shopping Centres - Base Buildings* | 403 | 403 | 403
Shopping Centres - Tenancy* | - | 1202 | 1202
Shopping Centres - Base +Tenancy* | - | 1605 | 1605
Supermarkets (Whole) * | - | 3375 | 3375
Hospitals | 1420 | 1542 | 1676
Schools | 166 | 178 | 191
VET buildings | 368 | 367 | 366
Universities | 780 | 868 | 965
Public Buildings# | 1111 | 947 | 768
Law Courts | 467 | 550 | 642
* Only limited time-series data was available for retail buildings, insufficient to describe any intensity trends. #Museums, galleries and libraries.