ANALYSIS OF CHANGES 2023 National Electrical Code® Comprehensive Quick-Reference Handout • Chapters 1–8

⚡ GLOBAL CHANGES & STRUCTURAL UPDATES

SYSTEMS EXCEEDING 1,000V AC / 1,500V DC — Several new articles were created to address medium-voltage systems. Existing requirements were relocated from various articles for improved usability.

NEW ARTICLES FOR SYSTEMS >1,000V AC / 1,500V DC

| NEW | Art. 235 | Branch Circuits, Feeders, and Services Over 1,000V ac or 1,500V dc. |
| --- | --- | --- |
| NEW | Art. 245 | Overcurrent Protection for Systems Over 1,000V ac or 1,500V dc. |
| NEW | Art. 305 | General Requirements for Wiring Methods/Materials >1,000V ac or 1,500V dc. |
| NEW | Art. 315 | Medium Voltage Conductors, Cable, Cable Joints, and Cable Terminations [replaced former Art. 311]. |
| NEW | Art. 395 | Outdoor Overhead Conductors, Over 1000 Volts [was Art. 399]. |
| NEW | Art. 495 | Equipment for Systems >1,000V ac or 1,500V dc [was Art. 490]. |

OTHER NEW ARTICLES

| NEW | Art. 369 | Insulated Bus Pipe (IBP) / Tubular Covered Conductors (TCC). |
| --- | --- | --- |
| NEW | Art. 371 | Flexible Bus Systems. |
| NEW | Art. 512 | Cannabis Oil Equipment and Systems Using Flammable Materials. |
| NEW | Art. 722 | Cables for Power-Limited Circuits and Fault-Managed Power Circuits [from Art. 725]. |
| NEW | Art. 724 | Class 1 Power-Limited Circuits (covers Class 1 power-limited remote-control and signaling circuits per 724.1) [from Art. 725]. |
| NEW | Art. 726 | Class 4 Fault-Managed Power Systems. |

CHAPTER 7 HOUSEKEEPING

| DEL | Art. 712 | DC Microgrids — deleted; requirements relocated to Art. 705. |
| --- | --- | --- |
| MOVED | Art. 722 | Cables for power-limited and fault-managed circuits — relocated from Art. 725. |
| MOVED | Art. 724 | Class 1 power-limited, remote-control, and signaling circuits — relocated from Art. 725. |

📖 CHAPTER 1 — GENERAL (Art. 90 & 100)

| REV | 90.1 | Article 90 renumbered to comply with the 2020 NEC Style Manual. |
| --- | --- | --- |
| REV | 90.4 | New Informational Note added; section editorially revised. |
| REV | 90.5 | Applicability of referenced standards changed. |
| REV | Art. 100 | Scope and layout revised to correlate with 2020 NEC Style Manual. All 800+ definitions now consolidated in Article 100. |
| REV | Art. 100 | "Accessible" (wiring methods) — clarified. |
| REV | Art. 100 | "Appliance" — types of appliances now stated in definition. |
| REV | Art. 100 | "Attachment Fitting, Weight-Supporting (WSAF)" — revised for accuracy. |
| REV | Art. 100 | "Battery, Stationary Standby" — revised for accuracy. |
| NEW | Art. 100 | "Branch Circuit, Motor" — new definition added. |
| NEW | Art. 100 | "Cable Connector" (Hazardous Locations) — new definition. |
| NEW | Art. 100 | "Cable Joint" — new definition for medium voltage splices. |
| NEW | Art. 100 | "Cable Termination" — new definition for MV cable connections. |
| NEW | Art. 100 | "Class 4 Circuit" and related terms — new definitions for new technologies. |
| REV | Art. 100 | "Commissioning" — relocated and revised for accuracy. |
| REV | Art. 100 | "Communications Circuit" — revised for accuracy. |
| NEW | Art. 100 | "Cord, Flexible" / "Cord Connector" / "Cord Set" — new definitions added. |
| NEW | Art. 100 | "Counter (Countertop)" — new definition added. |
| NEW | Art. 100 | "Emergency Luminaire, Battery-Equipped" — new definition. |
| REV | Art. 100 | "Emergency Luminaire, Directly-Controlled" — revised for clarity. |
| NEW | Art. 100 | "Emergency Power Supply System (EPSS)" — new term added. |
| NEW | Art. 100 | "Energized, Likely to Become" — now a defined term. |
| REV | Art. 100 | "Equipotential Plane" — revised to fix error; agricultural definition revised for clarity. |
| NEW | Art. 100 | "Fault-Managed Power" — new definition for Class 4 (Art. 726) circuits. |
| NEW | Art. 100 | "Fibers/Flyings, Combustible" and "Ignitible" — now defined. |
| NEW | Art. 100 | "Ground-Fault Circuit Interrupter, Special Purpose (SPGFCI)" — new type of GF protection. |
| NEW | Art. 100 | "Grounded System, Impedance" — now defined. |
| REV | Art. 100 | "Microgrid" — term simplified from "microgrid system"; more clearly defined. |
| NEW | Art. 100 | "Normal High-Water Level" — new definitions for electrical datum plane. |
| NEW | Art. 100 | "Panelboard, Enclosed" — new term to avoid misuse of existing terms. |
| NEW | Art. 100 | "Passenger Transportation Facilities" — new term added. |
| NEW | Art. 100 | "Patient Care-Related Electrical Equipment" — new definition. |
| REV | Art. 100 | "Pool, Permanently Installed" / "Pool, Storable" — water depth removed from definitions. |
| NEW | Art. 100 | "Power-Supply Cord" — now defined. |
| NEW | Art. 100 | "Primary Source" — new definition added. |
| NEW | Art. 100 | "Receptacle, Weight-Supporting Ceiling (WSCR)" — now defined. |
| NEW | Art. 100 | "Restricted Industrial Establishment" (Hazardous Locations) — new term. |
| NEW | Art. 100 | "Servicing" — new definition added. |
| NEW | Art. 100 | "Short Circuit" — new definition for existing term. |
| REV | Art. 100 | "Stand-Alone System" — revised for accuracy. |
| NEW | Art. 100 | "Stored-Energy Power Supply Systems (SEPSS)" — new definition. |
| NEW | Art. 100 | "Stranding" types (Compact, Compressed, Concentric) — now defined. |
| NEW | Art. 100 | "Transfer Switch, Meter-Mounted" — new definition. |
| REV | Art. 100 | "Transformer" — edited for accuracy and usability. |
| REV | Art. 100 | "Uninterruptible Power Supply (UPS)" — edited for accuracy. |
| NEW | Art. 100 | "Unit Equipment" — new definition for existing term. |
| NEW | Art. 100 | "Work Surface" — now a defined term. |

ARTICLE 110 — GENERAL REQUIREMENTS

| REV | 110.3 | Equipment examination/identification requirements revised; cybersecurity added at 110.3(A)(8) for network-connected life-safety equipment; 110.3(B) clarified for listed/labeled/identified equipment instructions. |
| --- | --- | --- |
| REV | 110.8 | Application of permitted wiring methods clarified. |
| REV | 110.9 | Editorially revised for consistency with defined terms. |
| REV | 110.12 | Editorially revised to comply with NEC Style Manual. |
| REV | 110.14 | Examples of dissimilar metals removed. |
| REV | 110.16 | Arc-flash hazard warning requirements increased and clarified. |
| NEW | 110.17 | New section addressing servicing and maintenance of equipment. |
| NEW | 110.20 | New section addressing reconditioned equipment. |
| REV | 110.21 | Listing mark removal requirements for reconditioned equipment clarified. |
| REV | 110.22 | Supply circuit marking requirements for disconnecting means clarified. |
| REV | 110.26 | Egress obstruction clarified; limited access refined; working space must be as level and flat as practical; service equipment requires dedicated electrical space. Similar changes in 110.34. |
| NEW | 110.29 | New section correlating with changes in Art. 100 for "In Sight From." |

🔌 CHAPTER 2 — WIRING & PROTECTION (Art. 200–250)

| REV | 200.4 | Informational Note added indicating location of allowances "elsewhere in the Code." |
| --- | --- | --- |
| REV | 210.1 | Scope and title revised to limit applicability (not over 1,000V ac / 1,500V dc). |
| REV | 210.4 | Editorial revision; column-width panelboards now mentioned. |
| REV | 210.8(A) | Dwelling GFCI: Class A GFCI now required; "readily accessible" requirement retained; cord measurement revised; GFCI requirements greatly expanded to 125V–250V receptacles, including indoor damp/wet locations (item 11). |
| REV | 210.8(B) | Other than dwellings: damp locations, accessory buildings, laundry areas, and bathtub/shower stall areas added; 250V receptacles now included. |
| REV | 210.8(D) | Specific appliances: expanded list including dishwashers, electric ranges, wall-mounted ovens, counter-mounted cooking units, clothes dryers, and microwave ovens. |
| REV | 210.8(E) | GFCI for equipment requiring servicing — now required for all receptacles per 210.63. |
| REV | 210.8(F) | Outdoor outlets: GFCI required for dwelling outdoor outlets 50A or less, 150V-to-ground or less. Includes 240V HVAC "outlets" (Exception No. 2 delays GFCI requirement for listed HVAC equipment until Sept. 1, 2026). |
| REV | 210.11 | Dwelling unit garage circuit requirements reduced. |
| REV | 210.12 | AFCI requirements editorially revised; 10A circuits addressed; new locations added. |
| REV | 210.17 | Assisted living facilities must comply with hotel/motel circuiting requirements. |
| NEW | 210.18 | Multioutlet branch circuits rated 10A now permitted. |
| REV | 210.23 | Multioutlet 10A branch circuits now addressed. |
| REV | 210.52 | Stationary appliances addressed; receptacles no longer required for kitchen islands/peninsulas; if installed for an island/peninsula they must be above or in the countertop/work surface — below-counter installation no longer permitted (provisions for future wiring required if none installed). |
| REV | 210.62 | Show window receptacle requirements clarified. |
| REV | 210.70 | Battery-powered control devices addressed; lighting outlets now required in laundry areas; exterior illumination via indoor lighting not allowed; bulkhead doors addressed; stairway dimmer requirements clarified. |
| REV | 215.15 | Barriers over conductor terminals/busbars now required for feeder taps and transformer secondaries. |
| NEW | 215.18 | Surge protection now required for several occupancies. |
| REV | 220.1 | Article 220 reorganized for usability; scope revised. |
| REV | 220.5 | Garages must now be included in dwelling load calculations. |
| REV | 220.42 | Lighting loads for schools and sports arenas reduced; Table Note clarified. |
| REV | 220.53 | 75% demand factor for dwelling appliances no longer includes EVSE. |
| NEW | 220.57 | New section for Electric Vehicle Supply Equipment (EVSE) load calculations. |
| REV | 220.60 | Noncoincident load allowances clarified. |
| NEW | 220.70 | New allowances for Energy Management Systems (EMSs). |
| NEW | 220.110 | New section for receptacle loads in patient care spaces. |
| REV | 225.27 | Raceway seal requirements clarified. |
| NEW | 225.41 | Emergency disconnect now required for dwellings supplied by feeder circuits. |
| NEW | 225.42 | Surge protection now required for several occupancies. |
| REV | 230.7 | Underground boxes and enclosures now addressed. |
| REV | 230.8 | Raceway seal rules revised for consistency. |
| REV | 230.24 | Clearances for service conductors above roofs revised for consistency. |
| REV | 230.30 | Type TC-ER now allowed under certain conditions. |
| REV | 230.43 | TC-ER cable requirements expanded; flexible bus systems now allowed. |
| REV | 230.62 | Requirements for covering energized terminals in service equipment clarified. |
| NEW | 230.67 | Surge protection now required for several occupancies. |
| REV | 230.71 | Metering centers, transfer switches, and motor control centers clarified; existing equipment addressed. |
| REV | 230.75 | Marking requirements for multi-section switchboards/switchgear returned. |
| REV | 230.85 | Dwelling unit emergency disconnect requirements expanded and clarified. |
| NEW | Art. 235 | New article: Branch Circuits, Feeders, and Services Over 1,000V ac or 1,500V dc. |
| REV | 240.4 | Adjustable trip breakers addressed; copper-clad aluminum allowances added; dwelling feeders/services now included. |
| REV | 240.6 | 10A circuit breakers now standard; remotely adjusted breakers addressed. |
| NEW | 240.7 | Listing requirements for overcurrent and protective devices added. |
| NEW | 240.11 | General requirements for selective coordination added. |
| REV | 240.16 | Interrupting rating requirement for branch circuit OCPDs relocated here. |
| REV | 240.24 | Tool usage exception expanded; OCPDs not permitted in bathrooms of dwelling units, dormitories, or guest rooms/guest suites (dormitories added in 2023). |
| REV | 240.60 | Fuseholders must now be listed. |
| REV | 240.89 | Replacement trip units must now be listed. |
| REV | 242.2 | Reconditioned equipment now addressed. |
| NEW | 242.9 | Status indication now required for SPDs. |
| NEW | Art. 245 | New article: Overcurrent Protection for Systems Over 1,000V ac or 1,500V dc. |
| REV | 250.6 | Types of currents not considered objectionable clarified. |
| REV | 250.36 | Impedance grounded systems revised for accuracy. |
| REV | 250.64 | Editorial revisions; ventilation openings now addressed. |
| REV | 250.70 | Editorially revised; informational note added. |
| REV | 250.100 | Bonding in hazardous locations revised for accuracy. |
| REV | 250.109 | Metal enclosure fault current path allowance revised for accuracy. |
| REV | 250.114 | Icemakers must now be connected to an equipment grounding conductor. |
| REV | 250.118 | Stainless-steel FMC and liquidtight FMC now addressed. |
| REV | 250.130 | Replacement snap switches now addressed. |
| REV | 250.140 | Allowances for existing dryer and range connections expanded. |
| REV | 250.148 | Rules for bonding metal boxes clarified. |

🔧 CHAPTER 3 — WIRING METHODS & MATERIALS (Art. 300–398)

| REV | 300.4 | RTRC conduit protection relaxed; metal-corrugated roof decking rules clarified; protective fittings installation revised. |
| --- | --- | --- |
| REV | 300.5 | EMT cover (burial depth) requirements added in Column 3; warning ribbon requirements expanded. |
| REV | 300.6 | Corrosion protection requirements for enclosures clarified. |
| REV | 300.11 | Class 3 cable may now be secured to raceways in some instances. |
| REV | 300.14 | 6" free conductor rule clarified. |
| REV | 300.15 | Wiring method transitions now addressed. |
| REV | 300.17 | Cables now included in raceway fill section. |
| REV | 300.25 | Exception added for egress lighting at stair enclosures. |
| NEW | 300.26 | New section clarifying applicability of Article 300 to remote-control and signaling circuits. |
| NEW | Art. 305 | New article: General wiring method requirements for medium voltage systems. |
| REV | 310.3 | Specific requirements for copper-clad aluminum added. |
| REV | 310.10 | Parallel conductor requirements editorially revised. |
| REV | 310.15 | Rooftop temperature correction requirement slightly reduced. |
| REV | 312.8 | Wire bending space now addressed. |
| REV | 312.10 | Potential damage from screws and other fasteners now addressed. |
| REV | 312.102 | Cabinets, cutout boxes, and meter socket enclosures must now have a door or cover. |
| REV | 314.5 | Fasteners entering enclosures now addressed. |
| REV | 314.16 | Terminal blocks in enclosures now addressed. |
| REV | 314.17 | Revised for accuracy regarding conductors/cables entering boxes. |
| REV | 314.23 | Cord pendant-supported box requirements revised. |
| REV | 314.24 | Boxes with cables entering through back or sides now have specific size requirements. |
| REV | 314.25 | Conduit bodies must now have a cover, lampholder, or device. |
| REV | 314.27 | Box requirements for ceiling fans/weight-supporting ceiling receptacles clarified. |
| REV | 320.23 | Cable protection requirements in attics revised for accuracy. |
| REV | 334.10 | NM cable allowances clarified and expanded. |
| REV | 334.15 | Protective bushing requirement expanded. |
| NEW | 334.19 | Requirements for cables entering enclosures added. |
| REV | 334.24 | Bending radius requirements for flat cables clarified. Similar changes in Art. 338 (SE) and 340 (UF). |
| REV | 334.40 | Restrictions for splicing NM cable without a box lessened. |
| REV | 336.10 | Some tray cables may now be used for service conductors. |
| REV | 342.20 | Larger IMC now allowed. |
| REV | 342.30 | Securing raceways inside finished walls of existing buildings no longer required. Similar for Art. 344 (RMC). |
| REV | 348.2 | Reconditioning of FMC now addressed. Similar changes for other flexible raceways. |
| REV | 352.10 | Concrete encasement and physical damage more clearly addressed. |
| REV | 352.44 | Earth movement now included. |
| REV | 356.10 | Corrosive environments now addressed for LFNC. |
| REV | 358.10 | Fittings for directly buried EMT addressed; manufactured wiring systems addressed. |
| REV | 358.20 | Maximum allowable size for EMT increased. |
| REV | 362.10 | Allowable uses of ENT clarified. |
| NEW | Art. 369 | New article: Insulated Bus Pipe (IBP) / Tubular Covered Conductors (TCC). |
| NEW | Art. 371 | New article: Flexible Bus Systems. |
| REV | 376.60 | Requirements for metal wireways used as EGCs added. |

⚙️ CHAPTER 4 — EQUIPMENT FOR GENERAL USE (Art. 400–490)

| REV | 404.1 | Switch scope clarified. |
| --- | --- | --- |
| REV | 404.2 | Neutral conductor requirement at switch locations increased. |
| REV | 404.14 | Push-in connections addressed; dimmer switch requirements revised. |
| REV | 404.16 | Reconditioned equipment addressed. |
| NEW | 404.30 | Additional safety requirements for switch enclosures with doors added. |
| REV | 406.2 | Reconditioning now addressed for receptacles. |
| REV | 406.3 | Push-in connections and copper-clad aluminum conductors addressed. |
| REV | 406.4 | Replacement CO/ALR receptacles addressed; some floor receptacles may require GFCI protection. |
| REV | 406.6 | Restrictions on faceplates with night lights or USB chargers added. |
| REV | 406.9 | Receptacles/covers in damp or wet locations extensively revised; tub/shower requirements clarified. |
| REV | 406.12 | Tamper-resistant receptacle requirements clarified and expanded. |
| REV | 408.4 | Circuit directory requirements expanded and clarified. |
| REV | 408.9 | Enclosures for replacement panelboards now addressed. |
| REV | 408.38 | Available fault current must be considered when selecting panelboard enclosures. |
| REV | 408.43 | Panelboards no longer allowed to be installed facing downward. |
| REV | 410.71 | Disconnecting means requirements for fluorescent luminaires now apply to LED luminaires. |
| REV | 410.184 | GFCI requirements for horticultural lighting >150V to ground revised. |
| NEW | 410 Pt XVII | New Part XVII (410.190–410.197) for germicidal irradiation luminaires. |
| REV | 422.16 | Trash compactor cord requirements revised for consistency with dishwasher cords. |
| REV | 422.18 | Ceiling fan requirements revised for accuracy. |
| NEW | 424.48 | New section: heating cables in walls — identified as suitable, GFCI and AFCI protected, grounding means required, max 4 ft above floor; effective Jan. 1, 2026. Similar changes in 424.93 for heating panels. |
| REV | 426.28 | GFPE trip setting now addressed. |
| REV | 430.2 | Reconditioned motors now addressed. |
| REV | 440.8 | A/C and refrigeration equipment in bathrooms — new restrictions. |
| REV | 440.11 | Exposed live parts in disconnecting means addressed. |
| REV | 440.14 | Clearance requirements for disconnecting means added. |
| REV | 445.6 | Listing requirements for stationary generators increased. |
| REV | 445.18 | Generator disconnecting means requirements clarified. |
| NEW | 445.19 | Signage requirements for generator emergency shutdown device added. |
| REV | 450.2 | "Transformer" definition removed and turned into enforceable text. |
| REV | 480.1 | Article title and scope revised for accuracy (Stationary Standby Batteries). |

🏭 CHAPTER 5 — SPECIFIC OCCUPANCIES & LOCATIONS (Art. 500+)

| REV | 500.5 | Class III area classifications clarified. |
| --- | --- | --- |
| NEW | 500.7 | New protection techniques added (P through T) and helpful table added. |
| REV | 500.8 | Operating temperatures in Class III locations addressed; laser/optical fiber requirements clarified. |
| REV | 501.10 | Coated RMC and IMC now specifically addressed. |
| REV | 501.30 | Grounding and bonding clarified. Similar changes in Art. 502 and 503. |
| REV | 502.10 | Coated RMC and IMC addressed; EMT fittings must be compression type. |
| REV | 502.15 | Electrical sealing putty now allowed. |
| REV | 503.10 | Type P cable now allowed in Class III locations. |
| NEW | Art. 512 | New article: Cannabis Oil Equipment and Systems Using Flammable Materials. |
| REV | 517.10 | New informational notes added; pharmacies now addressed. |
| REV | 517.70 | Part V of Article 517 no longer limited to X-ray equipment. |
| REV | 547.26 | Nonmetallic cables no longer allowed in most concealed locations. |
| REV | 555.4 | Additional clearance requirements for service equipment added. |
| REV | 555.13 | Bonding requirements relaxed. |
| NEW | 555.14 | New requirements for equipotential bonding added. |
| REV | 555.15 | Replacement equipment now addressed. |
| REV | 555.35 | GFPE and GFCI requirements clarified and expanded. |
| NEW | 555.36 | New requirement for emergency disconnect for shore power. |
| NEW | 555.38 | New section for luminaires at marinas. |
| REV | 590.8 | Current-limiting OCPD requirement at service reduced for temporary wiring. |

🔋 CHAPTER 6 — SPECIFIC EQUIPMENT (Art. 600–695)

| REV | 604.100 | New options for raceway types in manufactured wiring systems. |
| --- | --- | --- |
| REV | 625.40 | EVSE circuiting requirements lessened. |
| REV | 625.42 | Energy management systems now allowed for reducing load requirements. |
| REV | 625.43 | Marking requirements for remote disconnecting means added. |
| REV | 680.5 | GFCI and SPGFCI protection requirements made clearer. |
| REV | 680.10 | Heating equipment without resistance elements now addressed. |
| REV | 680.11 | Underground wiring near pools must now be installed as a complete system. |
| REV | 680.14 | Equipment in corrosive environments more clearly addressed. |
| REV | 680.21 | Repaired motors now require GFCI or SPGFCI protection. |
| REV | 680.26 | Perimeter bonding conductor/grid location clarified. |
| REV | 680.41 | Equipment near spa, hot tub, or immersion pool now addressed. |
| REV | 680.50 | Equipment near fountains now addressed. |
| REV | 680.54 | Equipotential bonding of splash pads clarified. |
| REV | 690.4 | Floating structures with PV arrays now addressed. |
| REV | 690.12 | Exceptions for rapid shutdown requirements added. |
| REV | 695.1 | Fire pump article applicability clarified. |
| REV | 695.6 | Cable/raceway fittings must now be listed for wet locations. |
| REV | 695.7 | Voltage drop requirements revised to reflect NFPA 20® requirements. |
| NEW | 695.15 | Surge protection now required for fire pump controllers; exception added for diesel fire pumps. |

🚨 CHAPTER 7 — SPECIFIC CONDITIONS & SYSTEMS (Art. 700–760)

| REV | 700.3 | AHJ must now perform/witness commissioning; temporary source connection requirements expanded. |
| --- | --- | --- |
| REV | 700.4 | Parallel operation of sources addressed; load requirements clarified. |
| NEW | 700.5 | New requirement for redundant transfer equipment. |
| NEW | 700.11 | New section for emergency systems supplied by Class 2 circuits. |
| REV | 700.24 | Directly controlled emergency luminaire listing requirements clarified. |
| NEW | 700.27 | PoE switches and similar must now be listed for emergency use. |
| REV | 700.32 | Selective coordination for replacements and modifications addressed. |
| REV | 702.7 | Signage requirement for locations of other sources expanded. |
| REV | 705.11 | Connection to a service requirements clarified and simplified. |
| NEW | 706.15(E) | New battery disconnecting means requirements: disconnect within sight, series battery isolation, remote activation, and notification/marking requirements. |
| NEW | 708.7 | New cybersecurity requirements added for critical operations. |
| NEW | Art. 722 | New article: Cables for Power-Limited Circuits and Fault-Managed Power Circuits. |
| NEW | Art. 724 | New article: Class 1 Power-Limited Circuits (scope per 724.1 includes Class 1 power-limited remote-control and signaling circuits). |
| NEW | Art. 726 | New article: Class 4 Fault-Managed Power Systems. |
| NEW | 750.6 | Listing requirements for energy management systems added. |
| NEW | 750.30 | New requirements for EMS systems that limit loads. |
| NEW | 760.33 | Surge protection now required for fire alarm control panels. |

📡 CHAPTER 8 — COMMUNICATIONS (Art. 800+)

| REV | 810.1 | Article title changed to match its scope (Antenna Systems). |
| --- | --- | --- |