ANALYSIS OF CHANGES 2026 National Electrical Code® Comprehensive Quick-Reference Handout • Chapters 1–9 & Annexes

⚡ GLOBAL CHANGES & STRUCTURAL UPDATES

PREPARING FOR 2029 NEC® REFORMATTING The NEC® format has remained unchanged since 1937. Structural changes in the 2026 cycle lay the groundwork for a comprehensive reorganization in 2029. The proposed 2029 structure is located in Annex L of the 2026 NEC®.

NEW ARTICLES

| NEW | Art. 206 | Non-Power-Limited Remote-Control and Signaling Circuits [from 300.26] |
| --- | --- | --- |
| NEW | Art. 265 | Branch Circuits Over 1000V ac, 1500V dc [from deleted Art. 235] |
| NEW | Art. 266 | Feeders Over 1000V ac, 1500V dc [from deleted Art. 235] |
| NEW | Art. 267 | Outside BCs & Feeders Over 1000V ac, 1500V dc [from Art. 235 & 395] |
| NEW | Art. 268 | Services Over 1000V ac, 1500V dc [from deleted Art. 235] |
| NEW | Art. 270 | Grounding & Bonding of Systems Over 1000V ac, 1500V dc [from Art. 250 Pt X] |
| NEW | Art. 624 | Electric Self-Propelled Vehicle Power Transfer Systems (ESVSEs) |
| NEW | Art. 720 | General Requirements for Limited-Energy Systems Wiring Methods & Materials |
| NEW | Art. 721 | Power Sources for Limited-Energy Systems |
| NEW | Art. 722 | Limited-Energy Cables for Power-Limited, FMP, Optical Fiber & Comms Circuits |
| NEW | Art. 723 | Raceways, Cable Routing Assemblies & Cable Trays for Limited-Energy Systems |
| NEW | Art. 742 | Overvoltage Protection of Limited-Energy Systems |
| NEW | Art. 750 | Grounding and Bonding of Limited-Energy Systems |

RELOCATED ARTICLES

| MOVED | Art. 120 | Branch-Circuit, Feeder & Service Load Calculations [was Art. 220] |
| --- | --- | --- |
| MOVED | Art. 130 | Energy Management Systems [was Art. 750] |
| MOVED | Art. 772 | Fire Resistive Cable Systems [was Art. 728] |

DELETED ARTICLES

| DEL | Art. 235 | Contents relocated to new Art. 265, 266, 267, and 268 |
| --- | --- | --- |
| DEL | Art. 395 | Overhead Conductors Over 1,000V — relocated |
| DEL | Art. 770 | Optical Fiber Cables — relocated to Art. 722, Part VII |
| DEL | Art. 805 | Communications Circuits — relocated to Art. 722, 742, and 750 |
| DEL | Art. 840 | Premises-Powered Broadband — requirements covered elsewhere |

📖 CHAPTER 1 — GENERAL (Art. 90 & 100)

| REV | 90.2 | Scope differentiated: 90.1 = article scope, 90.2 = document scope. Special permission language deleted (covered in 90.4(C)). |
| --- | --- | --- |
| REV | 90.3 | Chapter 8 no longer independent from Ch. 1–7. Chapter titles updated (Ch. 5: Specific Occupancies, Ch. 6: Specific Equipment, Ch. 7: Specific Conditions, Ch. 8: Comms—Outside & Entering Buildings). |
| REV | Art. 100 | "Readily Accessible" definition clarified — reached quickly without using tools (other than a key), without climbing over or under barriers, without removing obstacles, or without using portable ladders. |
| NEW | Art. 100 | "Cable Tie" and "Cable Tie Fixing Device" definitions added; support method per 300.13(E). |
| REV | Art. 100 | "Energy Management System" revised — must control power, not just monitor. |
| NEW | Art. 100 | "Line-to-Ground" — new term applicable to both ac and dc systems. Excludes neutral conductor. |
| REV | Art. 100 | "OCPD" — streamlined definition; acronym may be used throughout the code. Types listed in 240.7. |
| NEW | xxx.2 / xxx.3 | Listing requirements consolidated to xxx.2; reconditioned equipment requirements to xxx.3 per NEC Style Manual 2.2.1. |

🔌 CHAPTER 2 — WIRING & PROTECTION (Art. 200–270)

| REV | 200.7(A) | Renumbered (was 200.6). New list item 9: single stripe (not green) permitted for grounded conductor identification. |
| --- | --- | --- |
| NEW | Art. 206 | Non-Power-Limited Remote-Control and Signaling Circuits — new article created from former 300.26. |
| REV | 210.8(A) | Dwelling GFCI: garages separated (item 2); accessory buildings expanded regardless of grade (item 3); indoor damp/wet locations added (items 13-14); exhaust fan exception broadened. |
| REV | 210.8(B) | Other than dwellings: indoor damp (item 8) and wet (item 9) locations separated; open aquatic vessels added (item 14); industrial exception rewritten for outdoor equipment. |
| REV | 210.8(F) | Outdoor outlets: amperage threshold increased 50A → 60A (single-phase, 150V-to-ground or less). Class C SPGFCI permitted for listed HVAC equipment. Disconnect must be marked with warning that Class C SPGFCI protection is provided. |
| NEW | Art. 100 GFCI | Class A GFCI: trips at ≥6 mA. New Class C, D, E Special-Purpose GFCI (SPGFCI) definitions added. Evaluated to UL 943C. |
| REV | 210.12(B) | AFCI: sunset date removed for arc welding exception; scope expanded to garages and accessory buildings. |
| REV | Countertop | Definition revised to include beverage preparation/serving. "Work Surface" revised to exclude beverage functions. |
| REV | Art. 250 | Part X (over 1000V grounding/bonding) relocated to new Art. 270. |

🔧 CHAPTER 3 — WIRING METHODS & MATERIALS (Art. 300–398)

| REV | 300.1 | Scope revised for clarity. |
| --- | --- | --- |
| NEW | 300.4(C) | Damaged conductors and wiring methods — new limitations added. |
| REV | 300.6(E) | Protection against physical damage for wiring under roof decking. |
| REV | 300.7(D)(3) | Underground installations: protection from damage requirements revised. |
| REV | 300.9(A) | Raceways exposed to different temperatures: condensation requirements revised. |
| NEW | 300.11(B) | Raceways in indoor wet locations above grade: new drainage requirements. |
| NEW | 300.13(E) | Securing and supporting: cable ties and cable tie fixing devices must be listed and identified for securement and support per new Art. 100 definitions. |
| NEW | 300.24 | New section addressing bends in wiring methods. |
| REV | 310.5(A) | Minimum conductor size requirements revised. |
| REV | 310.15(E) | Neutral conductor ampacity requirements revised. |
| REV | T310.16/.17 | Type XHWN removed from 90°C column (rated 75°C only); 16 AWG Cu and 14 AWG Cu-clad Al added to tables. |
| NEW | 312.3/315.3 | Reconditioned equipment requirements added for cabinets and MV cables. |
| NEW | 314.2 | Listing requirements added for boxes and conduit bodies. |
| REV | 314.16(B) | Box fill: splicing connectors (wire nuts, etc.) added to items NOT counted in box fill calculations. |

⚙️ CHAPTER 4 — EQUIPMENT FOR GENERAL USE (Art. 400–490)

| REV | 404.1 | Switch scope revised. |
| --- | --- | --- |
| REV | 404.10(A) | Accessibility and grouping of switch locations revised. |
| REV | 406.12(D)(3) | Receptacle replacements: GFCI protection requirements revised. |
| REV | 406.14(G) | Receptacle mounting orientation requirements revised. |
| REV | 406.26 | Tamper-resistant receptacle requirements revised. |
| REV | 408.6 | Short-circuit current rating requirements for switchboards/panelboards. |
| REV | 410.184 | GFCI/SPGFCI protection added for horticultural lighting equipment. |
| REV | 422.12 | Central heating equipment requirements revised. |
| REV | 422.13 | Storage-type water heater requirements revised. |
| NEW | 426.2 | Listing requirements added for fixed outdoor deicing/snow-melting equipment. |
| NEW | Art. 430 | New requirements for Design BE and CE energy-efficient motors (higher locked rotor currents). New 430.22(H) locked rotor current calculations; new Table 430.251(C). |
| REV | 430.3 | Reconditioned equipment requirements for motors revised. |

🏭 CHAPTER 5 — SPECIFIC OCCUPANCIES & LOCATIONS (Art. 500+)

| REV | 500.5(D) | Class III, Division 1 classification revised. |
| --- | --- | --- |
| REV | 500.8(G) | Equipment involving optical radiation in hazardous locations. |
| NEW | 501.3(A) | Reconditioned equipment: permitted types for Class I locations. |
| REV | 501.10 | Wiring methods for Class I, Div. 1 and Div. 2 locations revised. |
| REV | 501.130(C) | Luminaire retrofit kits for hazardous locations. |
| REV | 511.5(C) | Repair garages: major vs. minor classification revised. |
| REV | 511.10(B) | EV Power Transfer Systems in repair garages. |
| NEW | 512.6 | Prohibited locations for cannabis oil extraction equipment (assembly, educational, health care, residential, etc.). |

🔋 CHAPTER 6 — SPECIFIC EQUIPMENT (Art. 600–695)

| DEL | 600.4 | Sign markings requirements deleted. |
| --- | --- | --- |
| REV | 604.100 | Manufactured wiring systems construction revised. |
| DEL | 620.7(C) | Elevator sump pump GFCI requirements deleted. |
| NEW | 620.16(C) | Available fault current field marking required for elevator control panels (relocated from 620.51(D)). |
| NEW | 620.51(A) | Elevator disconnecting means: new Exception No. 3. |
| NEW | 620.62(B)(C) | Selective coordination for elevator replacements and modifications. |
| NEW | Art. 624 | Electric Self-Propelled Vehicle Power Transfer Systems (ESVSEs) — entirely new article. |

🚨 CHAPTER 7 — SPECIFIC CONDITIONS & SYSTEMS (Art. 700–760)

| REV | 700.4(D) | Emergency system record keeping requirements revised. |
| --- | --- | --- |
| REV | 700.4(F) | Temporary source of power for single alternate source systems. |
| REV | 700.6(C) | Bypass and isolation of transfer equipment. |
| REV | 700.10(D) | Emergency feeder-circuit wiring: concrete encasement minimum increased from 2 in. to 5 in.; 2 in. still permitted with documented 2-hour fire rating by a licensed PE. |
| REV | 700.12(F) | Microgrid systems for emergency power revised. |
| REV | 700.24 | Luminaires with control inputs for emergency illumination. |
| NEW | 700.28 | Class 4 powered emergency lighting systems — new section. |
| REV | 700.32 | Selective coordination for replacements (B) and modifications (C) revised. |

📡 CHAPTERS 7–8 — LIMITED-ENERGY & COMMUNICATIONS

MAJOR CHANGE: Chapter 8 Independence Removed Ch. 7 (Art. 720–760) now provides main installation requirements for ALL Limited-Energy Systems, including Communications. Redundancies between Ch. 7 & 8 eliminated. 2029 edition will finalize remaining cleanup.

| REV | Art. 800 | Significantly reduced — requirements moved to Ch. 7 limited-energy articles. |
| --- | --- | --- |
| REV | 800.24(A) | “Neat and workmanlike” changed to “professional and skillful” to align with 110.12. |
| DEL | 810/820/830 | Grounding sections relocated to new Art. 750. Installation methods moved to Art. 722. |
| DEL | Art. 805/840 | Deleted — requirements now in Art. 722, 742, and 750. |

📊 CHAPTER 9 & ANNEXES

| REV | Table 1 | Conduit/tubing fill percentages for conductors and cables revised. |
| --- | --- | --- |
| REV | Table 13 | Equipment suitable for hazardous (classified) locations revised. |
| DEL | Annex J | ADA Standards removed; notes now cite ANSI/ICC A117.1-2017. Annex retained for future use. |
| NEW | Annex L | Proposed 2029 NEC® structure located here. |