**2019 ANNUAL DRINKING WATER QUALITY REPORT**

**PWSID #: 6240007 NAME: johnsonburg municipal authority**

*Este informe contiene información importante acerca de su agua potable. Haga que alguien lo traduzca para usted, ó hable con alguien que lo entienda.* (This report contains important information about your drinking water. Have someone translate it for you, or speak with someone who understands it.)

***WATER SYSTEM INFORMATION:***

This report shows our water quality and what it means. If you have any questions about this report or concerning your water utility, please contact our office at (814) 965 – 4218 .We want you to be informed about your water supply. If you want to learn more, please attend any of our regularly scheduled meetings. They are held on the third Tuesday of each month at 6:00 PM, at the Johnsonburg Municipal Authority Office, located at 601 Market Street, Johnsonburg, PA 15845.

***SOURCE(S) OF WATER:***

Our water source(s) are:

|  |
| --- |
| Source ID 001 Silver Creek Reservoir, being a Surface Water Source  Source ID 002 Powers Run Reservoir, being a Surface Water Source |

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the *Safe Drinking Water Hotline* (800-426-4791).

***Monitoring Your Water:***

We routinely monitor for contaminants in your drinking water according to federal and state laws. The following tables show the results of our monitoring for the period of January 1 to December 31, 2019. The State allows us to monitor for some contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of our data is from prior years in accordance with the Safe Drinking Water Act. The date has been noted on the sampling results table.

***DEFINITIONS:***

*Action Level (AL)* **-** The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

*Maximum Contaminant Level (MCL)* - The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

*Maximum Contaminant Level Goal (MCLG)* - The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

*Maximum Residual Disinfectant Level (MRDL)* - The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

*Maximum Residual Disinfectant Level Goal (MRDLG)* - The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

*Minimum Residual Disinfectant Level* *(MinRDL) -* The minimum level of residual disinfectant required at the entry point to the distribution system.

*Level 1 Assessment –* A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.

*Level 2 Assessment –* A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an *E. coli* MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.

*Treatment Technique (TT)**-* A required process intended to reduce the level of a contaminant in drinking water.

*Mrem/year**=* millirems per year (a measure of radiation absorbed by the body)

*pCi/L**=* picocuries per liter (a measure of radioactivity)

*ppb*= parts per billion, or micrograms per liter (μg/L)

*ppm*= parts per million, or milligrams per liter (mg/L)

*ppq*= parts per quadrillion, or picograms per liter

*ppt*= parts per trillion, or nanograms per liter

***DETECTED SAMPLE RESULTS:***

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ***Chemical Contaminants*** | | | | | | | | |
| **Contaminant** | **MCL in CCR Units** | **MCLG** | **Level Detected** | **Range of Detections** | **Units** | **Sample Date** | **Violation Y/N** | **Sources of Contamination** |
| Chlorine | 4 | 4 | 0.64 | 0.04-1.40 | ppm | 2019 | N | Water Additive used to control microbes |
| Trihalomethanes (TTHM) | 80 | NA | 51 | 9-105 | ppb | 2019 | Y | By-Product of drinking water chlorination |
| Haloacetic Acids Five (HAA5) | 60 | NA | 153 | 10-1100 | ppb | 2019 | Y | By-Product of drinking water chlorination |
| Barium | 2 | 2 | 0.058 | 0.0164 – 0.0785 | ppm | 9/17/2019 | N | Discharge of drilling wastes; Discharge from metal refineries; Erosion of natural deposits |

\*EPA’s MCL for fluoride is 4 ppm. However, Pennsylvania has set a lower MCL to better protect human health.

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ***Entry Point Disinfectant Residual*** | | | | | | | |
| **Contaminant** | **Minimum Disinfectant**  **Residual** | **Lowest**  **Level Detected** | **Range of Detections** | **Units** | **Sample Date** | **Violation Y/N** | **Sources of Contamination** |
| **Chlorine**  Powers Run (116)  Silver Creek (115) | 0.2 | 0.50  0.30 | 0.50-1.17  0.30-1.16 | ppm | 2019 | N | Water additive used to control microbes. |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ***Lead and Copper*** | | | | | | | |
| **Contaminant** | **Action Level (AL)** | **MCLG** | **90th Percentile Value** | **Units** | **# of Sites Above AL of Total Sites** | **Violation Y/N** | **Sources of**  **Contamination** |
| Lead | 15 | 0 | 0.204 | ppm | 0 | N | Corrosion of household plumbing. |
| Copper | 1.3 | 1.3 | 0 | ppm | 0 | N | Corrosion of household plumbing. |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ***Microbial (related to Assessments/Corrective Actions regarding TC positive results)*** | | | | | |
| **Contaminants** | **TT** | **MCLG** | **Assessments/**  **Corrective Actions** | **Violation**  **Y/N** | **Sources of Contamination** |
| Total Coliform  Bacteria | Any system that has failed to complete all the required assessments **or** correct all identified sanitary defects, is in violation of the treatment technique requirement | N/A | See detailed description under “Detected Contaminants Health Effects Language and Corrective Actions” section | N | Naturally present in the environment. |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ***Microbial (related to E. coli)*** | | | | | |
| **Contaminants** | **MCL** | **MCLG** | **Positive Sample(s)** | **Violation**  **Y/N** | **Sources of Contamination** |
| *E. coli* | Routine and repeat samples are total coliform-positive **and** either is *E. coli*-positive **or** system fails to take repeat samples following *E. coli-*positive routine sample **or** system fails to analyze total coliform-positive repeat sample for *E. coli.* | 0 | 0 | N | Human and animal fecal waste. |
| **Contaminants** | **TT** | **MCLG** | **Assessments/**  **Corrective Actions** | **Violation**  **Y/N** | **Sources of Contamination** |
| *E. coli* | Any system that has failed to complete all the required assessments **or** correct all identified sanitary defects, is in violation of the treatment technique requirement | N/A | See description under “Detected Contaminants Health Effects Language and Corrective Actions” section | N | Human and animal fecal waste. |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ***Turbidity*** | | | | | | |
| **Contaminant** | **MCL** | **MCLG** | **Level Detected** | **Sample**  **Date** | **Violation**  **Y/N** | **Source of Contamination** |
| Turbidity | TT=1 NTU for a single measurement | 0 | 14.65 | 11/1/19 | Y | Soil runoff |
| TT= at least 95% of monthly samples<0.3 NTU | 91.8 | 11/2019 | Y |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ***Total Organic Carbon (TOC)*** | | | | | |
| **Contaminant** | **Range of % Removal Required** | **Range of percent removal achieved** | **Number of quarters out of compliance** | **Violation**  **Y/N** | **Sources of Contamination** |
| TOC  300 Powers  301 Silver Crk | 25 - 35% | 0% - 61.17%  0% - 54.34% | 2  3 | Y | Naturally present in the environment |

***DETECTED CONTAMINANTS HEALTH EFFECTS LANGUAGE AND CORRECTIVE ACTIONS:***

|  |
| --- |
| **Turbidity:** Has no health effects. However, turbidity can interfere with disinfection and provide a medium for microbial growth. Turbidity may indicate the presence of disease-causing organisms. These organisms include bacteria, viruses, and parasites that can cause symptoms such as nausea, cramps, diarrhea and associated headaches. *Corrective Action: Authority staff is improving monitoring, undergoing training, and external oversight, system maintenance and construction is underway for a new state-of-the-art water treatment facility to offer enhanced treatment, construction completion estimated 2nd quarter 2021.*  **Total Trihalomethanes (TTHMs):** Some people who drink water containing THMs in excess of the MCL over many years may experience problems with their liver, kidneys, or central nervous system, and may have an increased risk of getting cancer. The distribution system dead end lines, aged water and removal efficiency during treatment results in the reaction with disinfection chemicals and creates associated by-products TTHMs.  *Corrective Action: Authority is working to correct distribution system issues, optimize treatment and construction is underway for a new state-of-the-art water treatment facility to offer enhanced treatment, construction completion estimated 2nd quarter 2021.*  **Haloacetic Acids (HAA):**  Some people who drink water containing HAA in excess of the MCL over many years may have an increased risk of getting cancer. The distribution system dead end lines, aged water and removal efficiency during treatment results in the reaction with disinfection chemicals and creates associated by-products HAAs.  *Corrective Action: Authority is working to correct distribution system issues, optimize treatment and construction is underway for a new state-of-the-art water treatment facility to offer enhanced treatment, construction completion estimated 2nd quarter 2021.*  **Total Organic Carbon:** TOC has no health effects. However, TOC provides medium for the formation of disinfection byproducts. These byproducts include THMs and HAAs. Drinking water containing these byproducts in excess of the MCL may lead to adverse health effects, liver or kidney problems, or nervous system effects, and may lead to an increased risk of getting cancer. Removal efficiencies of the existing treatment facilities are limited. *Corrective Action: Authority is working to correct optimize treatment, and construction is underway for a new state-of-the-art water treatment facility to offer enhanced treatment, construction completion estimated 2nd quarter 2021.* |

***OTHER VIOLATIONS:***

|  |
| --- |
| On October 31 and November 1, the Silver Creek treatment plant experienced an upset in water quality resulting in the inability of the facility to meet effluent turbidity limits, and exceeded treatment technique requirements. The system is undergoing monitoring, external oversight; and a new treatment facility is under construction. *Inadequately treated water may contain disease-causing organisms. These organisms include bacteria, viruses, and parasites which can cause symptoms such as nausea, cramps, diarrhea and associated headaches. A boil water advisory was issued and sampling conducted.*  In addition, the following violations are also noted: samples were taken/reported late for Soluble Organic Chemicals (SOC’s) (1st quarter 2019); Failure to monitor for TOC (7/1/2019); Failure to record turbidity and perform self-assessments (9/19, 10/19, 11/19, 12/19); exceedance of running annual average for HAAs (7/19, 10/19); low chlorine residual in Distribution system (8/19), |

***EDUCATIONAL INFORMATION:***

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water include:

* + Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban stormwater run-off, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
* Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by‑products of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, and septic systems.
* Radioactive contaminants, which can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, EPA and DEP prescribes regulations which limit the amount of certain contaminants in water provided by public water systems. FDA and DEP regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s *Safe Drinking Water Hotline* (800-426-4791).

***Information about Lead***

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Johnsonburg Municipal Authority is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the *Safe Drinking Water Hotline* or at [*http://www.epa.gov/safewater/lead*](http://www.epa.gov/safewater/lead)*.*

***OTHER INFORMATION:***

|  |
| --- |
| **If you want a printed copy, please contact our office at (814) 965 – 4218**  **All future Consumer Confidence Report’s (CCR’s) will be available on our website at:**  [**www.johnsonburgmunicipalauthority.com/ccr**](http://www.johnsonburgmunicipalauthority.com/ccr) |