## Slide 1
ASTM D02 Committee Week
Diesel Corrosion and Micelle Control
SAE J1488 Micelle Filtration

## Slide 2: What We Will Cover
Summary - Why Corrosion and Micelles Now?
Details – micelles, biosurfactants
How SAE J1488 micelle filtration controls corrosion and water
What tests to use, field test results
Long term diesel storage
Home heating diesel storage
Notes: Most generator owners not aware of corrosion risk

## Slide 3: Summary: Why Corrosion Now?
*KEY* water has migrated into the fuel column, water bonds with surfactants to form a bottom layer of micelles
Microbial growth dramatically increases in the bottom micelle layer, MIC greatly increases
Water concentrated in bottom layer in Micelles, no free water

## Slide 4: Summary: Why Corrosion Now?
Traditional water tests cannot detect water “hidden” in micelles
Water “hidden” in micelle, traditional filters cannot touch water to remove it, micelles bypass filters and damage injectors

## Slide 5: Basics: What is a Micelle? 2 D
*KEY* both water and surfactants are polar molecules
Polar Head of Surfactant Bonds to Water
Encapsulates Water
Note water droplet not shown
Notes: Water droplet not shown
2D model
polar head surfactant bonds to water droplet

## Slide 6: What is a Micelle? 3 D
Water droplet encapsulated by surfactant molecules
The fatty acid tail forms a barrier, isolating the water
from filter material, water tests, and fuel
A 3D example of an inverse micelle, a phospholipid molecule
Note water droplet not shown
Micelle small, surfactant molecule approx. 50 atoms
Micelles settles to bottom, concentrate water and surfactants on bottom, reduce lubrication

## Slide 7: Latest CRC Research, July 2021, Micelles
Figure 62. Surfactants – a) schematic of surfactant molecule showing polar head and nonpolar tail; b) schematic of invert-emulsion micelle encapsulating water droplet and nonpolar tails extending into the medium (i.e., fuel); c) schematic of invert emulsion micelles dispersed in fuel; d) photo of 10 mL each fuel and water – left: before shaking; right: 24h after shaking (note stability of invert emulsion).
CRC Project DP-07-16-01, “Identification of Potential Parameters Causing Corrosion of Metallic Components in Diesel Fuel Underground Storage Tanks”: "The results from this 12-week study confirmed that the presence of free-water was essential to corrosion."
Notes: Most important part of study:
Micelles explain: J1488 filtration results and fuel sample results
Molecular weight of ULSD and biodiesel similar, they stay mixed
Micelles settle to bottom, taking water and surfactants
Both water and biodiesel removed from body of fuel, and concentrated towards bottom.
<100 ppm water mid tank, bottoms 3,000 to 3000 ppm, no freestanding water
little biodiesel mid tank? reduced lubricity
Layer greatly increased microbial growth volume

## Slide 8: Microbial Growth Volume Dramatically Increases
Free Standing Water
LSD Before 2006
Microbial growth volume thickness sheet of paper
More microbes, more acids, more corrosion, more biosurfactants . . .
ULSD/Biodiesel
Microbial growth volume up to 6 inches thick, microbes produce acids
Tank
Tank
Notes: Neat diesel not polar.
To give an idea of scale, we have printers at home, a bundle of paper is an inch thick, and holds 200 sheets, times number of inches of the micelle layer

## Slide 9: Biosurfactants
Thanks to Dr. Fred Passman for introducing me to the concept of biosurfactants: “In my experience, microbial production of biosurfactants is the primary cause of invert emulsion formation in fuels.”

## Slide 10: Biosurfactants
From page 2: “In situ Linkage of Fungal and Bacterial Proliferation to Microbiologically Influenced Corrosion in B20 Biodiesel Storage Tanks”
“copious amounts of fatty acids are produced as bi-products of
the metabolism of FAME by microorganisms”
Fatty acids are biosurfactants

## Slide 11: Corrosion Mechanism: Detail
B5 produced by blending dry 100% ULSD with dry 100% biodiesel
B5 absorbs water from the atmosphere, creates the initial micelle layer
Microbial growth greatly increases, microbes produce acids and biosurfactants, which form more micelles with newly absorbed water, increasing the micelle layer, which produce more biosurfactants and more acids …….
Notes: My understanding is the blending of neat ULSD and biodiesel create the initial micelle bottom layer (invert emulsion) which then becomes populated with microbes, which create biosurfactants, and hence create more micelles increasing the layer thickness

## Slide 12: Lab Tests for Micelles and Corrosion
ASTM D664 (TAN ) – Total Acid Number – .08 limit
ASTM D6304 Karl Fisher (KF): Traditional water tests cannot detect water in micelles
ISO 4406 Particulate: also indicates microbial growth
Visual: look for hazy fuel, visible water, particulate, corrosion
Notes: In addition to corroding the diesel infrastructure:

## Slide 13: Corrosion Control: SAE J1488 Micelle Filtration
One industry has addressed micelle removal: the diesel industry filtration test for biodiesel blends, J1488
Updated in 2010 to address difficulty in filtering water encased in surfactants
*KEY* Filtering of Micelles 200 ppm Water Controls Microbial Growth and Corrosion

## Slide 14: Corrosion Control: SAE J1488 Micelle Filtration
  200 ppm is also the water warranty limit for generator manufacturers, OEM’s want fuel sample with warranty claims, now denying claims
  Similarly, Injector manufacturers have stringent rules for fuel quality for injector warranty
  Note J1488 filtration removes water, surfactants are returned to tank

## Slide 15: Field Results – SAE J1488 Filtration
J1488 Field Results
Over 10+ Years
All of my installed J1488 filtration sites are below limits for water, TAN, and particulates
Non J1488 filtered tanks all have excessive levels
J1488 filtration effective at controlling corrosion and micelle numbers
Notes: I have taken fuel samples over 10 years, both J1488 filtered fuel, and non filtered fuel

## Slide 16: SAE J1488 Test Procedure
J1488 two phase test:
1st phase uses pure diesel, tests free water filtration
2nd phase uses B20 equivalent ~IFT 17: tests micelle filtration
2500 ppm water added to each test phase

## Slide 17: SAE J1488 Test Procedure
Results:
1st phase – free water: all filters very efficient ~ 100 %
2nd phase – micelles: – filter cannot contact water encapsulated in micelle, low efficiency
Need a 92% filtration efficiency to keep water < 200 ppm: 2500 * ( 1 - .92 ) = 200
< 200 ppm water controls microbial growth, and MIC, vast majority of micelles removed

## Slide 18: SAE J1488 and Diesel Corrosion Control
SAE J1488 micelle filtration
is the key technology to enhance the safe use of diesel by removing micelles formed by biosurfactants
In addition to corroding the diesel
infrastructure, the public is at risk:

## Slide 19
Corrosion, Threat to Emergency Generators, Engines
Acidified fuel corrodes injectors, the
micron sized needles and orifice; all metal
components – valves, pistons
Single injector failure stops engine
Generator software hunts for power range for
injectors, if outside specs, shuts generator down
Emissions increase, spray patterns affected
Injector orifice/needle tips micron size
Notes: 60% of major outages now costing more than $100,000
Over 75% of IT leaders experienced an outage in the last 36 months, and 20% of those outages were ranked “severe”
Over 75% of survey respondents reported that their most recent outage could have been prevented with better practices and procedures in place – up 25% from 2019

## Slide 20
Micelles Bypass Filters, Damage Injectors
35,000+ psi, designs for 60,000+ psi
Damage to injector needle and orifice by pitting and steam explosions
Emissions increase, spray patterns affected
Power reduced, water dilutes fuel
Notes: 60% of major outages now costing more than $100,000
Over 75% of IT leaders experienced an outage in the last 36 months, and 20% of those outages were ranked “severe”
Over 75% of survey respondents reported that their most recent outage could have been prevented with better practices and procedures in place – up 25% from 2019

## Slide 21
Micelles Bypass Filters, Damage Engine
Reduced lubricity, surfactants provide lubrication, concentrated in micelle bottom layer, bulk of fuel low lubrication, friction damage to injectors, pistons, all moving parts
Notes: 60% of major outages now costing more than $100,000
Over 75% of IT leaders experienced an outage in the last 36 months, and 20% of those outages were ranked “severe”
Over 75% of survey respondents reported that their most recent outage could have been prevented with better practices and procedures in place – up 25% from 2019

## Slide 22
Corrosion, Threat to Home Heating Storage
Tens of thousands of thin walled 275 gallon tanks installed
Acidified fuel corrodes tanks, piping, injectors in furnaces & boilers
Increased risk of environmental
contamination
Emissions increase
Notes: Farm house tank failed, insurance company spent $500,000. jacking up the house and remediating the soil

## Slide 23: Relevant Research Papers
CRC Project DP-07-16-01 2021
“Identification of Potential Parameters Causing Corrosion of Metallic Components in Diesel Fuel Underground Storage Tanks”
USAF, U of Oklahoma, B20 year long study, 2020
“In situ Linkage of Fungal and Bacterial Proliferation to Microbiologically Influenced Corrosion”
EPA 2016 “Investigation Of Corrosion-Influencing Factors In Underground Storage Tanks With Diesel Service”
Battelle Report 2012 Corrosion in Systems Storing and Dispensing Ultra Low Sulfur Diesel (ULSD), Hypotheses Investigation
Moisture Absorption In Biodiesel And Its PetroDiesel Blends 2007
15 – 25 X pure diesel, 1,000 – 1,700 ppm, hits saturation in a day

## Slide 24: About Pat Smyth: Speaker
Sept 2022 SAE Test Standards Committee, Member
June 2022 ASTM Working Group on Diesel Corrosion, Member
Sept 2018 National Tanks Conference Louisville Ky
November 2018 National Association Corrosion Engineers (NACE) Washington DC
Sept 2016 EPA Washington DC, Office of Underground Storage Tanks
Lecturer in BioFuelNet Canada’s Advanced Biofuels Course, hosted on McGill University’s myCourses platform