## Sheet1
| GUALALA COMMUNITY SERVICES DISTRICT | [22 empty] | ORDER # 92-120
|  |  | 2019 |  |  | Year Annual Report
Total Flows
| Influent | Influent | SRGL | Coliform | Inf. BOD | EFF. BOD | Inf. TSS | Eff. TSS | Chlorine | Turbidity | Rainfall | Leachate | Ammonia | Ammonia | TON | TON | TKN | TKN | Nitrite | Nitrite | Nitrate | Nitrate | Perc. Pond
Month | GCSD | CSA6N | Effluent | MPN | mg/l | mg/l | mg/l | mg/l | mg/l | NTU | Inches | Gallons | Inf. Mg/l | Eff. Mg/l | Inf. Mg/l | Eff. Mg/l | Inf. mg/l | Eff. Mg/l | Inf. Mg/l | Eff. Mg/l | Inf. Mg/l | Eff. Mg/l | MG
January | 1.0562 | 2.039 | 0.46473 | <2.0 | 158 | 7.25 | 76 | <1.0 | 3.09 | 0.12 | 10.88 | 22966 | 38 | 0.5 | 8.7 | <0.40 | 47 | 0.75 | 7 | <0.40 | 8.3 | 44 | 0
Febuary | 1.435 | 0.085 | 3.3008 | <2.0 | 123 | <5.0 | 122 | <1.0 | 3.31 | 0.25 | 19.8 | 25023 | 19 | <0.20 | 5.5 | <0.40 | 24 | <0.40 | 1.6 | <0.40 | 9 | 30 | 0
March | 1.1103 | 2.6209 | 2.9483 | <2.0 | 102 | <5.0 | 97 | <1.0 | 3.14 | 0.21 | 10.23 | 35026 | 9.9 | <0.20 | 7.5 | <0.40 | 17 | <0.40 | 1.3 | <0.40 | 4 | 19 | 4.5406
April | 0.7998 | 2.5246 | 1.6843 | <2.0 | 165 | 7.07 | 88 | 1.07 | 2.82 | 0.29 | 3.44 | 12530 | 30 | 0.2 | 9.1 | <0.40 | 39 | <0.40 | <0.40 | <0.40 | 4.4 | 30 | 0
May | 1.1065 | 1.5081 | 1.8327 | <2.0 | 146 | <5.0 | 75 | 1.87 | 2.89 | 0.56 | 6.77 | 0 | 24 | 0.4 | 8.5 | <0.40 | 33 | 0.75 | 5.4 | <0.40 | 11 | 53 | 0
June | 0.9771 | 1.4263 | 5.8352 | <2.0 | 143 | <5.0 | 80 | <1.0 | 2.62 | 0.32 | 0 | 0 | <0.20 | 29 | <0.40 | 10 | <0.40 | 39 | 0.57 | <0.40 | 7.5 | 38 | 0
July | 1.0976 | 0.7281 | 6.5763 | 6.6* | 156 | <5.0 | 73 | 3.1 | 2.83 | 0.18 | 0 | 0 | 42 | <0.20 | 11 | <0.40 | 53 | <0.40 | 7.4 | 2.8 | 7.4 | 45 | 0
August | 1.0197 | 1.3268 | 7.1337 | <2.0 | 152 | <5.0 | 100 | 1.87 | 2.85 | 0.47 | 0 | 0 | 34 | <0.20 | 14 | <0.40 | 48 | <0.40 | N/A** | N/A** | <0.20 | 39 | 0
September | 0.6435 | 0.7505 | 5.2968 | <2.0 | 183 | <5.0 | 62 | <1.0 | 3.08 | 0.49 | 0.47 | 0 | 37 | <0.20 | 7.5 | <0.40 | 45 | <0.40 | 4.8 | <0.40 | 7.4 | 48 | 0
October | 0.6516 | 0.6968 | 2.2604 | <2.0 | 149 | <5.0 | 113 | 1.7 | 3.65 | 0.64 | 0 | 0 | 39 | <0.20 | 26 | <0.40 | 65 | <0.40 | 5.9 | <0.40 | 8 | 53 | 0
November | 0.807 | 0.9719 | 1.8376 | <2.0 | 127 | <5.0 | 96 | <1.0 | 3.66 | 0.47 | 4.66 | 0 | 37 | <0.20 | 14 | <0.40 | 51 | <0.40 | 1.1 | <0.40 | 5 | 53 | 0
December | 0.7885 | 1.4958 | 0 | <2.0 | 122 | 7.625 | 63 | 1.25 | 2.85 | 0.22 | 5.79 | 9605 | 34 | <0.20 | 8.8 | <0.40 | 43 | <0.40 | 4.9 | <0.40 | 11 | 56 | 0
Yearly Total | 11.4928 | 16.1738 | 39.1708 |  | 1726 |  | 1045 |  |  |  | 62.04 | 105150 | [10 empty] | 4.5406
Monthly Average | 0.95774 | 1.3478 | 3.2642 | <2.0 | 143.8333 | 1.83 | 87.0833 | <1.0 | 3.0658 | 0.35167 | 5.17 | 8762.5 | 31.2636 | 0 | 10.9636 | 0 | 42.2727 | 0 | 3.997 | 0 | 7.5455 | 42.3333 | 0.37838
*Bad sample was collected on July 31, 2019. Operator took sample without wearing gloves, which caused a high reading.
** Nitrite was not conducted for the month of August due to Lab Equipment failure.
|  |  | Reviewed by: | [8 empty] | Date: | 2020-01-20