| INFORMATION | PLAN CHECK NO.: |  |  | EXPIRATION DATE: |  |  |  |  |  |  |  | STATUS: |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PROJECT ADDRESS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | WORK DESCRIPTION: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | APPLICANT’S NAME: |  |  |  |  |  |  | TEL. NO.: |  |  |  |  |  |  |
|  | ADDRESS: |  |  |  |  |  |  | EMAIL: |  |  |  |  |  |  |
|  | USE | OCCUPANCY GROUP | FLOOR AREA |  | OCCUPANT LOAD | TYPE OF CONSTR. |  |  |  | NO. OF STORIES |  |  |  | FIRE SPRINKLER LOCATION |
| INSTRUCTIONS | Your application for a permit, together with plans and specifications, has been examined and you are advised that the issuance of a permit is withheld for the reasons hereinafter set forth. The approval of plans and specifications does not permit the violation of any sections of the Building Code or other local ordinances or state laws. In an effort to streamline the plan review process, please follow the steps outlined below to ensure that there is no delay in processing your application and reviewing your responses to these plan check comments. - Comments with circled item numbers apply to this plan check. - Revised plans and calculations shall incorporate or address all comments marked on the original checked set of plans, calculations, and this plan review checklist. Provide a written response to each comment and show where and how it has been addressed. Identify the sheet number and detail or reference note on the revised plans where the corrections are made. Time spent searching for the corrected items on the revised plans or calculations will delay the review and approval process. Once all comments on the plans, calculations, and this checklist have been addressed, contact the plan check staff to schedule an appointment to review the changes made. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | PLAN REVIEWER: |  |  |  |  |  | TEL. NO.: |  |  |  |  |  |  |  |
|  | ADDRESS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | EMAIL: |  |  |  |  |  | WEBSITE: |  |  |  |  |  |  |  |
|  | Should you have any questions or need clarification pertaining to the comments made on your project, you may contact the plan check staff by telephone from to M T W TH F. - Bring the original checked set of plans and calculations along with this checklist to the meeting. Do not schedule an appointment meeting with the plan check staff until all comments have been addressed. - Incomplete, indefinite or faded drawings or calculations will not be accepted. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NOTE | Numbers within the parenthesis ( ) refer to the section of the applicable code. 2016 California Building Code (CBC), Table (T), 2016 California Plumbing Code (CPC), 2016 California Mechanical Code (CMC), 2016 California Fire Code (CFC) |  |  |  |  |  |  |  |  |  |  |  |  |  |

- PART I: GENERAL REQUIREMENTS

- A.	PERMIT APPLICATION

- Provide a fully dimensioned plot plan to scale, in ink and copy it to the plot plan sheet provided by the department. Include the following information as applicable: project address, type of construction, number of stories, use and occupancy of the building, fire separation distance or setback of building to property lines or other buildings on the lot, lot size and dimensions, street center line, alley, number of parking spaces, location of all other buildings on the lot, legal description, and permit application number.

- Valuation provided or determined during the initial submittal process was not accurate.

- Valuation is revised to $________.

- Pay additional required plan check fee of $________.

- Provide complete and correct legal description (i.e., Tract, Lot, Block, APN, metes and bounds, etc.).

- Provide complete information for (applicant) (owner) (engineer) (architect) (contractor) (______________).

- Separate permit application is required for the following items:

- a.	Retaining walls or block fence walls

- b.	Grading work

- c.	Swimming pools

- d.	Separate structures

- e.	Shoring

- f.	Demolition

- g.	Electrical, Mechanical, and/or Plumbing work

- h.	Fire sprinkler systems

- i.	Signs

- j.	Others_________________________________

- When all required approvals are obtained, the permit application must be signed by the property owner, licensed contractor, or authorized agent at the time the permit is to be issued:

- a.	For owner-builder permits: Owner’s signature can be verified with owner’s driver license. Owner’s representatives must present owner’s approval with a notarized letter from the owner.

- b.	For contractor building permits: Prior to the issuance of a building permit, the contractor shall have the following:

- i.	Certificate of workers Compensation Insurance made out to the Contractors State License Board.

- ii.	Copy of Contractors State License or pocket ID.

- iii.	Copy of city business tax registration certificate or a newly paid receipt for one.

- iv.	Notarized letter of authorization for agents.

- B.	ADMINISTRATION

- Obtain all approvals/clearances from the following department, bureau, or agency noted below. It is necessary to apply immediately for the signoff as it can take months for some departments, bureaus, or agencies to review and approve the project. All required approvals/clearances must be secured prior to permit issuance.

- The final set of construction documents must be stamped by the following department/bureau/agency:

- a.	Planning

- b.	Fire

- c.	Public Works

- d.	Health

- e.	Others_________________________________

- Adjoining public and private property shall be protected from damage during construction, remodeling and demolition work.  The person making or causing an excavation to be made shall provide written notice to the owners of adjoining buildings advising them that the excavation is to be made and that the adjoining buildings should be protected. Said notification shall be delivered not less than 10 days prior to the scheduled.  (CBC 3307.1)

- Building projections into public properties must comply with Chapter 32. Note on the plans:  "Temporary pedestrian protection shall be provided as required by Section 3306.  (CBC 3201.3, 3202.3.4, CBC 3306)

- Each sheet of the construction documents must bear the signatures, registration number and expiration date of the registered design professional in responsible charge licensed in the State of California.

- The address of the project and the name/address of the owner are required on the first sheet or title sheet of the construction documents. Include the name/address of the registered design professionals and/or consultants on the construction documents where applicable.

- _____ set(s) of construction documents will be required during permit issuance. Construction documents must be:

- a.	Quality blue or black line drawings with uniform and light background color.

- b.	Max. 36' x 48" size with min. 1/8" lettering size.

- c.	Sticky back details must produce prints without contrasting shades of background color.

- Provide the following type of information with each set of construction documents:

- a.	Topography Survey Map

- b.	Grading

- c.	Floor Plans

- d.	Two Elevations

- e.	Construction Sections

- f.	Foundation Plans

- h.	Framing Plans

- i.	Structural Details

- j.	Others_________________________________

- Provide a fully dimensioned plot plan to scale showing:

- a.	Legal Description

- b.	Building Lines

- c.	Easements

- d.	Lot Size

- e.	Highway Dedication Lines

- f.	Zone Boundaries

- h.	Alley

- i.	Street Centerline

- j.	Parking Spaces

- k.	Use of all Buildings

- l.	Size of all buildings

- m.	Show use of each room

- Show the building area, occupancy group(s), use(s), type of construction(s), number of story(ies), height, type of fire sprinklers system provided, and the number of parking space(s) on the first sheet or title sheet of the construction documents. Include justification and analysis for increase in area, height, and/or story.

- Show on site plans the natural and finish grade elevations around the perimeter of the building. Show elevations for all floors and top of roof. Survey map signed by a licensed Surveyor or Civil Engineer may be required by the department.

- Remove all plans, details or notes that do not pertain to the project.

- PART II: BUILDING CODE

- A.	GENERAL REQUIREMENTS

1.	The following nonstructural products shall comply with an 	approved ICC evaluation report.  Copy the report and conditions of 	approval onto the plans and show compliance with those conditions.

☐ 	Deck Coating		☐  Roofing Materials

☐  Exterior Siding 		☐  Skylights

☐  Fire Rated Assemblies

☐  Sound/Thermal Insulation

☐  Damp proofing material behind basement walls

☐  Others such as ________________________

2.	Add notes on plans:

*	The construction shall not restrict a five-foot clear and unobstructed access to any water or power distribution facilities (Power poles, pull-boxes, transformers, vaults, pumps, valves, meters, appurtenances, etc.) or to the location of the hook-up. The construction shall not be within ten feet of any power lines-whether or not the lines are located on the property. Failure to comply may cause construction delays and/or additional expenses.

*	Shower compartments and walls above bathtubs with installed shower heads shall be finished with a smooth, nonabsorbent surface to height not less than 72 inches above the drain inlet. (CBC 1210.2.3). Use of water-resistant gypsum backing board shall be as stated in CBC 2509.3

*	Water heaters must be strapped to a wall

(CPC 507.2)

*	Unit skylights and tubular daylighting devices shall be tested and labeled as complying with AAMA/WDMA/CSA 101/I.S./A440.  The label shall state the name of the manufacturer, the approved labeling agency, the product designation and the performance grade rating. (CBC 2405.5)

*	A copy of the evaluation report and/or conditions of listing shall be made available at the job site.

- B.	OCCUPANCY CLASSIFICATION

1.	When the sleeping units are not equipped with cooking facilities and the stay of the guests is no more than 30 days, the building shall be classified as R1 occupancy. Even with cooking facilities such as the “extended-stay hotels”, they are still considered as R1 due to the time duration of the stay.

2.	Dormitory for elderly with a 24-hour a day medical supervision with more than 5 occupants shall be classified as I2. (CBC 308.4)

3.	All congregate living facilities such as small boarding houses, convents, dormitories, monasteries or non-transient motels for blended families no more than 16 occupants and small enough to operate as a single family unit shall be classified as R3 occupancy.

(CBC 310.5)

4.	All institutional facilities that accommodate six or less people are to be classified as Group R3.1 (CBC 310.5.1). Comply with special requirements per CBC Section 435.

5.	Residential care /assisted living facilities including more than six ambulatory clients (exclude staff) shall be classified as R4. (CBC 310.6)

6.	Townhouses not more than 3 stories above grade in height with a separate means of egress for each unit shall be classified as R3 occupancy. (If a portion of the means of egress is exiting through a common area such as an exit court on the side of the building, this townhouse should be classified as a R2 occupancy).

- Adult care or child care for less than 24 hours with six or less clients shall be classified as R3 occupancy. (CBC 310.5)

- Residential care / assisted living facilities with more than 6 ambulatory clients and no more than 6 non-ambulatory or bedridden clients shall be classified as R4 (CBC 310.6) Comply with Section 435 for special requirements.

9.	This is a mixed occupancy building and subject to the provisions of CBC Section 508.

10.		The following are required for attached garage / carport (U occupancy):

a.	Garage shall not exceed 1000 sq. ft. except a private garage accessory to Group R3 occupancy shall not exceed 3000 sq. ft.  (CBC 406.3.1)

b.	Separation from other than private garages adjacent to dwelling units shall comply with CBC Section 508 & T508.4 (CBC 406.3.4).

c.	Separation from the dwelling unit and its attic area by means of a minimum 1/2-inch gypsum board applied to the garage side.

(CBC 406.3.4.1).

d.	Separated from all habitable rooms above by not less than a 5/8-inch Type X gypsum board or equivalent and ½-inch gypsum board applied to structures supporting the separation.

(CBC 406.3.4.1)

e.	Doors between garage and the dwelling unit shall be self-closing and self-latching, solid wood or solid or honeycomb core steel not less than 13/8 inches thick, or have a minimum fire protection rating of 20 minutes. (CBC 406.3.4.1)

f. 	Garage shall not open directly into a room used for sleeping purposed.  (CBC 406.3.4.2)

g.	Ducts in a private garage and ducts penetrating the walls or ceilings separating the dwelling unit from the garage shall be constructed of a minimum 0.019-inch sheet steel and shall have no openings into the garage. (CBC 406.3.4.3)

h.	Exterior walls of a U occupancy less than 5' from a property line must be one-hour construction without openings.  	(CBC T602)

i.	Concrete or similar noncombustible and non-absorbent floor, or asphalt surface at ground level only.  The minimum thickness of concrete floor slabs supported directly on the ground shall not be less than 3-1/2 inches.  (CBC 406.4.5)

- C.	BUILDING LIMITATION

1.	Show on plans:

❏	Height (existing, proposed)

❏	Number of stories (existing, proposed)

❏	Number of basement level(s)

❏	Occupancy Group(s)

❏	Type(s) of Construction

❏	Fire District(s)

❏	Fire Walls (CBC 706)

❏	Unobstructed yards (CBC 506.3)

❏	Sprinkler Type (CBC 903.2.8, T506.2)

❏	Use of all rooms/areas on floor plans

❏	Fire Alarm (CBC 907)

❏	Allowable floor Area Analysis (CBC 506)

2.	The building as shown is a mixed-occupancy (separated occupancy) building.

a.	In each story, the sum of the ratios of the actual building area of each separate occupancy divided by the allowable building area per story of each occupancy must not exceed one.

(CBC 508.4.2)

b.	For the maximum area of a building, the sum of the ratios of the total actual area for each separate occupancy divided by the allowable area per story for each separate occupancy must not exceed two.  (CBC 506.2.4)

- Unobstructed yards of minimum 20’ must be maintained at minimum 25% of the building perimeter to permit a (______) % floor area increase.  Provide calculation of If determination.  (CBC 506.3)

- Allowable area per story is defined as:

a.	Single occupancy, multistory building

Aa = [At + (NS x If)] x Sa 			(CBC 506.2.3)

b.	Mixed occupancy, multistory building

Aa = [At + (NS x If)]				(CBC 506.2.4)

Where:

Aa = Allowable area (square feet).

At = Tabular allowable area factor (NS, S1, S13R, or SM value as applicable) in accordance with T506.2

NS = Tabular allowable floor area factor in accordance with T506.2 for non-sprinklered building (regardless of whether the building is sprinklered)

If = Area factor increase due to frontage (percent) as calculated in accordance with CBC Section 506.3

Sa = Actual number of building stories above grade plane, not to exceed two for multistory.

4.	Building exceeds allowable height limit of T504.3 for Type (____) construction. (CBC 503):

Max (____) feet in height

Max (____) stories in height.

5.	Maximum 3 / 2 stories allowed for R1 and R2, type (VA /VB) construction (CBC T504.4)

6.	R2 occupancy above S2, type I or type IV construction may measure the height in terms of stories from above the parking area when building complies with Section (CBC 510.4).

7.	Provide calculations for establishing grade plane as per Section 202.  Attach calculations and established grade planes on elevations plans and site plan.

(CBC 202)

- Show maximum height of the structure (in feet and stories) from top of roof to grade plane (to the average height of the highest roof surface) on all elevation views.  (CBC 202)

9.	Lowest level is determined not to be a basement.   This level is considered as 1st story above grade plane.  Include this story in total building height.

(CBC 202)

10.	Automatic sprinkler system (NFPA-13) may be used for only one of the following purposes:

a. 	Height increase		 (CBC 504.3)

b. 	Area increase  		 (CBC 506.2)

11.	Automatic sprinkler system (NFPA-13) may be used for both height and area increase for R2 occupancy, type VA construction only. (CBC T504.3, T506.2)

12.	Indicate area increase method on plan.  Indicate if automatic sprinkler system is used for area increase, height increase or fire-resistance rating substitution.

13.	This structure is of type (____) construction. Show on the plans the required (____) rated roof, (____) rated exterior wall construction, (____) structural frame protection, and (____) floor construction. (CBC T601)

a.	Structural steel members shall be protected with an approved product.  Thicknesses of fire proofing material shall be specified on the plans. (CBC 703.2)

b.	Restrained Construction - Steel members shall be identified by the Engineer. (CBC 703.2.3)

14.	Exterior (bearing) (nonbearing) walls of Type (____) construction must be of (____) hour rated construction. (CBC T601)

15.	Fire partitions and smoke barriers shall be continuous to the underside of the floor or roof sheathing and passing through any concealed spaces or attic areas (CBC 708.4, 709.4)

- D.	SPECIAL USE OR AREAS

1.	This structure has an Atrium(s).  Comply with CBC Section 404 (CBC 404.1 thru 10)

- E.	FIRE-RESISTANCE RATED CONSTRUCTION

1.	Clearly identify the locations of the Fire Areas, Fire Walls, Fire Barriers and Fire Partitions on the plans.  Provide complete legends and details.

(CBC 706, 707, and 708)

2.	Fire rated assemblies shall be per CBC T721, generic assemblies of Gypsum Handbook, or ICC approval.

3.	Show the fire separation distance: to interior lot line; to centerline of the street, and to an imaginary line between two buildings on the property.  The distance shall be measured at right angles from the face of the wall. (CBC 202)

4.	Provide complete analysis for protected and unprotected exterior wall openings per CBC Section 705.8 & Equation 7-2.  Openings are not allowed when the fire separation distance is less or equal to 3’. (CBC T705.8)

a.	Door openings in exterior walls must be protected with (3/4-hour) or (1½ hour) fire assemblies (CBC T716.5)

b.	Window openings in exterior walls must be protected with (1/3-hour), (3/4-hour) or

(1½ hour) fire assemblies.

(CBC T716.6)

5.	Provide (____) hour fire resistance rating for exterior walls for R2, type (____) at (____) ft from property line or assumed property line. (____) hour fire resistance rating exterior wall required for building zero feet from P.L.

6.	Projections shall not extend any closer to the line used to determine the fire separation distance or not more than a minimum 24" / 40" from line used to determine the fire separation distance with fire separation distance of (____) ft. (CBC T705.2)

7.	Provide minimum 30 inch high parapet at (____) walls. (CBC 705.11)

8.	Provide details to show that Fire Wall complies with CBC Section 706 including but not limited to:

a.	Fire Rating shall be (____) hour per T706.4

b.	Fire walls must remain structurally stable in the event of collapse of construction on either side during a fire.  Provide a detail to show that joist supported by the fire wall is spliced and not continuous (plywood membrane may be continuous), or provide double fire walls or provide justification for any other method used.  (CBC 706.2)

c.	Shall be noncombustible material, except in Type V construction per CBC 706.3.

d.	Shall have horizontal continuity per CBC 706.5.

e.	Shall extend vertically from the foundation to a point 30 inches above the roof per CBC 706.6.

f.	The area of each opening in Fire Walls is limited to 156 sf.  Total width of the openings is limited to 25 percent of the wall length in the story under consideration. (CBC 706.8)

g.	All openings in fire walls shall be protected with fire assemblies having a fire-resistive rating of (1½) (3) hours. (CBC T716.5)

h.	Ducts and air transfer openings through Fire Walls should be avoided. If allowed, duct and air transfer opening penetrations shall be protected as required in CBC Section 714 and 717. Dampers are required. (CBC 705.10)

i.	Exits must be provided independently for each area bounded by fire walls except for horizontal exits per CBC Section 1026.

9.	Fire wall cannot create a separate building for the purpose of automatic fire sprinkler system requirements as set forth in Chapter 9, unless the fire wall is 4 hours with no openings. (CBC 706.1.1)

10.	A complete (____) hour separation is required between Group (____) and Group (____) Occupancies. Separation walls shall be fire barriers complying with CBC Section 707. Horizontal assemblies shall comply with CBC Section 711. Openings in the separation shall have (____) hour fire assemblies.  (CBC 508.4.4.1, T508.4, 707, 712, 715)

11.	Fire barriers and horizontal assemblies separating single occupancies into different fire areas shall be (____) hour fire rated per CBC T707.3.10.

12.	Areas of each opening in fire barrier are limited 156 sf.  Total width is limited to 25 percent of the wall length in the story under consideration.

(CBC 707.6)

- Elevator lobby is required at each floor where an elevator enclosure connects more than 2 stories. (CBC 3006.2)

- Provide (____) hour rated Fire Partition at walls separating dwelling units and common areas, corridors, and elevator lobbies. (CBC 708.1, 708.3)

- Fire barrier at vertical occupancy separations must have continuity and must extend through underfloor area, attic areas, and suspended ceiling areas.

(CBC 707.5)

- Opening protectives shall be per CBC Section T716.5.  Doors shall be (____) hour fire rated and windows shall be (____) hour fire rated.

(CBC T716.5, T716.6)

- Openings through a floor/ceiling assembly shall be protected by a (1) (2) hour shaft enclosure.  The shaft enclosure shall be constructed of fire barriers and/or horizontal assemblies. (CBC 713.2, 713.4)

- A floor opening connecting not more than two stories is permitted if it complies with all the conditions per CBC Section 712.1.9. If not, the atrium provision shall be utilized for open two story spaces.  See additional corrections for atrium.

19.	Penetrations in a fire-rated wall shall be protected by an approved fire stop material in accordance with CBC Section 714.3.1.

  - Steel, Copper or ferrous pipes or conduits may penetrate concrete or masonry walls where the penetrating item is a maximum 6-inch diameter and the area of the opening through the wall does not exceed 144 square inches.

  - Membrane penetrations of maximum 2-hour fire- resistance rated wall and partitions by steel electrical outlet boxes not exceeding 16 square inches are permitted provided openings do not exceed 100 square inches for any 100 square feet of wall area. Outlet boxes on opposite sides of walls or partitions must be separated by a horizontal distance of 24 inches. (CBC 714.3.2)

  - Where walls are penetrated by other materials or where larger openings are required than permitted in (b) above, they must be qualified by tests conducted in accordance with CBC Section 714.3.1.1.

20.	Smoke and fire dampers must be installed in the following locations per CBC Section 717.5.

a.	Duct penetrations of fire walls in accordance to section (CBC 717.5.1)

b.	Duct penetrations of fire barriers, except exit enclosures and exit passageways where they are not allowed to penetrate. (CBC 717.5.2)

c.	Ducts penetrating shafts. (CBC 717.5.3)

d.	Ducts penetrating fire partitions and fire-rated corridor walls. See exception for steel ducts with no openings into corridor (CBC 717.5.4)

e.	Ducts penetrating smoke barriers (CBC 717.5.5)

f.	Ducts penetrating exterior walls (CBC 717.5.6)

g.	Ducts penetrating smoke partitions (CBC 717.5.7)

h.	Ducts penetrating horizontal assemblies.

(CBC 717.6)

21.	Show draft stop location on plans. Also, provide these notes on the plans:

- In buildings used for residential occupancies, draft stops must be installed in wood frame floor construction containing concealed space.  Draft stopping shall be located above and in line with the dwelling unit and sleeping unit separation. (CBC 718.3.2).

- In buildings used for residential occupancies, draft stops must be installed in the attic (mansards) (overhangs) (false fronts set out from walls) (similar concealed spaces) formed by combustible construction.  Draft stopping shall be installed above and in line with sleeping unit and dwelling unit separation walls that do not extend to the underside of the floor sheathing above. (CBC 718.4.2).

c.	Draft-stopping materials must not be less than ½-inch gypsum board, 3/8-inch plywood, 3/8-inch Type 2-M particle board or other materials approved by the building department.  Draft-stopping must be adequately supported.

(CBC 718.3.1)

22.	Draft stops shall be provided within attics, mansards, overhangs and similar concealed spaces formed of combustible construction, unless the building is sprinklered with NFPA13 sprinkler system (3000 sf between draft stops).  (CBC 718.4.3)

23.	Draft stop shall be provided within a concealed floor-ceiling assembly formed of combustible construction, unless the building is sprinklered with NFPA 13 sprinkler system. (CBC 718.3.2)

24.	Horizontal occupancy separation must be supported with a structural system having equivalent fire-resistive protection. (CBC 704.1)

25.	Note on plans: Fire blocking must be provided in accordance with CBC Section 718 at the following locations:

a.	In concealed spaces of stud walls and partitions, including furred spaces, at the ceiling and floor levels. (CBC 718.2.2)

b.	In concealed spaces of stud walls and partitions, including furred spaces, at 10-foot intervals along the length of the wall. (CBC 718.2.2)

c.	At all interconnections between concealed vertical and horizontal spaces such as occur at soffits, drop ceilings, cove ceilings and similar locations. (CBC 718.2.3)

d.	In concealed spaces between stair stringers at the top and bottom of the run and between studs along and in line with the run of stairs if the wall under the stairs is unfinished. (CBC 718.2.4)

e. 	In openings around vents, pipes, ducts, chimneys, fireplaces and similar openings which afford a passage for fire at ceiling and floor levels, with noncombustible materials. (CBC 718.2.5)

26.	This building is of Type V-A / III-A construction, provide / show:

a.	Continuous drywall behind all tubs is required unless the walls are within the unit and non- bearing. Back to back tubs with a common plumbing wall are impractical in 1-hour buildings.

b.	All interior bearing walls shall be constructed of not less than 1-hour fire-resistive construction.

(CBC T601)

c.	Attic access openings in 1-hour ceiling can be 2 layers of 3/4" plywood or one layer of 1-5/8" T&G material, self-closing.

d.	All openings in floors are required to be enclosed by a shaft having wall, floor, and ceiling of (____) hour fire resistive construction.  (CBC 713.1)

e.	Recessed ceiling light fixtures must be boxed around with 5/8" Type “X” drywall” to maintain the 1-hour ceiling assembly.

f.	Continuous drywall is required behind all electrical service panels, fire hoses and medicine cabinets.

g.	Exhaust fans from the bathroom must enter through the wall. Dampers are required if the ceiling is penetrated. (CBC 717.5)

h.	Plumbing penetration through horizontal occupancy separations shall be boxed out and filled with approved safing material. Insulation is not approved.

I.	Penetration of the 1 hour ceiling by ducts from the FAU and the stove hood require dampers (use a ductless hood whenever possible). Attic units (including heat pumps) require dampers at all ceiling penetrations. (CBC 714.1.1)

j.	Steel beams and columns shall be protected as required for 1-hour protection. Where ceiling forms the protective membrane for fire-resistive  assemblies (occupancy  separations and rated roof/ceiling or floor/ceiling assemblies), the construction (floor joists) and their supporting horizontal structural members (beams) need not be individually fire protected except where such members support directly applied loads from more than one floor or roof.  The required fire resistance shall not be less than that required for individual protection of members. (CBC 704.3)

k.	All plumbing penetrations thru walls which require protected openings (Fire walls, Fire barriers, Fire partitions) are required to be galvanized or cast iron piping.

27.	S2 Occupancy, Type I construction garage requires 2 hour separation (minimum floor assembly for S2 occupancy) from R2 occupancy, but not less than required per CBC T508.4.  Show details.

(CBC 510.4, 508.3.3, T508.4).

      - A rated self-closing door between the garage and  (CBC 406.3.4)

28.	S2 Occupancy garage shall comply with the followings:

      - Concrete or similar noncombustible and nonabsorbent floor, or asphalt surface at ground level only.  (CBC 406.4.5)

      - Sloped floor to facilitate the movement of liquids to a drain or toward the main vehicle entry doorway.  (CBC 406.4.5)

      - Floor system designed for uniform or concentrated   loads per CBC T1607.1

      - Minimum headroom of 7ft. (CBC 406.4.1)

      - Vehicle barriers not less than 2 feet 9 inches high placed at the end of drive lanes, and at the end of parking spaces where the difference in adjacent floor elevation is greater than 1 foot. (CBC 406.4.3)

      - Vehicle barriers designed in accordance with CBC Section 1607.8.3.

- F.	INTERIOR FINISHES

1.	Indicate on plans that interior finish materials applied to wall and ceilings shall be tested as specified in CBC Section 803.  In addition, provide details showing application in accordance with CBC Section 803, 804, and T803.11.

2.	The flame-spread rating of paneling materials on the walls of the corridor, lobby and exit enclosure must be identified on plans.  (CBC T803.11)

3.	An automatic sprinkler system is required throughout per CBC Section 903.2.8.

- G.	FIRE PROTECTION

1.	Building with floor areas over 1500 sf shall be sprinklered where 20 sq. ft. of opening for every 50 ft. of wall length is not provided. (CBC 903.2.11.1)

2.	An automatic sprinkler system is required throughout all buildings with a Group “R” fire area. Note on plan: “This building and garage must be equipped with an automatic fire extinguishing system, complying with (NFPA-13 / NFPA-13R); The Sprinkler System plans shall be submitted and approved as a deferred submittal prior to installation.” (CBC 903.2)

3.	Exceptions to, or reductions in building code requirements based on the installation of automatic fire extinguishing system is not allowed when utilizing NFPA-13R type residential sprinkler system allowed for R occupancies.

(CBC 903.2.8, T504.3, T504.4 & T506.2)

4.	Show the location on the plans. Class I, II or III standpipe (dry, wet, combination) are required in this building. (CBC 905.3.1)

- Provide automatic sprinkler system at top of rubbish and linen chutes and in their terminal room.

- (CBC 903.2.11.2)

6.	Waste and linen collection rooms over 100 square feet shall provide 1 hour separation or provide automatic fire-extinguishing system or classify room with occupancy comply with separation per CBC Table 509.

7.	The Type I parking structure permitted by CBC Section 510.3 is a story (first story) and not a basement.  Because of this, the structure is 4 stories in height and requires sprinklers throughout.

(CBC 903.2)

8.	Add note: “This building shall be provided with a manual alarm system with the capability to support visible alarm notification appliances in accordance with NFPA 72.

(CBC 907.2.9, 907.5.2.3.3, 907.5.2.3.4)

9.	Provide an automatic alarm system for the hotel with both visual and audible alarms activated by the both in-room smoke detector and the building fire alarm system on (____) sleeping units. (CBC 907.5.2.3.3)

10.	The following note shall be provided on the plans:

“Buildings shall have approved radio coverage for emergency responders.  See California Fire Code Section 510 for more details.”

This note shall apply to all new buildings meeting any one of the following conditions:

a.	There are more than 3 stories above grade

plane.

b.	The total building area is 50,000sf or more.

c.	The total basement or parking area is

10,000sf or more.

d.	Any basement or level that extends 2 or more 	stories below grade plane.

e.	Any building that is 21,000s. or greater and is 	equipped with a solar voltaic system.

- H.	MEANS OF EGRESS

1.	Exterior exit stairs and ramps shall be located at least 10 feet from adjacent lot lines and from other buildings on the same lot. (CBC 1027.5)

2.	All stairways shall be built of materials consistent with the types permitted for the type of construction of the building, except that wood handrails shall be permitted for all types of construction. (CBC 1011.7)

3.	For areas having fixed seats and aisles, the occupant load shall be determined by the number of fixed seats installed therein. The occupant load for areas in which fixed seating is not installed, such as waiting spaces shall be determined in accordance with CBC Section 1004.1.2 and added to the number of fixed seats. (CBC 1004.4)

4.	For areas having fixed seating without dividing arms, the occupant load shall not be less than the number of seats based on one person for each 18 inches of seating length. (CBC 1004.4)

5.	The occupant load of seating booths shall be based on one person for each 24 inches of booth seat length measured at the backrest of the seating booth. (CBC 1004.4)

6.	Show detailed summary of the floor area and all deductions (if used) for Gross and/or Net floor area. (CBC 1004.1)

7.	Use correct occupant load factor for the function of space according to CBC T1004.1.2.

8.	Two exits are required from each space or story.	(CBC T1006.2.1)

a.	Occupant load > 49, (A, B, E, F, M, U)

b.	Occupant load > 10, (R)

c.	Occupant load > 29, (S)

d.	Common path of egress > 75ft.

e.	Common path of egress > 100ft. (B, F, S) sprinklered building

f. 	Common path of egress > 125ft. (R2) sprinklered building

9.	Provide two means of egress for stories exceeding the limits of CBC T1006.3.2(1) and T1006.3.2(2).

10.	Where two or more exits are required, at least two exits must be separated by ½ the maximum diagonal length of the area served.  See exceptions.

(CBC 1007.1.1)

11. Where more than one exits are required, the means of egress shall be configured such that the loss of any one exit shall not reduce the available capacity to less than 50% of the required capacity. (CBC 1005.5)

12.	All exit doors shall comply with CBC Section 1010.

a.	Clear width of each door opening shall be min. 32" or per Section 1005.1, whichever is greater.

b.	Min. door height of 6'-8".

c.	Shall be capable of opening 90 degrees.

d.	The maximum width of a swinging door leaf shall be 48” nominal.

e.	Exit door shall be pivoted or side-hinged swinging type (CBC 1010.1.2)

13.	Door(s) # (____) serve(s) an area that has an occupant load of 50 or more. Swing this/these door(s) in the direction of egress travel.	(CBC 1010.1.2.1)

14.	Show the path of exit travel to and within exits. The exit path shall be identified by exit signs conforming to the requirements of CBC Section 1013. Exit signs shall be readily visible from any direction of approach. Exit signs shall be located as necessary to clearly indicate the direction of egress travel. No point shall be more than 100 feet from the nearest visible sign. (CBC 1013)

15.	The capacity of the means of egress required from any story of a building shall not be reduced along the path of egress travel until arrival at the public way. (CBC 1005.4)

16.	Change of elevation at (______) is less than 12 inches, provide sloped surface.  If slope is greater than 5%, ramps shall comply with CBC Section 1012. (CBC 1003.5)

17.	Provide a 1hr. fire rated corridor in accordance with CBC T1020.1

a.	Occupant load > 30

b.	Occupant load >10

18.	Detail and reference all rated corridor construction and protected openings in accordance to CBC Section 709 for fire partitions. Protection to be of a 20min. doors and 45min. for other openings.

(CBC 1020.1)

19.	Provide a minimum corridor width per CBC T1020.2 or per CBC Section 1005.1.  (CBC 1020.2)

20.	Revolving doors used for egress purpose shall be accompanied by a side-hinged swinging egress door located a maximum of 10 feet along the same wall. (CBC 1010.1.4.1)

21.	Provide complete details for ramps when used as part of the egress component.  Show width, slope, landing and handrails dimensions accordance with CBC Section 1012.

22.	Thresholds at doorways shall not exceed 0.50” in height.  0.75” in height for sliding doors serving dwelling units.  (CBC 1010.1.7)

23.	Floors or landings on each side of doors to have the same elevation. Landings shall be level except for exterior landings (max. 2% slope).  (CBC 1010.1.5)

24.	Landing width at doors must have a min. clear dimension of doors served. Landings shall have a length measured in the direction of travel of not less than 44" (36").  (CBC 1010.1.6)

25.	Doors shall not project more than 7" into the required corridor width or at landings when fully opened and not more than 50% in any position.

(1010.1.6)

26.	Dead end corridors must not exceed 20 feet, or 50 feet for a sprinklered bldg.  (CBC 1020.4)

27.	Detail all stairways to comply with CBC Section 1011:

a. 	Rise: 7" max. Run (tread): 11” min. (CBC 1011.5)

b.	Rise: 7.75” max. Run (tread): 10” for stairs within dwelling units. (CBC 1011.5.2)

c.	Headroom clearance: 6'-8." 	(CBC 1011.3)

d.	Width: (44") (36”) (48” between hand rails for accessible stairs). (CBC 1011.2)

e.	Landing width: Same as stairway served.

(CBC 1011.6)

f.	Landing length: Same as width, max. 48”.

(CBC 1011.6)

g.	Provide a landings at every 12 feet of vertical rise at stairways.  (CBC 1011.8)

h.	Handrail height: 34-38”, max 4” openings                    (CBC 1014.2 and 1015.4)

i.	Handgrip portion of handrail shall not be less than 1.25" and not greater than 2" in cross-section for circular type.  4”- 6.25”perimeter for other shapes.  (CBC 1014.3)

j.	A minimum 1½” handrail clearance from adjacent wall.  (CBC 1014.7)

k.	Handrail extension of 12" beyond the top and bottom riser.  (CBC 1014.6)

l.	1-hour fire rated construction for the enclosed usable space under the stairs.  (CBC 1011.7.4)

m.	Curved stairways:  (CBC 1011.9)

n.	Spiral stairways:  (CBC 1011.10)

28.	Provide 42” high guards at Decks; Landings; Balconies and Walkways where there a vertical drop of greater than 30”. (CBC 1015)

29.	For glass handrails and guards, the panels and their support system shall be designed to withstand the loads specified in Chapter 16.  A safety factor of four shall be used. The minimum nominal thickness of the glass shall be 1/4 inch.  (CBC 2407)

30.	The means of egress system must have a clear ceiling height of 7’-6”.  (CBC 1003.2)

31.	Show calculations for all egress component widths to comply with CBC Sections 1005.2 and 1005.3.

32.	Provide min. 48” plus width of door when doors are placed in series.  (CBC 1010.1.8)

33.	Provide a barrier in the exit enclosure at (______) to prevent entry into the basement level.  (CBC 1023.8)

34.	Building has an exit enclosure connecting more than 3-stories.  Provide an approved stairway sign indicating the floor level, terminus of the top and bottom of the stair and the identification number of the stair.  It shall be located approximately 5 ft. above the floor landing and be readily visible when the stair doors are in an open or closed position.

(CBC 1023.9)

35.	Open space under exterior stairways shall not be used for any purpose.  (CBC 1011.7.4)

36.	Provide floor-level exit signs in all interior corridors of Group A, E, I, and R-2.1 occupancies and in all areas serving guest rooms of hotels in Group R, Division 1 occupancies.  (CBC 1013.7)

37.	The exit passageway may only be used as a means of egress.  Provide a 1-hour fire-resistance rating or of the same rating required for any connecting exit enclosure.  Walls, floors and ceilings shall be constructed as fire barriers in accordance with CBC Sections 707, 1024.1 & 1024.3.

38.	Opening into exit passageways shall be limited to those necessary for egress from normally occupied spaces. Elevators shall not open into an exit passageway. Openings and penetrations shall comply with CBC Section 716.  (CBC 1024.5)

39.	Spiral stairways shall not serve as required exit for an area exceeding 250 and serves not more than 5 occupants. (CBC 1011.10)

40.	For buildings located four or more stories in height above grade plane, one stairway shall extend to the roof surface, unless the roof has a slope steeper 4:12 (33%). (CBC 1011.12)

41.	Vertical exit enclosures: (CBC 1023.2)

a.	Connecting 4-stories more: provide 2-hour fire-resistance rating construction (fire barrier);

b.	Connecting up to 3-stories: provide 1-hour fire-resistance rating construction (fire barrier);

c.	All openings to be protected in accordance to CBC Section 716.  Openings shall be limited to those necessary for exit access to the enclosure from normally occupied space ad for egress from the enclosure. (CBC 1023.4)

42.	Accessible Means of Egress: (CBC 1009)

a.	In buildings where a required accessible floor is four or more stories above or below the level of exit discharge, egress elevator shall be provided, see exceptions.  (CBC 1009.2.1)

b.	Provide 48” clear width between handrails.

(CBC 1009.3)

c.	Platform lifts not allowed as part of accessible means of egress.  (CBC 1009.5)

d.	Max force to operate doors is limited to 15-lb. (CBC 1010.1.3)

e.	Show location and dimension area of refuge. (CBC 1009.6)

i.	Size: (2) 30”x48” or 1/200, whichever is greater.  (CBC 1009.6.3)

ii.	Separation from other space by a smoke barrier.  (CBC 1009.6.4) (Detail construction per CBC Section 709)

iii.	Note: Two-way communication required (CBC 1009.8)

iv.	Signage on door of area of refuge.

(CBC 1009.9)

v.	Exterior area of refuge to comply with CBC Section 1009.7.

43.	Egress through intervening space is not allowed to go through: (CBC 1016.2)

a.	Different tenant space or dwelling units.

b.	A room that can be locked to prevent egress.

c.	Commercial kitchens.

d.	Storage rooms, closets or similar spaces.

44.	Egress convergence applies at (______).  Show calculation for egress width to account for combined occupant load from floor above and below.

(CBC 1005.6)

45.	Horizontal exits: (CBC 1026)

a.	Detail horizontal exits as a 2-hour fire barrier or a fire wall in accordance to CBC Section 706.

b.	Provide self-closing or automatic closing doors

c.	Not allowed as the only exit from a space

d.	Horizontal exits cannot exceed 50% of total exits required

e.	Provide clear summary for the refuge area.  Show capacity for a minimum of 3 sq. ft. for each combined occupant to be accommodated therein.

46.	Egress balconies to comply CBC Section 1021.  Detail plans to meet all requirements.

47.	One openable window with an openable area of not less than 5.7 sq. ft., minimum clear 24" height and 20" width, and a sill height not over 44" above the floor is required in all bedrooms below the fourth story and basement.  (CBC 1030.2)

48.	Escape and rescue windows with a finished sill height below the adjacent ground elevation shall have a window well complying with CBC Section 1030.5.

49.	Provide calculation to show that existing egress system is adequate to accommodate new usable outdoor area.  (CBC 1004.5)

50.	Show and dimension common path of egress travel from each space. (CBC T1006.2.1)  Common path of egress travel shall not exceed 75 ft. or 125 feet provided the R2 is protected throughout with an approved automatic sprinkler system in accordance with CBC Section 903.3.1.1.

51.	Label each space to match the function of space according to CBC T1004.1.2.

52.	Legend on floor plans to show where exits are located and the travel distance to it from the most remote point within a story, measured along the natural and unobstructed path of egress travel.

53.	Show clear width dimension at corridors and exit passageways where doors open into it.

54.	Area of refuge cannot project into egress path of travel.

55.	Hatch/label and dimension all area of refuge.

56.	For high-rise buildings, provide smoke proof or pressurized exit enclosures for buildings required to comply with CBC Section 403.5.4 or 405.7.2.

(CBC 1023.11)

Note on Plans:

1.	Exit signs shall be internally or externally illuminated

2.	Exit signs illuminated by an external source shall have an intensity of not less than 5 foot candles (54 Iux).

3.	Internally illuminated signs shall be listed and labeled and shall be installed in accordance with the manufacturer’s instructions and CBC Section 2702.

4.	Exit signs shall be illuminated at all times.

5.	Exit signs shall be connected to an emergency power system that will provide an illumination of not less than 90min. in case of primary power loss.  (CBC 1013.5-1013.6.3)

6.	Egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort.  (CBC 1010.1.9)

7.	Door handles, lock and other operating devices shall be installed at a min. 34” and a max. 48” above the finished floor.  (CBC 1010.1.9.2)

8.	All egress door operation shall also comply with CBC Section 1010.1.9.

9.	The means of egress, including the exit discharge, shall be illuminated at all times the building space served by the means of egress is occupied. The means of egress illumination level shall not be less than 1foot-candle at the walking surface.  (CBC 1008.1)

10.	The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate the following areas:

a.	Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress.

b.	Corridors, exit enclosures and exit passageways in buildings required to have two or more exits.

c.	Exterior egress components at other than their level of exit discharge until exit discharge is accomplished for buildings required to have two or more exits.

d.	Interior exit discharge elements, as permitted in CBC Section 1028.1, in buildings required to have two or more exits.

e.	Exterior landings, as required by CBC Section 1010.1.6, for exit discharge doorways in buildings required to have two or more exits.

11.	The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with CBC Section 2702.  (CBC 1008.3)

12.	Emergency lighting facilities shall be arranged to provide initial illumination that is at least an average of 1 foot-candle (11 lux) and a minimum at any point of 0.1 foot-candle (1 lux) measured along the path of egress at floor level. Illumination levels shall be permitted to decline to 0.6 foot-candle (6 lux) average and a minimum at any point of 0.06 foot-candle (0.6 lux) at the end of the emergency lighting time duration. A maximum-to-minimum illumination uniformity ratio of 40 to 1 shall not be exceeded. (CBC 1008.3.5)

13.	The exit signs shall also be connected to an emergency electrical system provided from storage batteries unit equipment or an on-site generator set, and the system shall be installed in accordance with the Electrical Code.  For high rise buildings, see section CBC Section 403.

- I.	INTERIOR ENVIRONMENT

1.	Provide stairway illumination. Minimum 1 foot-candle at tread runs.  (CBC 1205.4)

- Provide 32" wide doors to all interior accessible rooms.  (CBC 1010.1.1)

- One room must be a minimum of 120 sq. ft. in area. Other habitable rooms, except kitchens, must be a min. of 70 sq. ft.  (CBC 1208.3)

4. 	Habitable rooms other than a kitchen shall not be less than 7' in any direction.  (CBC 1208.1)

5. 	Required ceiling height is 7'-6" minimum and 7'-0" minimum in kitchen, bathrooms, laundry rooms and storage rooms.  (CBC 1208.2)

6. 	Provide natural light in (habitable rooms) (______) by means of exterior wall openings with an area not less than 8% of floor area.  (CBC 1205.2)

7. 	Provide natural light for adjoining spaces.

(CBC 1205.2.1)

8. 	Provide natural ventilation in (habitable rooms) (bathrooms) (______) by means of operable exterior wall openings with an area not less than 4% of floor area.  Mechanical ventilating systems may be permitted.  (CBC 1203.5.1)

9. 	Provide natural ventilation for adjoining spaces.

(CBC 1203.5.1.1)

10. 	For the purpose of providing natural light or ventilation at exterior openings of buildings, a minimum yard of 3 feet in width for one and two story building is required. For buildings more than two stories, the minimum width of the yard shall be increased to 1 foot for each additional story.

(CBC 1206.2)

11.	Courts used for natural light or ventilation and having window opening on opposite side shall not be less than 6 feet in width.  Courts bounded on three or more sides by the wall of the buildings shall not be less than 10 feet in length, unless bounded one end by a public way or yard.  For buildings more than two stories in height, the court shall be increased 1 foot in width and 2 feet in length for each additional story. (CBC 1206.3)

12.	A mechanical ventilation system in lieu of openable windows in the bathroom, toilet room and laundry, which furnishes five air changes per hour direct to the outside, is required.

13.	Attic ventilation of 1/150 of the area of ventilated space (approximately 10 sq. in. for each 10 sq. ft. of attic area) is required.  (CBC 1203.2)

14.	An attic access opening (20" x 30") is required at each separate attic space with a minimum of 30" clearance.  (CBC 1209.2)

15.	Under-floor ventilation shall be not less than 1/150 of under floor area.  (CBC 1203.4)

16.	Show minimum 18" x 24" under floor access opening.

(CBC 1209.1)

17.	Openings below grade for the purpose of natural ventilation shall have a minimum size according to CBC Section 1203.5.1.2.

18.	Provide a door and window schedule. Show type and size of each.

19.	Indicate on plans that interior finish materials applied to wall and ceilings shall be tested as specified in CBC Section 803. Specify the classifications per CBC T803.11 and Section 803.1.  Clearly indicate on plans.

20. 	All shower compartments, regardless of shape, shall have a minimum finished interior area of not less than 1024 square inches and shall be capable of encompassing a 30 inch minimum area and dimensions shall be maintained to a point 72 inches above the shower drain inlet.

(CBC 1210.2.3, CPC 408.6)

21.	Provide (____) water closets for women, (____) water closets for men, and (____) urinals.

(CBC 2901, CPC T422.1)

22.	Toilet rooms shall be provided with a fully openable exterior window with an area not less than 3 square feet or a vertical duct not less than 100 square inches in area for the first water closet plus 50 square inches additional of area for each additional water closet, or a mechanically operated exhaust system capable of providing a complete change of air every 15 minutes.  Such mechanically operated exhaust system shall be connected directly to the outside, and the point of discharge shall be at least 3 feet from any opening that allows air entry into occupied portions of the building.

23.	Toilet room floors shall have a smooth, hard non-absorbent surface such as portland cement, ceramic tile or other approved material that extends upward onto the walls at least 4".  (CBC 1210.2.1)

24.	Walls and partitions within 2 feet of service sinks, urinals, and water closets shall have a smooth, hard, nonabsorbent surface, to a height of not less than 4 feet above the floor, and except for structural elements, the materials used in such walls shall be of a type that is not adversely affected by moisture. (CBC 1210.2.2)

25.	Cement, fiber-cement, or glass mat gypsum backers in compliance with ASTM C1178, C1288 or C1325 shall be used as a base for wall tile in tub and shower areas and wall and ceiling panels in shower areas. Water-resistance gypsum backing board shall be used as a base for tile in water closet compartment walls when installed in accordance with GA-216 or ASTM C840. Regular gypsum wallboard is permitted under tile or wall panels in other wall and ceiling areas when installed in accordance with GA-216 or ASTM C840. Water-resistant gypsum board shall not be used in the following locations:

(CBC Section 2509)

- Over a vapor retarder.

- In areas subject to continuous high humidity, such as saunas, steam rooms or gang shower rooms.

- On ceilings where frame spacing exceeds 12 inches o.c. for ½ inch thick and more than 16 inches o.c. for 5/8 inch thick.

26.	Revise plans to show compliance with the sound transmission requirements for common interior walls, partitions and floor/ceiling assemblies between adjacent dwelling units and sleeping units or between dwelling units and sleeping units and adjacent public areas such as halls, corridor, stairways or service areas.  (CBC Section 1207.1)

27.	One elevator in buildings four or more stories above or below grade plane shall be of such a size to accommodate a 24-inch by 84-inch ambulance stretcher in the horizontal, open position and shall be identified by the international symbol for emergency medical services.  See CBC Section 3002.4a for exceptions.  (CBC 3002.4)

28.	Add note on plans:

a.	Every space intended for human occupancy shall be provided with natural light by means of exterior glazed openings in accordance with CBC Section 1205.2 or shall be provided with artificial light that is adequate to provide an average illumination of 10 foot-candles over the area of the room at a height of 30 inches above the floor level.  (CBC 1205.1 and 1205.3)

- J.	BUILDING ENVELOPE

1.	A fire retardant roof covering is required.  Provide a complete description on plans.  (CBC 1505.1)

2.	Show roof slope(s), drain(s) and overflow drain(s) or scuppers on the roof plan.  Provide a detail of the roof drain and overflow system.

a.	Size the roof drains and overflow drains according to Chapter 11 of the CPC.

(CBC 1503.4)

b.	The roof drain and overflow drain must be independent lines to a yard box.

c.	Roof drainage is not permitted to flow over public property.  (CBC 3201.4)

d.	Overflow scuppers shall be designed in accordance to CPC Section 1101.12.2.1.

e.	Show roof elevation to provide a minimum ¼ in per foot roof slope for drainage or design to support accumulated water.

3.	Provide access to all mechanical equipment located on the roof as required by CBC Section 1209.3.

4.	Show that the penthouse satisfies the requirements of CBC Section 1510.2.

5.	Skylights set at an angle of less than 45 degrees from the horizontal plane shall be mounted at least 4 inches above the plane of the roof on a curb constructed as required for the frame.  Except for R3 occupancies, skylights without a curb shall be permitted on roof(s) with a minimum slope of 14 degrees (three units vertical in 12 units horizontal) (CBC Section 2405.4, 2610.2).  Glass skylights shall comply with CBC Section 2405.  Plastic skylights shall comply with CBC Section 2610.

6.	For pre-fab fireplaces, provide manufacturer, model, and Underwriter Laboratories certification number (or ICC’s). For masonry fireplaces, provide details and calculations for chimney.  (CBC 2111)

7.	Provide veneer details.  Show method of anchorage, size and spacing of anchors.  Comply with requirements per CBC Section 1405.6.

8.	In R1 and R2 occupancies, where the top of the sill of an operable window opening is located less than 36 inches above the finished floor and more than 72 inches above the finished grade or other surface below on the exterior of the building, shall comply with CBC Section 1015.8.

9.	Details of the guardrails at the floor and roof openings, occupied roofs and balconies or porches more than 30" above grade are required.  Guardrails shall be 42" in height, have intermediate rails or balusters spaced at 4" maximum. It shall be designed per CBC Section 1607.8.  (CBC 1015.2)

10.	Each pane of safety glazing installed in hazardous locations shall be identified by a manufacturer’s designation specifying who applied the designation, the manufacturer or installer and the safety glazing standard. The following shall be considered specific hazardous locations for the purposed of safety glazing. Glazing in:

(CBC Section 2406)

a.	Swing doors.

b.	Fixed and sliding panels of sliding door assemblies and panels in sliding and bi-fold closet door assemblies.

c.	Storm doors.

d.	Unframed swinging doors.

e.	Doors and enclosures for hot tubs, whirlpools, saunas, steam rooms, bathtubs, and showers.

f.	Fixed or operable panels adjacent to a door where the nearest exposed edge of the glazing is within 24 inches (610 mm) arc of either vertical edge of the door in a closed position and where the bottom exposed edge of the glazing is less than 60 inches (1525 mm) above the walking surface.  Read code for exceptions.

g.	Fixed or operable panel, other than described in items e and f, which meets all of the following conditions (read code for exception with special installation).

i.	Exposed area of an individual pane greater than 9 square feet (0.84 m2)

ii.	Exposed bottom edge less than 18 inches (457 mm) above the floor.

iii.	Exposed top edge greater than 36 inches (914 mm) above the floor.

iv.	One or more walking surfaces within 36 inches (914 mm) horizontally of the plane of the glazing.

h.	Guards and railings regardless of area or height above a walking surface. Included are structural baluster panels and nonstructural in-fill panels.

i.	Walls and fences enclosing indoor and outdoor swimming pools and spas where all of the following conditions are present:

i.	The bottom edge of the glazing is less than 60 inches (1525 mm) above a walking surface on the pool or spa side of the glazing.

ii.	The glazing is within 60 inches (1525 mm) of a swimming pool or spa water’s edge.

j.	Adjacent to stairways, landings and ramps within 36 inches horizontally of a walking surface; when the exposed surface of the glass is less than 60 inches above the plane of the adjacent walking surface(read code for exception with special installation).

k.	Adjacent to stairways within 60 inches horizontally of the bottom tread of a stairway in any direction when the exposed surface of the glass is less than 60 inches above the nose of the tread (read code for exception with special installation).

11.	Architectural projections on (______) are limited to       (______) (not allowed).  (CBC Section 3202)

12.	Add note on plans:

a. 	Provide an approved spark arrester for the chimney of a fireplace, stove, or barbecue.

(CBC Section 2113.9.2)

b. 	Provide a weep screed for stucco at the foundation plate line a minimum of 4 inches above the earth or 2 inches above paved areas. Weep screeds shall be of a type which will allow trapped water to drain to the exterior of the building. (Show these dimensions on a foundation detail drawing).

(CBC Section 2512.1.2)

- K.	ADDITIONAL WRITTEN COMMENTS

| No. | ###### Comment | Code Sec. No. |
| --- | --- | --- |