Off-Grid Solar Design Worksheet for Mwase

Solar PV Off-Grid System Design: Foundations and AI Applications

IEEE IAS/PES PowerAfrica 2026

Dr. Henry Louie and Dr. Oluleke Babayomi

| Parameter | Initial | After five years |
| --- | --- | --- |
| Avg. daily load (kWh/day) | 7.875 | 10.05 |
| Peak individual load (kW) | 4.11 | 5.24 |
| Coincidence factor | 0.37 | 0.37 |
| Peak aggregate load (kW) | 1.52 | 1.94 |
| Power factor | 0.85 | 0.85 |

System Architecture

DC Bus Voltage: _____________________

Inverter Design

Assumptions: Design margin: 0.20, Power Factor: 0.85, Inverter Efficiency: 85%

Inverter Power Requirement: __________________________________

Max. Inverter DC Current: _____________________________________

Battery Bank Design

Assumptions: Days of Autonomy: 2, End of Life Rating: 80%, Maximum depth-of-discharge: 80%, Design Margin: 7.5%

Battery Capacity Table

|  | 10 hr (42 A, 0.1C) | 20 hr (22.5 A, 0.05C) | 100 hr (5.4 A, 0.01C) |
| --- | --- | --- | --- |
| Capacity | 420 Ah | 450 Ah | 540 Ah |

Average Battery Load: __________________________________

Battery Capacity Cx: _____________________________________

Battery Capacity C’x: _____________________________________

Daily Depth-of-Discharge: _____________________________________

Battery Bank Capacity: _____________________________________

Number of Series Batteries: ________________

Number of Battery Bank Strings: ________________

Solar Array Design

Assumptions: Loss estimate: 22%, Temperature De-rating: 9.5%, Design Margin: 30%,  PV module rating 350 W,

Insolation Table (kWh/m2/day)

| Tilt | Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Latitude -15o | 5.51 | 5.61 | 5.69 | 5.76 | 5.36 | 4.90 | 5.15 | 5.99 | 6.51 | 6.78 | 6.19 | 5.54 |
| Latitude | 5.08 | 5.39 | 5.77 | 6.31 | 6.40 | 6.01 | 6.20 | 6.87 | 6.85 | 6.64 | 5.76 | 5.09 |
| Latitude + 15o | 4.47 | 4.94 | 5.54 | 6.46 | 6.89 | 6.58 | 6.78 | 7.23 | 6.76 | 6.15 | 5.08 | 4.44 |

Charge Controller Parameters

| Charge Controller Parameters | Value |
| --- | --- |
| Maximum power | 3500 W |
| Maximum open-circuit voltage | 150 V |
| Maximum short-circuit current | 60 A |

Rated PV requirement PPV,rated: __________________________________

Rated PV requirement P’PV,rated: _____________________________________

Rated PV requirement P’’PV,rated: _____________________________________

Rated PV requirement P’’’PV,rated: _____________________________________

Number of PV Modules: __________________________

Maximum PV Modules per String: _________________________

Maximum PV Modules per Controller: ____________________