Low Energy Separator Specification for HVAC Systems

SECTION 23 25 00 – HVAC Water Treatment

NON-MEDIA WATER FILTRATION EQUIPMENT

PART 1 GENERAL

1.1	DESCRIPTION

- This section specifies equipment to remove suspended solids in circulating HVAC water systems, including the following:

    - Cooling Tower Water Circulation Systems

    - Evaporative Condenser Spray Water

    - Closed Chilled Water Loops

    - Closed Heated Water Loops

1.2	RELATED WORK

- Test requirements and instructions on use of equipment/system: Section 01 00 00, GENERAL REQUIREMENTS.

- General mechanical requirements and items, which are common to more than one section of Division 23: Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION

- Piping and valves: Section 23 21 13, HYDRONIC PIPING and Section 23 22 13, STEAM AND CONDENSATE HEATING PIPING.

1.3   	QUALITY ASSURANCE

- Refer to paragraph, QUALITY ASSURANCE in Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION.

- Technical Services: Provide the services of an experienced water treatment specialist or technical representative approved by the Water Treatment System Manufacturer to direct flushing, cleaning, pre-treatment, training, debugging, and acceptance testing operations; direct and perform chemical limit control during construction period.

1.4	SUBMITTALS

- Submit in accordance with Section 01 33 00, SUBMITTAL PROCEDURES.

- Manufacturer's Literature and Data including:

    - Low Energy Vortex type water solids removal separator, including installation and operating instructions

- Maintenance and operating instructions in accordance with Section 01 00 00, GENERAL REQUIREMENTS suitable for inclusion into a standard 3-ring binder

PART 2 - PRODUCTS

2.1	GENERAL

- The Contractor shall furnish and install a Low Energy Vortex Solids Separator as shown and detailed on the contract documents. All components of the system provided will be manufactured and supplied by a single company and be certified to be functionally compatible, such as the CS/SS Separators manufactured by General Water Systems of Corona, CA or an approved substitution.

  - NON-MEDIA FILTRATION SYSTEM

- Provide A Low Energy Vortex type Solids Separator as shown and detailed on the contract documents equal to the CS/SS Separator manufactured by General Water Systems of Corona, CA or an approved substitution.

- System Description:

    - System shall consist of a Low Energy Vortex Separator and Solids Removal System.

- Low Energy Separator

    - Employ A low energy vortex style, solids from liquid separator to remove particulates from the HVAC Water Circulation System.

    - Low Energy Separator shall be constructed to ASME standards with high quality carbon steel or stainless steel as shown and detailed on the contract documents

    - Material thickness shall be a minimum of 0.25 inches.

    - Maximum operating pressure shall be 150 psig unless otherwise specified.

    - Low Energy Separator inlet shall be capable of passing a solid sphere equal to 25 percent of the inlet pipe connection size.

    - Low Energy Separator shall be designed to minimize internal turbulence that results in higher pressure drops for a given flow and more chance for entrainment of particulates in the outlet water discharge.

    - Low Energy Separator shall operate properly with a pressure drop across the separator n the range of 4-8 psi.  Separators designed for higher pressure drops such as 8-12 psi will not be acceptable.

    - Low Energy Separator shall not have flanged body or removable dome.

      - No slots or movable parts are allowed in the head area that requires servicing or cleaning.

    - Low Energy Separator shall incorporate both an automatic internal air bleed and manual air bleed.

    - Deposition slots shall be installed at the bottom spin plate to facilitate collection and removal of solids from the separator.

- Solids Removal System

    - The Low Energy Separator will be equipped with a means of automatically removing solids from the collection chamber.  System chosen will be as described in the contract documents and will consist of one of the following:

      - A timer controlled motor-operated purge valve to flush solids collected in the separator periodically down the service drain.

        - Normally, a fast acting motorized ball valve (MBV) is supplied that will stop at its then position upon loss of power.

          - Cycle time for the MBV option is between 11 and 25 seconds.

          - Normal time between purge cycles is from 4 to 8 hours.

          - A slow acting spring return motorized ball valve such as the MBVSR used for system bleed control with cycle time longer than 30 seconds shall not be used as proper flushing action cannot be obtained.

        - If the contract documents so state a battery backup system can be applied to the faster operating motorized ball valve to provide for failsafe operation (MBVFS option).

        - If the purge valve option is elected, the contractor shall provide either on of the following:

          - A drain sized to prevent overflowing during the normal unrestricted operation of the valve.  Restricting flow rate with a throttling valve is not acceptable as it will prevent proper flushing of the solids collection area.

          - A surge tank sized large enough to collect the full discharge of the valve during normal unrestricted operation of the valve and slowly discharge to the floor drain without overflow

      - A Recovery Tank is available for those instances where it is not desirable to flush solids collected down the drain or lose treated closed loop water.

        - The Recovery Tank is fitted with a 25-micron filter bag, inlet/outlet liquid filled gauges, manual air bleed valve, and flow sight glass with propeller.

        - Recovery tank is fitted with a monitoring package including Differential Pressure switch with local “Clean-Dirty-Change” indicator.  The magnetic operated Reed Switch will provide alarm indication for the Building Management System.

PART 3 - EXECUTION

  - EXAMINATION

- Verify field conditions and suitability for installation according to manufacturer’s published installation data.

  - INSTALLATION

- Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

- Install equipment level and plumb.

- Install equipment per recommendations in the manufacturer's published installation data.

- Cleaning of piping systems using the vortex Low Energy Separation System:

    - The use of a Separator System does not relieve the contractor or owner of normal cleaning of the system prior to startup.

    - Immediately after hydrostatic testing of piping, systems shall be cleaned, drained, and flushed with clean water. Any chemical cleaners used in this process shall be thoroughly flushed from the piping system.

    - Under no circumstance will water be allowed to sit stagnant or circulate without water treatment after initial testing or cleaning.

    - Proper system layup procedures must be followed anytime the water system is not running.

        - An appropriate vapor type corrosion inhibitor as determined by the factory trained and certified water treatment specialist shall be first circulated in the system for a period of time as required by the treatment manufacturer and dictated by the size of the system treated. .

        - The system shall be drained of all water.

        - Immediately prior to putting the HVAC Separator System into operation, the system shall be re-filled with clean water.

    - Consult with Water Treatment System Manufacturer or the local Representative for additional details.

- CONNECTIONS

    - Piping installation requirements are specified in other Division 23 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

    - Install piping adjacent to equipment to allow service and maintenance.

    - Separator purge line (if required) should be routed to the nearest floor drain or surge tank, if required.

      - Floor drain shall be large enough to take the full amount of water flow from the separator during its purge cycle without overflowing.

      - Confirm with the Low Energy Separator Manufacturer what the required maximum flow rates are for the separator with purge valve.

    - Confirm applicable electrical requirements in Division 26 Sections for connecting electrical equipment.

        - Provide proper electrical ground to the equipment.

        - Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

  - TESTING

- Engage a factory-authorized service representative to perform startup service for the Low Energy Separator.

    - Inspect field-assembled components and equipment installation, including piping and electrical connections. Report results in writing.

    - Inspect piping and equipment to determine that systems and equipment have been cleaned, flushed, and filled with water, and are fully operational.

    - Place Low Energy Separator into operation and check for proper differential pressure as measured from the inlet and outlet connections of the separator.

  - The Field Service Technician shall provide an Initial Start-up Service Report to the operator and the Manufacturer TRAINING

- Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain the HVAC Separator System and equipment.

- Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

    - Schedule at least one (1) hour of training with Owner.

    - Provide at least seven days' advance notice.

- Review data in maintenance manuals.

END OF SECTION