GLS™ CleanSweep™ Specification

for

Low Energy Cooling Tower Filtration

SECTION 23 25 00 – HVAC Water Treatment

COOLING TOWER WATER LOW ENERGY FILTRATION SYSTEM

PART 1 GENERAL

1.1	DESCRIPTION

- This section specifies cleaning and treatment of circulating HVAC water systems, including the following:

    - Tower Cooling Water - Closed Loop Systems Fluid Coolers

    - Tower Cooling Water – Open Cooling Loop Systems

    - Tower Cooling Water – Evaporative Condensers

1.2	RELATED WORK

- Test requirements and instructions on use of equipment/system: Section 01 00 00, GENERAL REQUIREMENTS.

- General mechanical requirements and items, which are common to more than one section of Division 23: Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION

- Piping and valves: Section 23 21 13, HYDRONIC PIPING and Section 23 22 13, STEAM AND CONDENSATE HEATING PIPING

1.3   	QUALITY ASSURANCE

- Refer to paragraph, QUALITY ASSURANCE in Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION.

- Technical Services: Provide the services of an experienced water treatment specialist or technical representative approved by the Water Treatment System Manufacturer to direct flushing, cleaning, pre-treatment, training, debugging, and acceptance testing operations; direct and perform chemical limit control during construction period.

1.4	SUBMITTALS

- Submit in accordance with Section 01 33 00, SUBMITTAL PROCEDURES.

- Manufacturer's Literature and Data including:

    - Non-media Low Energy Filtration skid for cooling tower solids removal, including installation and operating instructions.

    - Optional Tower Sweeper system designed by Filter Skid Manufacturer if included in the contract documents

- Maintenance and operating instructions in accordance with Section 01 00 00, GENERAL REQUIREMENTS suitable for inclusion into a standard 3-ring binder

PART 2 - PRODUCTS

  - GENERAL

- To help prevent particle fouling of the cooling system’s various components, reduce maintenance and servicing of equipment and maintain optimum energy efficiency of the system heat exchangers and cooling towers, the Contractor shall furnish and install a Low Energy Cooling Tower Filtration System as shown and detailed on the contract documents.

  - LOW ENERGY TOWER FILTRATION SYSTEM

- All components of the system provided will be manufactured and supplied by a single company and be certified to be functionally compatible, such as the GLS™ manufactured by General Water Systems of Corona, CA or an approved substitution.

- Provide the optional Low Energy Sweeper System using water jets to move debris in the basin for picking up by the filtration unit if shown and detailed on the contract documents.

- System Description:

    - System shall consist of a Low Energy Vortex Solids Separator, Pump and Motor, Pump Suction Strainer, Control Panel and means for removal of collected solids as specified in the contract documents.

    - Provide Low Energy Filtration Skid with Inlet Block Valve and Outlet Throttling Valve as shown and detailed on the contract documents to allow for servicing of system components and adjustment for proper operation.

    - If a Sweeper System is detailed in the contract documents, it shall be of Low Energy Design and provided by the Filtration System Manufacturer.  Systems preinstalled by the Tower manufacturer that are not approved by the Filtration System Manufacturer as of proper Low Energy design are not acceptable. Size and Design the Low Energy Filtration System to reduce the amount of debris circulating in the cooling system water.

        - Size GLS™ Systems to provide a minimum of 10 percent of the total tower recirculation rate as detailed on the contract documents or 1.5 gpm per square foot of swept area for sweeper systems.

        - Calculated flows shall be at 40 Feet Total Dynamic Head for standard systems that do not use Sweepers.

        - For Sweeper Systems, calculated flows shall be at 40 feet total dynamic head.  The typical high pressure sweeper systems requiring 60 to 100 feet of total dynamic head are not acceptable.  The Filter System Manufacturer based upon proposed skid location and lengths and sizes of interconnecting pipe will calculate actual required head.

- Low Energy Separator

    - A low energy vortex style, solids from liquid separator shall be employed to remove particulates from the cooling tower basin and circulating water.

    - Low Energy Separator shall be constructed to ASME standards with high quality carbon steel or stainless steel as shown and detailed on the contract documents

    - Material thickness shall be a minimum of 0.25 inches.

    - Maximum operating pressure shall be 150 psig unless otherwise specified.

    - Low Energy Separator inlet shall be capable of passing a solid sphere equal to 25 percent of the inlet pipe connection size.

    - Low Energy Separator shall be designed to minimize internal turbulence that results in higher pressure drops for a given flow and more chance for entrainment of particulates in the outlet water discharge.

    - Low Energy Separator shall operate properly with a pressure drop across the separator in the range of 4-8 psi.  Separators designed for higher pressure drops such as 8-12 psi will not be acceptable as more than 40 feet of head will be required by the system.

    - Low Energy Separator shall not have a flanged body or removable dome.

        - No slots or movable parts are allowed in the head area that require servicing or cleaning.

    - Low Energy Separator shall incorporate both an automatic internal air bleed and manual air bleed.

    - Deposition slots shall be installed at the bottom spin plate to facilitate collection and removal of solids from the separator.

    - The GLS™ Separator system is equipped with a timer controlled motor-operated purge valve to flush solids collected in the separator periodically down the service drain.

      - Normally a fast acting motorized ball valve (MBV) is supplied that will stop at its then position upon loss of power.

        - Cycle time for the MBV option is between 11 and 25 seconds.

        - Normal time between purge cycles is from 4 to 8 hours.

      - A slow acting spring return motorized ball valve such as the MBVSR used for system bleed control with cycle time longer than 30 seconds shall not be used as proper flushing action cannot be obtained..

      - If the contract documents so state a battery backup system can be applied to the faster operating motorized ball valve to provide for failsafe operation (MBVFS option).

      - If the purge valve option is elected, the contractor shall provide either one of the following:

        - A drain sized to prevent overflowing during the normal unrestricted operation of the valve.  Restricting flow rate with a throttling valve is not acceptable as it will prevent proper flushing of the solids collection area.

        - Size a surge tank large enough to collect the full discharge of the valve during normal unrestricted operation of the valve and slowly discharge to the floor drain without overflow.

      - Recovery Tank in lieu of the purge valve is not acceptable.

- Pump and Motor will be as shown and detailed on the contract documents.

    - Piping between pump and separator will be provided with union or flanged connections to allow for easy replacement of pump seals when required.

- A basket strainer with 0.25 inch perforated 304 stainless steel screen shall protect the pump inlet.

- Low Energy Filtration System electrical panel shall be certified and labeled to UL 508A and CSA 22.2 14-95, with NEMA 4 powder coated steel, door interlock safety, fusible disconnect switch or disconnect motor starter with thermal overload, 120 VAC magnetic contactor, 460/120 VAC transformer with primary/secondary circuit breakers, pump “run” light and provision for automatic and manual operation.

- Low Energy Sweeper System, if required by the contract documents:

    - Sweeper system shall not consist of nozzles, eductors or other devices that require more than 6 psi of system pressure to operate properly.

    - The manufacturer shall provide custom System design and assembly drawing after receipt of purchase order.

    - System shall consist of a kit containing all PVC pipes, water jets, couplings, valves, pressure gauges, and other components required to assemble the complete system inside the tower basin.

      - Contractor shall be responsible for proper installation of equipment.

      - Manufacturer shall label and provide alignment marks to facilitate easy and accurate assembly.

    - System shall include an exit header suitable for vacuum extraction of suspended solids to effectively eliminate the suspended solids from entering the cooling system recirculation loop.

    - Low Energy Filtration System piping from the basin sweeper system to the filter skid shall be supplied and installed by the contractor..

PART 3 - EXECUTION

  - EXAMINATION

- Verify field conditions and suitability for installation according to manufacturer’s published installation data.

  - INSTALLATION

- Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

- Install equipment level and plumb.

- Install equipment per recommendations in the manufacturer's published installation data.

- Cleaning of piping systems using the GLS/GLR™ Tower Basin Filtration System

    - The use of a Low Energy Tower Basin Filtration System does not relieve the contractor or owner of normal cleaning of the system prior to startup.

    - Immediately after hydrostatic testing of piping, systems shall be cleaned, drained, and flushed with clean water.  Any chemical cleaners used in this process shall be thoroughly flushed from the piping system.

    - Under no circumstance will water be allowed to sit stagnant or circulate without water treatment after initial cleaning and testing.

    - Proper system layup procedures must be followed anytime the water system is not running.

        - An appropriate vapor type corrosion inhibitor as determined by the factory trained and certified water treatment specialist shall be first circulated in the system for a period of time as required by the treatment manufacturer and dictated by the size of the system treated.

        - The system shall be drained of all water.

        - Immediately prior to putting the Low Energy Tower Basin Filtration System (GLS™) into operation, the system shall be re-filled with clean water.

    - Consult with Water Treatment System Manufacturer or the local Representative for additional details.

- CONNECTIONS

    - Piping installation requirements are specified in other Division 23 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

    - Install piping adjacent to equipment to allow service and maintenance.

    - Separator purge line should be routed to the nearest floor drain or surge tank, if required.

    - Floor drain shall be large enough to take the full amount of water flow from the separator during its purge cycle without overflowing.

      - Confirm with the Low Energy Bypass Filtration System Manufacturer what the required maximum flow rates are for the separator with purge valve.

    - Confirm applicable electrical requirements in Division 26 Sections for connecting electrical equipment.

        - Provide proper electrical ground to the equipment.

        - Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

  - TESTING

- Engage a factory-authorized service representative to perform startup service for the Low Energy Tower Basin Filtration System.

    - Inspect field-assembled components and equipment installation, including piping and electrical connections. Report results in writing.

    - Inspect piping and equipment to determine that systems and equipment have been cleaned, flushed, and filled with water, and are fully operational.

    - Place HVAC Low Energy Tower Filtration System into operation and check sweeper system, if installed, for proper orientation in the tower basin. The Field Service Technician shall provide an Initial Start-up Service Report to the operator and the Manufacturer.

- No water system using a Lowe Energy Tower Basin Filtration System shall be put into operation without the Low Energy Tower Basin Filtration System being energized and fully operational. Failure to comply may result in damage to connected heat exchange equipment from dirt and debris.

  - TRAINING

- Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain Tower Basin Filtration System and equipment.

- Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

    - Schedule at least two (2) hours of training with Owner.

    - Provide at least seven days' advance notice.

- Review data in maintenance manuals.

END OF SECTION