Sand Filter Specification for HVAC Systems

SECTION 23 25 00 – HVAC Water Treatment

CIRCULATING WATER FILTRATION SYSTEM

PART 1 GENERAL

1.1	DESCRIPTION

- This section specifies cleaning and treatment of circulating HVAC water systems, including the following:

    - Tower Cooling Water

    - Evaporative Condenser Spray Water

    - Chilled Water Closed Loops

    - Heated Water Closed Loops

1.2	RELATED WORK

- Test requirements and instructions on use of equipment/system: Section 01 00 00, GENERAL REQUIREMENTS.

- General mechanical requirements and items, which are common to more than one section of Division 23: Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION.

- Piping and valves: Section 23 21 13, HYDRONIC PIPING and Section 23 22 13, STEAM AND CONDENSATE HEATING PIPING.

1.3   	QUALITY ASSURANCE

- Refer to paragraph, QUALITY ASSURANCE in Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION.

- Technical Services: Provide the services of an experienced water treatment specialist or technical representative approved by the Water Treatment System Manufacturer to direct flushing, cleaning, pre-treatment, training, debugging, and acceptance testing operations; direct and perform chemical limit control during construction period.

1.4	SUBMITTALS

- Submit in accordance with Section 01 33 00, SUBMITTAL PROCEDURES.

- Manufacturer's Literature and Data including:

    - Filtration skid including sand filter, pump, PLC controller and automatic valves.

    - Sweeper jet system for cooling tower solids removal, if provided, including installation drawings and operating instructions.

- Maintenance and operating instructions in accordance with Section 01 00 00, GENERAL REQUIREMENTS suitable for inclusion into a standard 3-ring binder.

PART 2 - PRODUCTS

  - GENERAL

- The Contractor shall furnish and install a Sand Filter System as shown and detailed on the contract documents. All components of the system provided will be manufactured and supplied by a single company and be certified to be functionally compatible, such as the SFS™ or SFC™ manufactured by General Water Systems of Corona, CA or an approved substitution.

  - BYPASS SAND FILTER SYSTEM

- Provide an integrated Bypass Sand Filter System treatment skid as shown and detailed on the contract documents equal to the SFS/SFC™ manufactured by General Water Systems of Corona, CA or an approved substitution.

- Provide the optional Low Energy Sweeper System using water jets to move debris in the basin for picking up by the filtration unit if shown and detailed on the contract documents.

- System Description:

    - The Bypass Filtration System will remove up to 95% of suspended solids 10 microns and larger circulating in the HVAC water circulation system with standard No. 20 Silica Sand Media (Other Media is available by special order).

    - For Cooling Tower Basin Water, the system will include a self-contained, skid mounted Sand Filter System.

    - If a Sweeper System is detailed in the contract documents, it shall be of Low Energy Design and provided by the Filtration System Manufacturer.  Systems preinstalled by the Tower manufacturer that are not approved by the Filtration System Manufacturer as of proper Low Energy design are not acceptable.

      - Sweeper system shall not consist of nozzles, eductors or other devices that require more than 4 psi of system pressure to operate properly.

      - The manufacturer shall provide custom System design and assembly drawing after receipt of purchase order.

      - System shall consist of a kit containing all PVC pipes, water jets, couplings, valves and other components required to assemble the complete system inside the tower basin.

        - Contractor shall be responsible for proper installation of equipment.

        - Manufacturer shall label and provide alignment marks to facilitate easy and accurate assembly.

      - Low Energy Filtration System piping from the basin sweeper system to the filter skid shall be supplied and installed by the contractor.

    - Calculated flows shall be at 40 Feet Total Dynamic Head for systems using the Low Energy Sweeper System.  The typical high pressure sweeper systems requiring 60 to 100 feet of total dynamic head are not acceptable.  The Filter System Manufacturer based upon proposed skid location and lengths and sizes of interconnecting pipe will calculate actual required head.

    - Calculated flows shall be at 30 Feet Total Dynamic Head for standard systems that do not use Sweepers.

    - Filter is designed to process 10-15% of the tower water recirculation rate at the proper discharge pressure to operate the basin sweeper system if provided.

    - For Closed Loop applications the system will include a self-contained, skid mounted Sand Filter System designed to process 8-10% of the closed loop recirculation rater at 30 Feet Total Dynamic Head..

    - Backwash can be with either with System Water (SFS Unit) or City Water (SFC Unit) as stated in the contract documents.

    - Backwash drain connection must be sized to handle the Sand Filter Design Flow Rater for up to 3 minutes.  Instead of a large drain pipe, an appropriate sized backwash surge tank can be provided.

- Sand Filter System:

    - Sand Filer System will be factory-assembled with one source of supply and warranty for all parts and components such as the SFS™ or SFC™ by General Water Systems.  System shall include the following items and features.

        - Filter tank shall be sized for 20 gpm/sq. ft. of filter bed surface.

        - Filter media will be provided for field installation into tank.

        - Inlet and Outlet Pressure gauges and differential pressure switch.

        - End suction pump and motor package.

        - Prewired control panel with PLC automatic backwash control.

        - Top Service Port

        - Automatic and manual air relief valves

        - Removable under drain stainless steel wedge-wire screens.

        - Automatic electric operated backwash valves.

    - Tank shall be constructed with high quality carbon steel, stainless steel or fiberglass as shown and detailed on the contract documents

        - Carbon Steel and Stainless Steel tanks shall be rated for a maximum working pressure of 80 psig at 100°F.

        - Fiberglass tanks shall be rated for a maximum working pressure of 50 psig at 104°F.

    - System Pump shall be end suction, close coupled, cast iron type with bronze impeller and TEFC motor with 1.15 service factor.  Mechanical seal shall be Carbon, Silicon Carbide Viton™ type.

    - Control panel shall be in a NEMA 4 watertight powder coated enclosure suitable for outdoor installation.  Fiberglass Enclosures are not acceptable.

    - Lateral/Under Drains shall be of 316 stainless steel wedge wire screen in the carbon steel and stainless steel tanks.  The drains shall be of PVC screen in the Fiberglass tanks.

    - Cast Iron Basket Strainer with ¼” perforated 304 stainless steel internal screen and quick opening cover shall protect pump inlet on systems with cooling tower basin sweepers.

    - Piping shall be Schedule 80 PVC with exterior enamel finish.

    - Cast Iron Y-Strainer will be supplied on units using system water for backwash (SFS™) to prevent debris from clogging the Under Drain screens.  Y-Strainer will be made of cast iron with 3/64” (16-mesh) perforated 304 stainless steel screen.

    - Frame for mounting pump shall be carbon steel with exterior powder coat finish.  Sand filters 36” diameter and smaller will be mounted on the pump frame.  Larger sand filter vessels will be equipped with legs for field mounting next to pump frame.

PART 3 - EXECUTION

  - EXAMINATION

- Verify field conditions and suitability for installation according to manufacturer’s published installation data.

  - INSTALLATION

- Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

- Install equipment level and plumb.

- Install equipment per recommendations in the manufacturer's published installation data.

- Cleaning of piping systems using the SFS/SFC™ Sand Filter System

    - The use of a Sand Filter System does not relieve the contractor or owner of normal cleaning of the system piping prior to startup.

    - Immediately after hydrostatic testing of piping, systems shall be cleaned, drained, and flushed with clean water.  Any chemical cleaners used in this process shall be thoroughly flushed from the piping system.

    - Under no circumstance will water be allowed to sit stagnant or circulate without water treatment after initial cleaning and testing.

    - Proper system layup procedures must be followed anytime the water system is not running.

        - An appropriate corrosion inhibitor as determined by the factory trained and certified water treatment specialist shall be first circulated in the system for a period of time as required by the treatment manufacturer and dictated by the size of the system treated.

        - The system shall be drained of all water.

        - Immediately prior to putting the Sand Filter System into operation, the system shall be re-filled with clean water.

    - Consult with Water Treatment System Manufacturer or the local Representative for additional details.

- CONNECTIONS

    - Piping installation requirements are specified in other Division 23 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

    - Install piping adjacent to equipment to allow service and maintenance.

    - Rout the Sand Filter backwash line to the nearest floor drain or surge tank, if required.

    - Floor drain shall be large enough to take the full amount of water flow from the sand filter during its backwash cycle without overflowing, otherwise provide a properly sized surge tank.

    - Confirm applicable electrical requirements in Division 26 Sections for connecting electrical equipment.

        - Provide proper electrical ground to the equipment.

        - Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

  - TESTING

- Engage a factory-authorized service representative to perform startup service for the Sand Filtration System.

    - Inspect field-assembled components and equipment installation, including piping and electrical connections. Report results in writing.

    - Inspect piping and equipment to determine that systems and equipment have been cleaned, flushed, and filled with water, and are fully operational.

    - Place HVAC water filtration system into operation and check sweeper jets, if installed for proper orientation in the tower basin during the preliminary phase of HVAC systems' startup procedures.

    - An Initial Start-up Service Report shall be provided to the operator and the Manufacturer by field service technician.

- No water system using a Sand Filtration System shall be put into operation without the Sand Filtration System being energized and fully operational. Failure to comply may result in damage to connected heat exchange equipment from dirt and debris.

  - TRAINING

- Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain Sand Filtration System and equipment.

- Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

    - Schedule at least two (2) hours of training with Owner.

    - Provide at least seven days' advance notice.

- Review data in maintenance manuals.

END OF SECTION