Bypass Feeder, GE ASME Professional Series for HVAC Systems

SECTION 23 25 00 – HVAC water treatment

chemical bypass feeders

- PRODUCTS

2.1           GENERAL

        - All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

        - Chemical Feed System Description:

Closed-Loop System:  One bypass feeder on each system with isolating and drain valves with inlet piping connecting to discharge of circulating pumps, and outlet side of feeder connected to suction side of pump unless otherwise indicated.

Introduce chemical treatment through bypass feeder when required or indicated by test.

  - Manufacturers

- Subject to compliance with requirements, provide products by one of the following:

- Griswold Water Systems or approved equal

  - Chemical feeding equipment

- Domed Bottom Bypass Feeder:  Provide the quantity and capacity of feeder as shown on the construction drawings.

1.  The feeder shall be constructed of steel or stainless steel as specified in the construction drawings.

2.   Capacity 2, 5, or 12 gallon.

3.   Steel feeders shall have a blue powder coat finish.

4.   The feeder will be rated for a minimum of 350 psig at 250 degrees F.

5.  Tank shall be provided with a wide mouth of not less than 4” inside diameter so that chemicals can be introduced without the need of a funnel.

6.   Four ¾” access ports for flow, vent, and drain.

7.  The enclosure shall be a grooved end cap. The retaining bolts are removable by a small adjustable wrench.  Rotating cap closures or closures requiring special wrenches shall not be considered equal.

8.   The feeder will include heavy legs, minimum 3/16” thick, welded to the sides of the vessel, with holes in the feet to allow floor mounting with anchor bolts.

9.   OPTIONS

                - Stainless steel basket with 1/8” perforations to hold solid chemicals or optional filter bag.

                - Filter Bag – The bypass feeder shall be provided with a 25 micron filter bag fully supported by a stainless steel filter basket.

                - Cartridge Filter Kit with 25 micron element rated for the specified maximum temperature of 100, 170 or 250 degrees F as stated on the construction drawings.

                - Plastic filling funnel kit with valve for introduction of liquid agents without opening the lid to the feeder.  Valve in kit will include an integral vent valve to bleed off air or release pressure.

                - Isolation valve kit includes two ¾” Griswold ball valves with integral ¼” drain/vent valves, minimizing installation time and cost by eliminating separate valves and piping components.